## Slide 1: Overhead Detail Inspection (ODI) Training
New Electrical System Inspectors (ESIs)
Module 6: Detail Inspection
Notes: The instructor notes for this course are divided into four sections, as is applicable:
References: Provides resource information about the source of the course content
Purpose: To explain the approach and intention of each slide
Delivery: To provide information and content to discuss with the group
  (Note: Some slides will not have specific delivery information. In this case, just present the contents of the slide.)
Checks: This section references the slide and uses as a type of asterisk. Its purpose is to remind the instructor to make the practical application of the course content to another program (e.g., Safety, Error Prevention, Rules That Will Keep You Alive, SCE Values & Goals, etc.)
------------------------------------------------
For this slide:
References:
Distribution Inspection & Maintenance Program (DIMP) manual
Distribution Vegetation Management Plan (DVMP)
Purpose: Detail inspections
Delivery:
Module 6 duration: 90 minutes
Instructor-led training

## Slide 2: Welcome & Introductions
Notes: Purpose: Introductions
Delivery:
Introduce yourself and ask the students to introduce themselves and their work location
NOTE: Slides 2-4 appear in all of the modules of this course in the event that multiple instructors teach and/or over multiple days. Feel free to skip these slides as necessary.

## Slide 3: Safety First!
First Aid kit
Volunteers
Earthquake procedures
In case of fire
Emergency exits
Where to gather outside
Notes: Purpose: Safety first
Delivery:
Review safety procedures
Understand what to do in an emergency

## Slide 4: Logistics & Guidelines
Cell phones/pagers off or silent
Restroom locations
Scheduled breaks and meals
Length of training
Class rules and guidelines
Notes: Purpose: Review class rules
Delivery: Review the classroom rules with students

## Slide 5: Detail Inspection

## Slide 6: Learning Objectives
At the end of this module, students will be able to:
  Explain the purpose and duties regarding a Detail Inspection
  Discuss the Distribution Assets that are inspected
  Discuss the steps of the inspection method
  Describe priority assignments
  Describe the differences between Transmission & Distribution reporting
  Describe P1 conditions relating to spills and vegetation
  Explain the purpose of the Annual Grid Patrol (AGP)
Notes: Purpose: Understand the requirements of the module
Delivery: Review slide with students

## Slide 7: Module Overview
Purpose
Inspector Duties
Distribution Assets Inspected
Inspection Method
Priorities
Transmission & Distribution Reporting
P1 Conditions (spills and vegetation)
Annual Grid Patrol (AGP)
Notes: Purpose: Prepare students for module
Delivery: Review a high-level overview of the module with students

## Slide 8: Purpose
Detail Inspection – for hazardous conditions, it is an evaluation of an SCE Distribution asset in close proximity to:
  Identify,
  Document,
  Validate, and
  Make public level repairs
Notes: Reference: Distribution Inspection & Maintenance Program (DIMP) manual
Purpose: Define the purpose of a Detail Inspection
Delivery: Same as slide

## Slide 9: Inspector Duties
Identifying discrepancies
Rating and recording conditions
Performing minor corrective action
Documenting priority rated safety and reliability conditions.
Notes: Reference: Distribution Inspection & Maintenance Program (DIMP) manual
Purpose: To Inform ESIs about their job duties and responsibilities for these inspections
Delivery: Discuss ESI job duties for performing detail inspections

## Slide 10: Distribution Assets Inspected
Poles
Crossarms
Insulators
Fuses
Transformers
Conductors
Regulators
Visible wires and cables, plus associated components
Notes: Reference: Distribution Inspection & Maintenance Program (DIMP) manual
Purpose: Brief review of Distribution’s assets inspected by ESIs
Delivery: As Module 4: Equipment Recognition described the assets, this module describes the process of the Detail inspection

## Slide 11: Inspection Method
This procedure provides instructions for inspecting a structure in its entirety
  When to record findings
  How to make repairs
  How to identify when a repair has already been made
  What signs to look for on the pole
  How to know when an ESI is looking for a discrepancy that does not exist (DNE)
Notes: Reference: Distribution Inspection & Maintenance Program (DIMP) manual
Purpose: Provide an overview of the inspection process
Delivery: Same as slide

## Slide 12: Inspection Method (cont.)
The ODI group quality performance goal is to achieve annual quality goals (Priority 1-2, a minimum of 94% at all times) and to establish continuous improvement practices
Safety is the first responsibility of each SCE employee
The ODI performance priorities are:
  Safety
  Quality
  Productivity
Notes: Reference: Distribution Inspection & Maintenance Program (DIMP) manual
Purpose: Explain SCE’s performance and safety goals regarding ODIs
Delivery: Same as slide

## Slide 13: Inspection Method (cont.)
An ESI inspects a pole using the following procedures:
  Identifies the pole using the correct FIM in the field tool
  Checks the field tool for existing conditions
  Visually inspects the pole
  Identifies any non-conforming conditions as defined in the ODI Manual
  Inputs findings in the field tool
  Confirms or corrects existing conditions
  Makes repairs at the public level
Notes: Reference: Distribution Inspection & Maintenance Program (DIMP) manual
Purpose: Explain the ODI procedures
Delivery: Same as slide

## Slide 14: Inspection Method (cont.)
Before approaching a structure, inspect the pole from a distance for potential safety hazards, using your binoculars
Notes: Reference: Distribution Inspection & Maintenance Program (DIMP) manual
Purpose: Explain the ODI procedures
Delivery: Same as slide

## Slide 15: Inspection Method (cont.)
(cont.) To determine span length:
Click the image or copy/paste into your browser
https://www.youtube.com/watch?v=S_kSyONkaDw&list=PLIPXTb5qqJ-PByh6D4MhZNFS3GhYQJYyT
Notes: Reference: See YouTube video
Purpose: Familiarize with the Range Finder
Delivery:
NOTE: Questions appear one at a time by click
Click on the link to watch the videos (1st video is 2 mins., altogether they are approximately 20 minutes total) https://www.youtube.com/watch?v=S_kSyONkaDw&list=PLIPXTb5qqJ-PByh6D4MhZNFS3GhYQJYyT

## Slide 16: Inspection Method (cont.)
Verify that you have the correct pole number in your field tool (laptop/iPad)
  View the conditions and note any work orders
  Inspect the structure and determine if the conditions exist
  Correct incorrect entries and validate the data
Notes: Reference: Distribution Inspection & Maintenance Program (DIMP) manual
Purpose: Explain the ODI procedures
Delivery: Same as slide

## Slide 17: Inspection Method (cont.)
Start an inspection at the Primary level (top of the pole) down to the lowest equipment
  Look for “High Voltage” sign damage
  Inspect insulators for squatters or damage such as large chips, loose or damaged connectors, or vandalism from a gun shot
  Inspect crossarm integrity for cracks, splits, burns, and under-arm conduit
Notes: Reference: Distribution Inspection & Maintenance Program (DIMP) manual
Purpose: Explain the ODI procedures
Delivery: Same as slide

## Slide 18: Inspection Method (cont.)
Start an inspection at the Primary level (cont.)
  Inspect the equipment attached to the crossarm, such as insulators, conductors, lightning arrestors, fuses, braces, etc.
  Look for trees encroachment, stress, sagging, entanglement, or anything interfering with the power lines
  Inspect for idle hardware (hardware not serving any purpose) and determine if it is causing a safety or reliability condition
  Inspect missing or damaged ground molding
Notes: Reference: Distribution Inspection & Maintenance Program (DIMP) manual
Purpose: Explain the ODI procedures
Delivery: Same as slide

## Slide 19: Inspection Method (cont.)
Inspect for secondary clearances issues beginning with the secondary crossarm
  Look for wood damage such as splits, cracks, idle equipment, burns, etc.
  Inspect insulators for squatters or damage such as large chips, loose or damaged connectors, or vandalism from a gun shot
  Check the secondary conductor for clearances, damage, and idle equipment
Notes: Reference: Distribution Inspection & Maintenance Program (DIMP) manual
Purpose: Explain the ODI procedures
Delivery: Same as slide

## Slide 20: Inspection Method (cont.)
Check secondary rack construction
  Check the rack for missing or damaged bolts and hardware, rollers, or idle equipment
  Check the conductor for bare wire, idle hardware
  Look for trees encroachment, stress, sagging, entanglement, or anything interfering with the power lines
Notes: Reference: Distribution Inspection & Maintenance Program (DIMP) manual
Purpose: Explain the ODI procedures
Delivery: Same as slide

## Slide 21: Inspection Method (cont.)
Inspect streetlight poles
  Ensure streetlight fixtures are attached to the structure
  Look for damage that could cause a safety or reliability problem
  Check that all conductors have adequate radial clearance (not in contact) with the light arm and light body
Notes: Reference: Distribution Inspection & Maintenance Program (DIMP) manual
Purpose: Explain the ODI procedures
Delivery: Same as slide

## Slide 22: Inspection Method (cont.)
Look closely at all service drops connected to the pole
  Use the measuring stick when in doubt to determine accurate measurements
  Look for adequate distance between the conductor and any physical structures such as buildings, garages, porches, etc.
  Measure service drops over paved alleys or dirt roads at the curve or middle of the road for distance between road and conductor
Notes: Reference: Distribution Inspection & Maintenance Program (DIMP) manual
Purpose: Explain the ODI procedures
Delivery: Same as slide

## Slide 23: Inspection Method (cont.)
Look closely at all service drops connected to the pole (continued)
  Follow the conductor from connection to connection for clear conductor path.
  Look for trees that contact with the drop. Contact causes conductor strain and abrasion and is not acceptable.
  When service drops are bare or have open wire they need to be identified for removal.
  Check that the weatherhead connection is solid and insulated.
Notes: Reference: Distribution Inspection & Maintenance Program (DIMP) manual
Purpose: Explain the ODI procedures
Delivery: Same as slide

## Slide 24: Inspection Method (cont.)
Check to make sure all discrepancies are identified properly and all repairs are made at the public level
  Inspect the entire ground molding very closely from bottom to top
  Look for separations, cracking, bowing, gaps, bad mounting, holes, or if it is missing completely
  Inspect the down guy for excessive slackness and anchor damage
  Inspect the guy guard for damage
  Install new guy guards if damaged or missing
Notes: Reference: Distribution Inspection & Maintenance Program (DIMP) manual
Purpose: Explain the ODI procedures
Delivery: Same as slide

## Slide 25: Inspection Method (cont.)
Check to make sure all discrepancies are identified properly and all repairs are made at the public level (continued)
  Install visibility strips or replace when needed (You must remove damaged strips; don’t install new strips over old)
  Inspect risers for damage, PVC separations, loose holders, and uncapped sweeps
  Repair risers when broken and conductor exposed. Cover with U-groove or split PVC
  Locate and report all damaged electrical manhole lids such as splice or switch boxes and other conductor connection covers
Notes: Reference: Distribution Inspection & Maintenance Program (DIMP) manual
Purpose: Explain the ODI procedures
Delivery: Same as slide

## Slide 26: Inspection Method (cont.)
Record all findings in the field tool
Make and verify all needed repairs
Notes: Reference: Distribution Inspection & Maintenance Program (DIMP) manual
Purpose: Explain the ODI procedures
Delivery: Same as slide

## Slide 27: Priorities
The condition of distribution assets is evaluated during inspections and patrols to determine and record the necessary corrective action in response to identified discrepancies
Discrepancy is a condition that:
  Conflicts with SCE standards, General Order (G.O.) 95, or G.O. 128 requirements
  Left unchecked, in the inspector’s opinion, the condition presents a hazard to the public, utility worker, or will negatively impact system reliability
Notes: Reference: DIMP Manual, Chapter GE-1, Section 2.0, page 5
Purpose: Discuss priorities
Delivery: Same as slide

## Slide 28: Priorities (cont.)
Discrepancies identified during:
  Detail inspections
  Annual Grid Patrols
  While performing associated tasks
They are cross-referenced with a risk assessment matrix and, as necessary, conditions are assigned a priority rating according to the Distribution Inspection and Maintenance Program (DIMP)
Notes: Reference: DIMP Manual, Chapter GE-1, Section 2.0, page 5
Purpose: Discuss priorities
Delivery:
Same as slide
Risk assessment matrix is on the next slide, and accessible by clicking on the URL

## Slide 29: Priorities (cont.)
Priority | Description
Priority 1 | A condition that requires immediate or same day corrective action. Temporary repairs or restoration methods may allow the condition to be re-rated to Priority 2.
Priority 2 | A condition that requires corrective action within 24 months.
Priority 3 | A condition that requires corrective action within 5 years.
Notes: Reference: DIMP Manual, Chapter GE-1, Section 2.0, page 5
Purpose: Discuss priorities
Delivery: Skip slide as necessary

## Slide 30
Priority 3
Action Required 5 Years
Action Required 5 Years
Priority 3
Action Required 5 Years
Priority 3
Action Required 5 Years
Notes: Reference: DIMP Manual, Attachment 1–3: Risk Assessment Matrix, page 10
Purpose: Discuss priorities
Delivery:
NOTE that P3s must be addressed within 5 years
Update picture upon DIMP update

## Slide 31: Priority 1 Conditions
This procedure is to ensure that P1 conditions found in the field are made safe, correctly reported, and documented
  Take as many pictures as needed to capture the condition of the structures and environment
  Call your immediate supervisor
  If your supervisor agrees with the P1 condition, call in the Priority 1
  Provide the information required for the P1, report to your supervisor
Notes: Reference: DIMP Manual, Attachments 1-1, 1-2, & 1-3, pages 7-10
Purpose: Discuss priorities
Delivery: Same as slide

## Slide 32: Priority 1 Conditions (cont.)
  Call the Distribution Operation Center (DOC) for that region. Refer to the ESI phone list.
  Describe the condition to the DOC as discussed
  Complete the Priority 1 Report and attach relevant pictures
Notes: Reference: DIMP Manual, Attachments 1-1, 1-2, & 1-3, pages 7-10
Purpose: Discuss priorities
Delivery: Same as slide

## Slide 33: Transmission & Distribution Structures
There are separate procedures for Distribution or Transmission Priority 1 reporting
Transmission:
  The ESI calls the supervisor and reports
  Supervisor calls Transmission with a report
  Transmission takes over the reported condition
  The Supervisor provides all the information to Transmission
  The ESI stands by if necessary to provide support
Notes: Reference: Distribution Inspection & Maintenance Program (DIMP) manual
Purpose: Discuss priorities
Delivery: Same as slide

## Slide 34: Transmission & Distribution Structures (cont.)
Distribution:
  The ESI calls supervisor
  The ESI or supervisor calls Distribution Operations Center (DOC)
  The ESI or supervisor provides information for report and obtains sequence number
  The ESI stands by if necessary to provide support
Notes: Reference: Distribution Inspection & Maintenance Program (DIMP) manual
Purpose: Discuss priorities
Delivery: Same as slide

## Slide 35: Vegetation Clearance – Priority 1 Conditions
For vegetation clearance issues:
  The DOC is not notified
  Instead, the ESI notifies the ODI Supervisor. It is the ODI Supervisor’s responsibility to contact the appropriate Vegetation Supervisor directly.
  NOTE: Vegetation clearance issues are 48” for primary and Transmission conductors; see the Distribution Vegetation Management Plan (DVMP)
Notes: References:
Distribution Inspection & Maintenance Program (DIMP) manual
Distribution Vegetation Management Plan (DVMP)
Purpose: Discuss vegetation clearance
Delivery: Same as slide

## Slide 36: Spills – Priority 1 Conditions
Oil Release – Oil in the environment, usually located on the side of a piece of equipment
Oil Leak – Oil release with evidence indicating that the oil is fresh (or possibly moving) and potential exists to contaminate the environment
Oil Spill – Oil has spread to the environment
  If the Priority 1 condition is due to an active oil spill, use an oil spill kit and contain the spread of oil
  Report the Priority 1 condition as required and contact the environmental specialist
Notes: Reference: Distribution Inspection & Maintenance Program (DIMP) manual
Purpose: Discuss spills
Delivery: Same as slide

## Slide 37: Annual Grid Patrols (AGP)
The Annual Grid Patrol (AGP)
  Performed by ESIs
  An evaluation of SCE’s electrical Distribution facilities
  Identifies and documents immediate safety with hazardous reliability conditions for corrective action
Because SCE does a detailed inspection of 20% of their poles each year, the AGP serves as a visual inspection of the remaining 80% of the poles for Priority 1 conditions
Notes: Reference: Distribution Inspection & Maintenance Program (DIMP) manual
Purpose: Discuss AGPs
Delivery: Same as slide

## Slide 38: Annual Grid Patrols (AGP) (cont.)
The AGP checks the condition of:
  Equipment, apparatus, and hardware
  Poles and structures
  Conductors
  Risers
The ESI performs a visual inspection of overhead electrical distribution facilities. This inspection includes the entire primary system and all publicly accessible overhead and underground assets to identify obvious safety and reliability items on both the primary and secondary areas.
Notes: Reference: Distribution Inspection & Maintenance Program (DIMP) manual
Purpose: Discuss AGPs
Delivery: Same as slide

## Slide 39: Annual Grid Patrols (AGP) (cont.)
The AGP is done on all the poles that do not receive an annual detailed inspection
This is a quick inspection from a vehicle or on foot using binoculars where the ESI identifies hazards and discrepancies according to the Grid Patrol Checklist in the DIMP
Notes: Reference: Distribution Inspection & Maintenance Program (DIMP) manual, see Attachment 2-1: Grid Patrol Guidelines
Purpose: Discuss AGPs
Delivery: Same as slide

## Slide 40: Module Wrap Up
Explain the purpose and duties regarding a Detail Inspection
Discuss the Distribution Assets that are inspected
Discuss the steps of the inspection method
Describe priority assignments
Describe the differences between Transmission & Distribution reporting
Describe P1 conditions relating to spills and vegetation
Explain the purpose of the Annual Grid Patrol (AGP)
Notes: References:
Distribution Inspection & Maintenance Program (DIMP) manual
Distribution Vegetation Management Plan (DVMP)
Purpose: Module wrap up
Delivery:
Discuss what was covered during the module
Emphasize critical points and mistakes/issues commonly made in the field
Ask for follow up questions

## Slide 41: Check Your Knowledge
Name at least 5 Distribution assets that are subject to ODIs.
List 4 duties for a Detail Inspection.
List the 3 ODI performance priorities.
Should ESIs use binoculars when conducting inspections?
Notes: Delivery:
Engage students in a discussion
Discuss the “why” for each answer (e.g., discuss why the 3 ODI performance duties are safety, quality, and productivity)
Answers:
Poles
Crossarms
Insulators
Fuses
Transformers
Conductors
Regulators
Visible wires
Cables
Identifying discrepancies
Rating and recording conditions
Performing minor corrective action
Documenting priority rated safety and reliability conditions
Safety, Quality, & Productivity
Yes
Please make note that because everyone does it differently, this may get multiple answers

## Slide 42: Check Your Knowledge (cont.)
What is the first thing an ESI does when he finds a Priority 1 condition?
What is the time frame for repairs for a Priority 1 condition?
What is the time frame for repairs for a Priority 2 condition?
Explain the AGP process.
Notes: Delivery:
Engage students in a discussion
Discuss the “why” for each answer (e.g., discuss why the 3 ODI performance duties are safety, quality, and productivity)
Answers:
Assess the situation for safety and call the supervisor
Within 24 hours
Within 24 months
The AGP is done on all the poles that were not scheduled for an annual detailed inspection
This is a quick inspection from a vehicle or on foot using binoculars where the ESI identifies hazards and discrepancies according to the Grid Patrol Checklist for Priorities 1 and 2

## Slide 43: End of Detail Inspection Module