## Glossary
Glossary
Risk Reduction Effectiveness | The percentage of total risk reduced by this mitigation if applied across entire wildfire risk as determined by MAV-F score. Its understood that drivers across territory may be different so this number could vary on a circuit by circuit basis. This mitigation effectiveness is expected to be the "average" for the wildfire risk MAV-F score.
Ignition Reduction Effectiveness | The percentage of expected ignitions reduced by this mitigation (some IOUs call this "ignition likelihood"). Its understood that drivers across territory may be different so this number could vary on a circuit by circuit basis. This mitigation effectiveness is expected to be the "average" for the entire HFTD.
Explanation of Difference in Effectiveness | Brief explanation of why Risk Reduction Effectivenss versus Ignitions reduction effectiveness are not the same. Example: "This mitigation is less effective at reducing vegetation igntions which contribute more to the wildfire risk than other ignitions types"
Applicable Scope | Scope of mitigation. Three possible answers are "selected circuits," "territory-wide" or "HFTD-wide."
Useful Life | Useful life of mitigation. For some mitigations that do not have a useful life, please use NA.
RSE (average) | Average Risk Spend Efficiency across HFTD. Please note if using HFRA.
RSE (top 20%) | Risk Spend Efficiency Across top 20% of risk
Cost | Total Cost per year 2022-2026
Cost per Mile | Cost per mile for mitigation

## Data Input
Mitigation | SCE WMP ID | Risk Reduction Effectiveness [4] | Ignition Reduction Effectiveness | Explanation of Difference in Effectiveness | Applicable Scope | Useful Life | RSE (average)[7] | RSE (top 20%) [8] | Estimate Cost ($000) 2022-2026 [9] [10] [11] | Cost ($000) per Mile
Asset Inspections [1] | N/A | N/A | N/A | N/A | Territory | N/A | N/A | N/A | N/A | SCE does not calculate this as the program is designed based on inspections, not miles.
Asset Inspections Above GO 165 Inspections* | See Asset Inspection tab | 2.2% [5] | 8.28% [5] | See Asset Inspections tab | HFRA | N/A | 704.2335 | 1168.4581 | 798184.1497 | SCE does not calculate this as the program is designed based on inspections, not miles.
Vegetation Management [1] | N/A | N/A | N/A | N/A | Territory | N/A | N/A | N/A | N/A | SCE does not calculate this as the program is designed based on inspections, not miles.
Vegetation Management Above Routine Vegetation Management** | See VM Inspection Tab | .02% [5] | 1% [5] | See Asset Inspections tab | HFRA | N/A | 27.2152 | 28.6681 | 235484.6987 | SCE does not calculate this as the program is based on grids, not miles.
Fast Trip and associated programs | SH-5 and SH-6 | 0.16% | 0.113% | Risk Reduction Effectiveness takes into account the wildfire consequences. Ignition Reduction Effectiveness focuses on the ignition and disregards the consequence impact of where the ignition occurs. | Selected Circuits | N/A | 5477.5876 | 8584.9086 | 16331 | SCE does not calculate this as the program is based on grids, not miles.
PSPS [2] | N/A | N/A | N/A | N/A | Selected Circuits | N/A | N/A | N/A | N/A | N/A
Undergrounding | SH-2 | 1.57% | 1.16% | Risk Reduction Effectiveness takes into account the wildfire consequences. Ignition Reduction Effectiveness focuses on the ignition and disregards the consequence impact of where the ignition occurs. | Selected Circuits | 45 yrs | 1376.6781 | 4866.1909 | 405937 | 4460.8462
Covered Conducrtor | SH-1 | 27.96% | 25.2% | Risk Reduction Effectiveness takes into account the wildfire consequences. Ignition Reduction Effectiveness focuses on the ignition and disregards the consequence impact of where the ignition occurs. | Selected Circuits | 45 yrs | 4069.7965 | 14163.2247 | 2364032 | 727.3945
Rapid Earth Fault Current Limiter (REFCL) [3] | SH-17, SH-18 | 5.269% | 1.964% | Risk Reduction Effectiveness takes into account the wildfire consequences. Ignition Reduction Effectiveness focuses on the ignition and disregards the consequence impact of where the ignition occurs. | Selected Circuits | 40 yrs | 42523.868 | 155309.0361 | 102718 | 68.433
SPD recognizes that each utility is performing inspections that greatly exceed regulatory minimum. The goal of this is better understand how each IOU's programs impact its total risk reduction.
* See Tab: Asset Inspections
** See Tab: VM Inspections
Note: All values are for 2023-2025.
[1] For the WMP, SCE did not calculate risk reduction for compliance activities, as these activities must be completed and are not incremental due to wildfire.
[2] SCE did not evaluate PSPS as a mitigation to wildfire.
[3] RSE values are for SH-17 only. SCE did not calculate an RSE value for SH-18.
[4] To calculate the Risk Reduction Effectiveness, SCE is using the risk reduction from RSE calculations.
[5] Value is the average from the Asset Inspection tab.
[6] Value is an average from the VM Inspection tab.
[7] Value is the average RSE over 2023-2025.
[8] Value is the RSE of the top 20% of the riskiest assets in scope for the mitigation.
[9] To be consistent with SCE's 2023-2025 WMP submission, the estimated cost is only for the 2023-2025 period.
[10] SCE excluded foundational costs (IT, etc.) associated with each mitigation to determine the estimated cost.
[11] Esitmated costs include only those activities where SCE calculated risk reduction effectiveness.

## Asset Inspections
Asset Inspections Above GO 95/165/167 Inspections | SCE WMP ID | IOU | Risk Reduction Effectiveness [2] | Ignition Reduction Effectiveness | Explanation of Difference in Effectiveness
Distribution Detailed Overhead Conductor Inspections | IN-1.1 | ALL | 2.1% | 8.05% | Risk Reduction Effectiveness takes into account the wildfire consequences. Ignition Reduction Effectiveness focuses on the ignition and disregards the consequence impact of where the ignition occurs.
Distribution Infrared Inspections | IN-3 | ALL | 6.296e-06% | 0.0001185% | Risk Reduction Effectiveness takes into account the wildfire consequences. Ignition Reduction Effectiveness focuses on the ignition and disregards the consequence impact of where the ignition occurs.
Distribution Wood Pole Intrusive Inspections | N/A | ALL | N/A | N/A | N/A
Distribution Overhead Patrol Inspections | See IN-1.1 | ALL | N/A | N/A | N/A
Transmission Detailed Overhead Conductor Inspections | IN-1.2 | ALL | 0.08122% | 0.1897% | Risk Reduction Effectiveness takes into account the wildfire consequences. Ignition Reduction Effectiveness focuses on the ignition and disregards the consequence impact of where the ignition occurs.
Transmission Infrared Inspections | IN-4 | ALL | 7.211e-06% | 2.058e-05% | Risk Reduction Effectiveness takes into account the wildfire consequences. Ignition Reduction Effectiveness focuses on the ignition and disregards the consequence impact of where the ignition occurs.
Transmission Wood Pole Intrusive Inspection | N/A | ALL | N/A | N/A | N/A
Transmission Overhead Patrol Inspection | See IN-1.2 | ALL | N/A | N/A | N/A
Substation Patrol Inspections [1] | N/A | ALL | N/A | N/A | N/A
Generation Inspections | IN-5 | SCE | 0.00264% | 0.03084% | Risk Reduction Effectiveness takes into account the wildfire consequences. Ignition Reduction Effectiveness focuses on the ignition and disregards the consequence impact of where the ignition occurs.
Transmission Conductor and Splice Assessments | IN-9A, IN-9B | SCE | 0.01261% | 0.004406% | Risk Reduction Effectiveness takes into account the wildfire consequences. Ignition Reduction Effectiveness focuses on the ignition and disregards the consequence impact of where the ignition occurs.
Note: All values are for 2023-2025.
[1] See SCE WMP Section 8.1.3.10
[2] To calculate the Risk Reduction Effectiveness, SCE is using the risk reduction from RSE calculations.

## VM Inspections
Vegetation Management Above Routine Vegetation Management | SCE WMP ID | IOU | Risk Reduction Effectiveness [3] | Ignition Reduction Effectiveness | Explanation of Difference in Effectiveness
Distribution Vegetation Management Plan (DVMP) (Routine Line Clearing) [1] | N/A | SCE | N/A | N/A | N/A
Transmission Vegetation Management Plan (TVMP) (Routine Line Clearing) [1] | N/A | SCE | N/A | N/A | N/A
Hazard Tree Management Plan (HTMP) | VM-1 | SCE | 0.01107% | 0.6842% | Risk Reduction Effectiveness takes into account the wildfire consequences. Ignition Reduction Effectiveness focuses on the ignition and disregards the consequence impact of where the ignition occurs.
Dead and Dying Tree Removal | VM-4 | SCE | 0.006935% | 0.2911% | Risk Reduction Effectiveness takes into account the wildfire consequences. Ignition Reduction Effectiveness focuses on the ignition and disregards the consequence impact of where the ignition occurs.
LiDAR [2] | VM-9 | SCE | N/A | N/A | N/A
Note: All values are for 2023-2025.
[1] For the WMP, SCE did not calculate risk reduction for compliance activities, as these activities must be completed and are not incremental due to wildfire.
[2] SCE did not calculate an RSE value for this activity.
[3] To calculate the Risk Reduction Effectiveness, SCE is using the risk reduction from RSE calculations.