## Sheet1
Confirmed Reportable Ignition Events | Primary Overhead Ignitions in HFRA |  |  |  | Average ignitions per year | Average % ignitions per year | Covered Conductor Mitigation Effectiveness (including Fire-Resitant Poles) (1)
Subdriver Type | 2015 | 2016 | 2017 | 2018 | 2015-2018 | 2015-2018
Veg. contact- Distribution | 6 | 5 | 8 | 4 | 5.75 | 15.75% | 71%
Animal contact (includes bird nests)- Distribution | 7 | 5 | 2 | 4 | 4.5 | 12.33% | 65%
Balloon contact- Distribution | 2 | 3 | 10 | 9 | 6 | 16.44% | 99%
Vehicle contact- Distribution | 3 | 2 | 2 | 7 | 3.5 | 9.589% | 82%
Other contact from object - Distribution | 2 | 4 | 3 | 0 | 2.25 | 6.164% | 77%
Wire-to-wire contact / contamination- Distribution | 1 | 0 | 1 | 2 | 1 | 2.74% | 99%
Anchor / guy damage or failure - Distribution | 0 | 0 | 0 | 0 | 0 | 0% | 0%
Conductor damage or failure — Distribution | 2 | 4 | 0 | 4 | 2.5 | 6.849% | 90%
Connection device damage or failure - Distribution | 2 | 4 | 1 | 0 | 1.75 | 4.795% | 90%
Crossarm damage or failure - Distribution | 0 | 0 | 1 | 0 | 0.25 | 0.6849% | 50%
Fuse damage or failure - Distribution | 0 | 1 | 0 | 0 | 0.25 | 0.6849% | 2%
Insulator and brushing damage or failure - Distribution | 1 | 2 | 2 | 1 | 1.5 | 4.11% | 90%
Lightning arrestor damage or failure- Distribution | 0 | 0 | 0 | 0 | 0 | 0% | 0%
Other - Distribution | 1 | 3 | 1 | 2 | 1.75 | 4.795% | 14.52%
Pole damage or failure - Distribution | 0 | 0 | 0 | 0 | 0 | 0% | 0%
Recloser damage or failure - Distribution | 0 | 0 | 0 | 0 | 0 | 0% | 5%
Voltage regulator / booster damage or failure - Distribution | 0 | 0 | 0 | 0 | 0 | 0% | 0%
Capacitor bank damage or failure- Distribution | 0 | 0 | 0 | 0 | 0 | 0% | 0%
Switch damage or failure- Distribution | 0 | 0 | 0 | 1 | 0.25 | 0.6849% | 2%
Transformer damage or failure - Distribution | 1 | 1 | 1 | 1 | 1 | 2.74% | 20%
Sectionalizer damage or failure - Distribution | 0 | 0 | 0 | 0 | 0 | 0% | 0%
All Other- Distribution | 2 | 0 | 1 | 0 | 0.75 | 2.055% | 0%
Contamination - Distribution | 0 | 0 | 0 | 0 | 0 | 0% | 0%
Utility work / Operation - Distribution | 0 | 0 | 0 | 0 | 0 | 0% | 0%
Vandalism / Theft - Distribution | 0 | 0 | 0 | 0 | 0 | 0% | 0%
Unknown - Distribution | 6 | 2 | 3 | 3 | 3.5 | 9.589% | 65.32%
Total Mitigation Effectiveness | [6 empty] | 72.85%
(1) Mitigation effectiveness values are based on Subject Matter Expert (SME) judgement on the ability for covered conductor + FR pole to address each risk driver. SME judgement was informed by benchmarking, analysis, and testing.