## Ignitions_CC on structure
Utility Name | Fire Start |  | Location |  |  |  | Fire |  |  | Utility Facility |  |  |  |  | Outage |  |  | Field Observation |  |  |  |  | CC Installed Before or After 2017 | Ignition Secondary/Service Lines | Secondary/Service Covered | Ignition Device Connected to CC | Ignition Key Learning | Exemption Status as of 2025
| Date | Time | Latitude | Longitude | Material At Origin | Land Use at Origin | Size | Suppressed By | Suppressing Agency | Facility Identification | Other Companies | Voltage (KVolts) | Equipment Involved With Ignition | Type | Was There an Outage | Date | Time | Suspected Initiating Event | Equipment /Facility Failure | Contact From Object | Facility Contacted | Contributing Factor
SCE | 2022-02-15 | 20:40 | 34.4036 | -119.4719 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Carpinteria Fire Department | OH-4129624E | None | 16 | Conductor | Overhead | Yes | 2022-02-15 | 21:25 | Contact From Object |  | Vegetation | Electric Facility | Unknown | After | No | N/A | No | Tree fell and pull 1/0ATW out of dead-end insulators. Started the ignition. | Exempt
SCE | 5/29/24 | 17:24 | 33.9399 | -116.6176 | Vegetation | Rural | Less Than .25 Acres | Self-extinguished |  | OH-4114811E | None | 12 | Other | Overhead | Yes | 5/29/24 | 17:24 | Equipment/Facility Failure | Connector |  |  | Unknown | After | No | N/A | Yes | Jumper connection failed, melted connector and bird guard. | Exempt
SCE | 6/26/24 | 07:15 | 35.1383 | -118.4906 | Vegetation | Urban | Less Than .25 Acres | Customer |  | OH-4009797E | BRIGHT HOUSE NETWORKS | 12 | Other | Overhead | No | N/A | N/A | Contact From Object |  | Animal | Electric Facility | Unknown | After | No | N/A | Yes | Bird landed on top phase of secondary connector and pushed it into neutral. | Exempt
SCE | 2021-09-05 | 12:54 | 34.2645 | -118.947 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-2177032E | AT&T California | 16 | Conductor | Overhead | No | N/A | N/A | Equipment/Facility Failure | Conductor |  |  | Other | After | Yes | Yes | No | Service conductor likely overloaded causing a WD. Started ground fire. | Exempt
SCE | 2024-09-08 | 11:29 | 34.2501 | -119.0331 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Ventura County Fire Department | OH-1500442E | None | 16 | Other | Overhead | No | N/A | N/A | Contact From Object |  | Vegetation | Electric Facility | Unknown | After | Yes | Yes | No | OH service splice failed, caused sparks to come down and started ground fire. | Exempt
SCE | 2023-10-26 | 16:44 | 33.9807 | -117.0503 | Vegetation | Rural | Less Than .25 Acres | Fire agency | Riverside County Fire Department | OH-4331309E | FRONTIER | 12 | Lightning Arrestor | Overhead | Yes | 2023-10-26 | 14:44 | Equipment failure | Lightning Arrester |  |  | Unknown | After | No | N/A | Yes | Failure at LA connection. Incandescent particles came down and started ignition. | Non-Exempt
SCE | 3/10/24 | 22:32 | 34.391 | -117.6093 | Vegetation | Rural | Less Than .25 Acres | Fire agency | San Bernardino County Fire Department | OH-2341991E | None | 12 | Other | Overhead | Yes | 3/10/24 | 22:32 | Equipment/Facility Failure | Pole |  |  | Weather | After | No | N/A | Yes | Erosion caused anchor anchor pulled out, caused pole to snap | Non-Exempt
SCE | 7/18/24 | 22:52 | 34.4699 | -118.1959 | Vegetation | Rural | Less Than .25 Acres | Fire agency | Los Angeles County Fire Department | OH-4429426E | None | 12 | Other | Overhead | Yes | 7/18/24 | 22:52 | Contact From Object |  | Vehicle | Pole | External Force | After | No | N/A | Yes | Car hit pole with capacitor bank on ground, resulted in a ground fire. | Non-Exempt
SCE | 2024-10-10 | 13:29 | 34.2572 | -117.0953 | Vegetation | Rural | Less Than .25 Acres | Self Extinguished |  | OH-1763305E | None | 12 | Transformer | Overhead | Yes | 10/10/24 | 13:29 | Lightning |  |  |  | Outside Force | After | No | N/A | Yes | Lightning struck OH transformer, blew lid, bushings, caused spot fire. | Non-Exempt
SCE | 2021-06-15 | 16:14 | 33.6638 | -116.9722 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Hemet Fire Agency | OH-4163014E | Frontier Communications | 12 | Conductor | Overhead | No | N/A | N/A | Vandalism/Theft |  |  |  | Other | After | Yes | Yes | No | Energy theft behind meter for growing operation. Service overloaded, parted and started small brush fire. | Non-Exempt
SCE | 2022-09-28 | 15:39 | 34.452 | -119.2342 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Ventura County FD | OH-4413379E | AT&T California | 16 | Conductor | Overhead | Yes | 2022-09-28 | 15:30 | Contact From Object | Conductor | Vegetation | Electric Facility | Outside Force | After | Yes | Yes | No | large tree fell into overhead span of secondary conductor resulting pole base fire. | Non-Exempt
SCE | 6/4/24 | 14:33 | 34.7616 | -118.7456 | Vegetation | Highly Rural | .26 - 9.99 Acres | Fire agency | U.S. Forest Service | OH-4650087E | None | 12 | Conductor | Overhead | Yes | 6/4/24 | 14:33 | Vandalism/Theft |  |  |  | Unknown | After | Yes | Yes | No | Suspected grow house overloaded secondary, causing secondary and service to come down. Resulted in ground fire | Non-Exempt
SCE | 7/10/24 | 10:59 | 33.7993 | -117.0744 | Vegetation | Rural | Less Than .25 Acres | Fire agency | Riverside County Fire Department | OH-1623579E | None | 12 | Conductor | Overhead | Yes | 7/10/24 | 10:59 | Contact From Object |  | Vegetation | Electric Facility | External Force | After | Yes | Yes | No | Service wire down likely due to vegetation abrasion over time that resulted in ground fire. | Non-Exempt
SCE | 2024-07-24 | 13:20 | 33.6707 | -117.2108 | Vegetation | Unknown | Less Than .25 Acres | Customer |  | OH-4978055E | None | 12 | Other | Overhead | No | N/A | N/A | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | After | Yes | Yes | Yes | service wire down likely due to preform splice failure. Resulted in grass fire. | Non-Exempt
SCE | 2022-02-04 | 10:51 | 34.3151 | -118.8966 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Ventura County Fire Department | OH-679512E | AT&T California | 16 | Conductor | Overhead | Yes | 2022-02-04 | 9:35 | Contact From Object |  | Vegetation | Electric Facility | Weather | After | No | N/A | No | Tree fell and took down 2 span 3 phases of 1/0ATW. Tree was the only thing caught on fire. | Unknown
SCE | 3/3/24 | 23:36 | 34.4353 | -118.3921 | Vehicle | Rural | Less Than .25 Acres | Fire agency | Los Angeles County Fire Department | OH-1790725E | TIME WARNER CABLE | 16 | Conductor | Underground | Yes | 3/3/24 | 23:36 | Contact From Object |  | Vehicle | Pole | External force | After | No | N/A | No | Car hit primary riser, both caught fire. | Unknown
SCE | 3/17/24 | 17:41 | 33.8011 | -117.1607 | Vegetation | Rural | Less Than .25 Acres | Fire agency | Riverside County Fire Department | OH-2113230E | TIME WARNER CABLE | 12 | Conductor | Overhead | Yes | 3/17/24 | 17:41 | Contact From Object |  | Other | Electric Facility | Weather | After | No | N/A | Yes | Lightning struck CC at insulator and caused it to fall down. | Unknown
SCE | 5/4/24 | 08:58 | 35.111 | -118.6194 | Vegetation | Rural | Less Than .25 Acres | Self-extinguished |  | OH-4010161E | None | 12 | Transformer | Overhead | Yes | 5/4/24 | 08:58 | Contact From Object |  | Animal | Electric Facility | Unknown | After | No | N/A | Yes | Bird nest on transformer bank caused fire. | Unknown
SCE | 5/16/24 | 09:30 | 34.4769 | -118.1362 | Vegetation | Rural | Less Than .25 Acres | Utility |  | OH-4187443E | None | 12 | Transformer | Overhead | No | N/A | N/A | Contact From Object |  | Animal | Electric Facility | External force | After | No | N/A | Yes | Bird nest on transformer bank caused fire. | Unknown
SCE | 5/23/24 | 14:13 | 34.3152 | -118.959 | Vegetation | Rural | Less Than .25 Acres | Self-extinguished |  | OH-1709216E | None | 16 | Fuse | Overhead | Yes | 5/23/24 | 14:13 | Equipment/Facility Failure | Fuse |  |  | Unknown | After | No | N/A | Yes | Melted transformer fuse bird guard caused vegetation fire. | Unknown
SCE | 6/21/24 | 09:54 | 33.8343 | -117.4933 | Vegetation | Rural | Less Than .25 Acres | Self-extinguished |  | OH-4412448E | None | 33 | Lightning Arrestor | Overhead | Yes | 6/21/24 | 09:54 | Equipment/Facility Failure | Lightning Arrestor |  |  | Human Error | After | No | N/A | Yes | Failed lightning arrestor | Unknown
SCE | 2024-07-27 | 19:33 | 34.6795 | -118.433 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Los Angeles County Fire Department | OH-709052E | None | 12 | Transformer | Overhead | Yes | 7/27/24 | 19:33 | Equipment/Facility Failure | Transformer |  |  | Weather | After | No | N/A | Yes | Transformer tap broke and arced into fuse cutout, resulted in vegetation fire. | Unknown
SCE | 2024-07-31 | 13:30 | 34.4356 | -117.5516 | Vegetation | Rural | Less Than .25 Acres | Self Extinguished |  | OH-2171072E | None | 12 | Fuse | Overhead | Yes | 7/31/24 | 13:30 | Contact From Object |  | Balloons | Electric Facility | Outside Force | After | No | N/A | Yes | Mylar balloon got across fuse holder tap and ground. | Unknown
SCE | 2024-11-09 | 15:44 | 33.9697 | -116.9031 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Riverside County Fire Department | OH-356425S | None | 12 | Other | Overhead | Yes | 11/9/24 | 15:44 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | After | No | N/A | Yes | secondaries are melted at the pole top connection, incandescent particle started the vegetation fire. | Unknown
SCE | 2024-12-01 | 09:33 | 34.3708 | -118.5599 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-1693555E | TIME WARNER CABLE | 16 | Lightning Arrestor | Overhead | Yes | 12/1/24 | 09:33 | Contact From Object |  | Animal | Electric Facility | Outside Force | After | No | N/A | Yes | Squirrel got under the lightning arrestor's cap and tracked to LA's mounting bracket. Incandescent particle caused spot fire | Unknown
SCE | 2022-01-09 | 16:10 | 34.1737 | -118.0436 | Building | Urban | Less Than .25 Acres | Fire Agency | Duarte FD | OH-4209491E | Frontier Communications | 4 | Conductor | Overhead | No | N/A | N/A | Contact From Object |  | Animal | Electric Facility | Outside Force | After | Yes | Yes | No | Squirrel chewed service conductor causing WD started a shed on fire. | Unknown
SCE | 2023-10-29 | 18:39 | 34.2566 | -118.6419 | Vegetation | Rural | Less Than .25 Acres | Fire agency | Ventura County Fire Department | OH-3004910E | AT&T CALIFORNIA | 16 | Conductor | Overhead | Yes | 2023-10-29 | 13:52 | Equipment failure | Conductor |  |  | Weather | After | Yes | Yes | No | secondary conductor faulted mid-span due to age/weathering/wind flexing. Phase arced to neutral, causing sparks to start ground fire. Root cause: Probable cause behind the 4/0AQ damage appears to be friction caused from contact with the customer's service wire. The contact/rubbing penetrated the covering of the phase. This resulted in arcing/melting of the aluminum and steel strands. | Unknown
Note on AB1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Phu Pham - is this a direct download or was it edited? And is AA something you added or was it there before? Reply: AA was original there. I added AB & AC. AD was from Kevin Arlic.