## Notes
Notes (Numbering refers to column where note is used)
General Note | Please see SCE's Cover Letter included with the Stakeholder Review Process (SRP) submission for additional description/ information about process and data
General Note | Program Blankets represent a group of smaller projects that can be aggregated from an operational and accounting perspective. Program Blankets do not have their own project data, such as location, age, status, dates, etc. Wherever data fields are not applicable at the Program Blanket level, SCE states "Not applicable at program level"
1A | SCE has provided a unique SRP ID for each line item to facilitate review of the spreadsheet: “PB” is an abbreviation for “Program Blanket” and “SP” is an abbreviation for “Specific Project.” Program Blankets represent capital expenditures for routine work with no specific planned in-service date that can be grouped together from an operational and accounting perspective. Specific Project work orders represent unique capital expenditure activities that are carried out as individual projects with a planned in-service date (i.e., SP-XX). “PB” line numbers without a decimal following the initial number are used for rows containing the program forecast for the entire blanket (i.e., PB-XX). SCE has also used bold font for these Program Blanket headers for ease of reference. “PB” line numbers with a decimal following the initial number are for individual projects that fall under their respective blanket and capture specific costs incurred (i.e., PB-XX.XX).
3A | For Program Blankets that include projects that span several locations, SCE states "Not applicable at program level"
3B | Internal Orders (IO's) - Utility Unique ID #1 (work order) are for Monthly Capital Order; therefore, project is treated similarly to a "program blanket"
8A | Operationally dependent for this purpose is defined as those projects that are bundled together to achieve efficiencies with design and construction or are related due to interdependencies (e.g., interconnection, deliverability, shared equipment, etc.). Constructed in tandem means project construction work/ schedule were directly dependent on one another or outages at one project were leveraged to perform work on another project. Projects that were constructed during the same timeframe, but are not dependent on one another are not considered related, so are not included. Importantly, SCE is only identifying related projects within the SRP Project Spreadsheet, and is not including all projects that could be considered related (e.g., CPUC-jurisdiction).
11A | GO 174 mandates substation inspections and requires that anomalies be addressed. According to the SC&M GO 174 Program, each substation will be inspected at least five (5) times annually. Grid Operations is responsible for performing these inspections. Documented anomalies are handled through SAP notifications created by Grid Operations via their field tool/SAP. These anomalies must be prioritized and addressed either immediately by Grid Operations or within a prescribed time frame by SC&M.
13A | For the purposes of this response, SCE interprets “NERC, WECC, or CAISO contingencies” to refer to NERC TPL 001-4 Reliability Standards, WECC Regional Reliability Criterion, or CAISO Planning Standards. Where projects are not subject to these analyses, SCE indicates any type of analysis performed to inform the need for the project.
14A | SCE monitors and maintains equipment to repair and prolong the life cycle. The primary alternative to this project would be to run the asset to failure. Because this presents safety and reliability risks to our employees, contractors, and the public, SCE does not deem this to be a prudent alternative. SCE may consider various alternatives related to the timing of asset replacement; for example, to advance or delay replacement considering the bundling of work for outages purposes, or to prioritize the highest or most emergent risks. Further details on this determination can be found in the Program Manual as provided in SCE’s SRP 12/1/20 (see (PUBLIC) SCE SRP_Dec 2020_SUB IR & Main Program_PB-05-PB-06, PB-11, PB-13-PB-19, PB-29.pdf)
16A | Program is primarily intended to mitigate wildfire risk and is identified as one of SCE's WMP activities
16B | Program is not primarily intended to mitigate wildfire risk but may have incidental or indirect wildfire-related benefits
16C | Program is not primarily intended to mitigate wildfire risk and has no discernable wildfire-related benefits
16D | Program is intended to repair or restore damage due to wildfire
17A | Electrical infrastructure and assets such as those addressed in this program/project can be adversely impacted by a variety of environmental factors, including but not limited to: temperature extremes, proximity to coastal environments, air particulate levels, wind, climate change, corrosive materials, and other environmental factors. Where applicable and known, SCE identifies conditions specific to the location of the project that may impact the asset(s). Environmental factors listed generally reflect best known information from project manager.
18A | While SCE is providing the name of a Project Manager for each project, SCE respectfully requests that any inquiries regarding this response be directed to Ainsley Carreno (ainsley.carreno@sce.com) who can facilitate a response to the inquiry, rather than the specific Project Manager listed.
19A | TLRR projects focus on structure work and do not involve transmission lines. SCE is providing the length of circuit miles that the towers cover, measured by the distance between the two furthest-most towers being addressed.
19B | Project does not include new transmission lines, or the length of new lines is minimal (e.g. may include reconfiguration of existing lines)
20A | For projects primarly involving work with a substation, SCE provides the footprint of the entire substation in which this project is occurring.
20B | Project primarily involves linear assets (transmission / telecomm lines) and/ or involves minimal or no work within a substation
21A | Program Blanket or Project does not include new transmission lines.
22A | Project primarily involves linear assets (transmission / telecomm lines) and/ or involves minimal or no work within a substation
23A | SCE does not have a utility-wide quantitative mechanism that scores and prioritizes all projects. However, many programs have prioritization methods applicable to projects within the program. In these cases, SCE provides a description of how work is prioritized within a program. While SCE does not have a utility-wide prioritization ranking system, please see tab "Supplement-Part 1" for additional details on how work is identified and prioritized for this area.
23B | Utility Prioritization ranking is not applicable and/ or need and timing is primarily determined by compliance with applicable transmission planning standards, CAISO TPP approval, third party executed agreements or other contractual requirements.
24A | Only includes work orders with FERC-jurisdictional spend.
25A | Only includes CWBS with FERC-jurisdictional spend.
27A | SCE is not currently aware of material changes in unique IDs affecting this program/project, and will track and document any changes to unique IDs in future responses to this SRP.
28A | For purposes of this data request, SCE is interpreting "utility approval" as approval to spend dollars to implement a project.
28B | While program blankets are reviewed and approved annually through the Annual Capital Operating Plan Process, they are not addressed in this question pertaining to projects. That said, in cases where a new program has been established and approved through FRM/CRT during the five-year historical period, SCE has noted it.
29A | SCE has provided the year in which approval has occurred through SCE's Project Management Work Initiation Form (PMWIF) / Annual Capital Operating Plan Process, except where the project has received approval through SCE's FRM/CRT governance forum or through an LGIA. In cases where CRT/FRM approval of project cost was received or LGIA executed, SCE notes that the year of approval shown may come after internal authorization for project scoping and/or approval to file an application with the CPUC (e.g. PTC). See Supplement- Part 2 for additional information on the utility approval process.
29B | While program blankets are reviewed and approved annually through the Annual Capital Operating Plan Process, they are not addressed in this question pertaining to projects. That said, in cases where a new program has been established and approved through FRM/CRT during the five-year historical period, SCE has noted it.
30A | SCE interprets the ‘Long-Term Transmission Investment Plan’ to be SCE’s capital forecast for transmission activities. Generally speaking, SCE maintains a five-year operating plan forecast of such activities alongside forecasts for all other company activities. If the Program Blanket or Specific Project has been in place prior to 2017, which is the first year of this DR's historical period, SCE has denoted "Pre-2017".
31A | Please see supplemental discussion on utility approval process in tab "Supplement- Part 2", which describes the Annual Capital Operating Plan process, as well as corporate governance and approval of capital projects that exceed specific thresholds. SCE is interpreting "utility approval" as approval to spend dollars to implement a project.
45A | Specific Projects can consist of several work orders with their own project statuses. SCE lists the most appropriate project status for the entire project.
46A | The requested information is not available as SCE does not maintain the AACE classification for any projects. SCE recognized that it has referenced the AACE classification guideline in its past filings as a means of supporting the requests for contingency as part of the licensing process of these projects.
48A | For the purposes of this response, "In-Flight Projects" are those projects currently in construction. Those projects with incentive CWIP or projects without incentive CWIP but with an in-service date of 2022 or 2023, which have their costs trued up in the TO2024 or TO2025 formula updates, are answered as "Yes". All projects which have in-service dates in other years, and do not have incentive CWIP, are answered as "No". Blanket Specifics at the program level are answered as "Not applicable at program level".
52A | SCE provides the Original Project Costs consistent with the initial internal approval. This estimate includes both FERC and CPUC jurisdictional spend. Where a project has been approved by Capital Review Team (CRT)/ Financial Risk Management Committee (FRM), SCE provides the associated costs; for all other projects, SCE provides the cost from the Project Management Work Initiation Form (PMWIF). For Programmatic Projects, Original Costs reflect the Work Order (WO) level costs. For Specific Projects, Original Costs reflects the PIN level costs (i.e., total project costs), which includes all project work orders and elements (i.e., including non-FERC elements, such as IT/Tel). SCE provides the source of the Original Project Cost in the Notes (Column 64), as well as indicates where costs are not verified with supporting documentation. Within the notes, SCE captures any deviations from this methodology or additional information, as appropriate.
52.1A | SCE is providing the FERC/CPUC split as provided in the 2023 "Spring Refresh" as the most current (and therefore accurate) split known at the time. SCE revises the jurisdictional split as project details emerge. As such, these jurisdictional splits can change over time. Where FERC percentage is not available, SCE indicates that in the Notes (Column 64).
53A | There are no cost caps for any of the items contained in this response. Further, SCE is unaware of any cost caps applicable to any of the projects or other items included in this response, either under California law, or any other applicable laws. The only cost caps that SCE is aware of and which could be imposed on any such projects would be pursuant to a successful FERC Order 1000 bid, should one be made with a specific cost cap. None of the projects noted in this response were based upon a successful FERC Order 1000 bid containing a specific cost cap. As such, cost caps do not apply to any projects or other items contained within this response.
54A | For Blanket-Specific Programs or Program Blankets, Current Projected Total or Actual Cost is direct capital expenditures only from Projected Capital Expenditures only (refer to Col. 55 & Note 55A).
54B | For Specific Projects, Current Projected Total or Actual Final Cost includes costs beyond the Recorded Period and/or Forecast Period of this information submission, where applicable. For Programmatic Projects, Current Projected Total or Actual Final Cost includes costs beyond the Recorded Period and/or Forecast Period of this information submission only to the extent that it is relied upon in SCE’s Five-Year Plan. For Programmatic Projects whose Projected Capital Expenditure that is not relied upon SCE's Five-Year Plan, Current Projected Total or Actual Final Cost is the fully loaded from the Recorded Period only.
55A | For Blanket-Specific Program or Program Blanket forecasts, SCE provides the forecast at the program level for the 5-year Forecast Period.
56A | For Specific Projects and Programmatic Projects, Actual Capital Expenditures include costs beyond the four-year Recorded Period of this data request.
57A | Project not subject to CAISO competitive solicitation.
59A | Cost-Benefit Analysis is only performed by the CAISO for Economic Projects and was not performed for this project.
60A | Blanket-Specific Programs or Program blankets without - Utility Unique ID #1 (Work Order Number) do not have CWIP balance at program level.

## Dec 2023 Data
SCE Stakeholder Review Process - Dec 1, 2023
| Project Description | [19 empty] | Project Description (Cont.) | [6 empty] | Utility/CAISO Approval and FERC Rate Cases | [9 empty] | CPUC Permit Status | [6 empty] | Project Status | [6 empty] | Costs | [24 empty] | Notes
0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 52.1 | 53 | 54 | 55.2023 | 55.2024 | 55.2025 | 55.2026 | 55.2027 | 55.Thereafter | 55 | 56.Prior | 56.2019 | 56.2020 | 56.2021 | 56.2022 | 56 | 56.1 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64
AB970 Identification of GIDAP/ TPP Projects | SRP ID | Include Project Name at date of report filing (identify all prior names of the project) | Latitude and Longitude (in decimal degrees) | City/Cities and County/counties | General project overview: what, where, and why. Discuss all assets to be installed and include all capacities (MVA) and voltages (kV). | Transmission line (new, reconductor, relocation), substation (breaker, transformer relay protection), etc. (provide list of all categories) | New, replacement, upgrade, etc. (provide list of all categories) | Identify all other projects in the spreadsheet that are operationally dependent on this project or vice versa and/or will be constructed in tandem with this project. | Select from the following to indicate the primary purpose of the project: Capacity Increase, Emergency Replacement, Infrastructure Enhancement, Infrastructure Replacement, Operations Support, Security, Work Requested By Others, or Other (if Other, include explanation in the "Notes" data field). | Select from the following applicable secondary purpose(s) of the project, which include but are not limited to: 3rd Party Damage, Age/Condition, Age/Condition - 230/115/70/60 kV Relay Replacement, Age/Condition - 500 kV Relay Replacement, Age/Condition - Anti Climb Guards, Age/Condition - Insulator Replacement - Steel, Age/Condition - Insulator Replacement - Wood, Age/Condition - Raptor Protection - Steel, Age/Condition - Replace 230/115/70/60 kV Breakers, Age/Condition - Replace 230/115/70/60 kV Transformers, Age/Condition - Replace 500 kV Breakers, Age/Condition - Replace 500 kV Transformers, Age/Condition - Replace Boardwalks, Age/Condition - Replace Breakers, Age/Condition - Replace Civil Structures, Age/Condition - Replace Conductor, Age/Condition - Replace Insulators, Age/Condition - Replace Other Substation Equipment, Age/Condition - Replace Other T-Line Equipment, Age/Condition - Replace Reactors, Age/Condition - Replace Relays, Age/Condition - Replace Relays, Age/Condition - Replace SCADA/RTU, Age/Condition - Replace Steel Poles, Age/Condition - Replace Switches, Age/Condition - Replace Transformers, Age/Condition - Replace Underground System, Age/Condition - Replace Wood Poles, Age/Condition - Switch Replacement - Steel, Age/Condition - Switch Replacement - Wood, Age/Condition - Targeted Relay Replacement, Age/Condition - Wood Pole Reframe, Animal Abatement, Automation, Bus Upgrade, Compliance - Remove Idle Facilities, Construct Roads/Gates/Culverts, Emergency Response - Fire Related, Emergency Response - Storm Related, Environmental, Facility Relocation, Fire Protection, Generation Interconnection, GO95 Mitigation - Steel, Install SCADA/RTU, Line Reconductoring, Line Termination, Load Interconnection, Modular Protection and Automation Control, NERC CIP Compliance, NERC Compliance - GO 95, New Substation, New T-Line, Priority 1 Steel Structure Replacement, Priority 1 Wood Structure Replacement, Protection NERC Compliance, Relay Upgrades, Replace Breakers, Replace Other Substation Equipment, Replace Transformers, Safety - Line Right of Way Access, SCADA Emergency Replacement, SCADA Switch Installation, Security Upgrades, Seismic Upgrade - Replace Conductor, Special Protection Scheme, Substation Capacity, Substation Reliability, System Design Upgrade, System Operations, Targeted Line Reliability, T-Line Capacity, T-Line Emergency, T-Line Reliability, Tools, Transformer Addition/Replacement, Underground Emergency, Voltage Conversion, Voltage Support. If the secondary purpose is to comply with a NERC, WECC, or CAISO requirement, list the standard, requirement, and/or any contingencies that are being addressed. | The last inspection of the asset being replaced or upgraded | What is the age in years of the asset being replaced or upgraded? | What types of analyses have been performed (e.g. load flow, short circuit, etc.)? List any field test and results. | What alternative solutions to this project were considered? and what were the costs associated with any alternatives? | Indicate whether the project is located in Tier 2 or Tier 3 in CPUC's High Fire-Threat Districts (HFTD) or Zone 1 in CalFire/USFS High Hazard Zone (HHZ). | Indicate whether the project is 1. related to repairing wildfire damage or 2. a measure identified in the Wildfire Mitigation Plan. If it is related to wildfires in some other way, please explain. | What environmental factors in the project's location may affect the length of the asset's service life? | Who is the person in charge of the implementation of this project? | Miles of transmission power lines included in the project. | Acres of substation footprint included in the project | Use kV for transmission power lines ratings. | Use MVA and/or kV for substations. | Using utility prioritization rank (e.g., RIPA) | Most specific (e.g. for SCE = Order Number) | Less specific (e.g. for SCE = Capital Work Breakdown Structure) | Least specific (e.g. for SCE = Project Identification Number) | If any of the Unique IDs above changed at any time, please note the date of change and the former ID. | Has utility company approved the project? Insert Yes or No. | If utility has approved the project, insert first year of internal approval. If not insert "n/a." | In what year was this project first included in the utility's long-term transmission investment plan? | If utility has approved the project, insert utility approval process for which a description has been provided to the CPUC. | Insert "Year" if approved by CAISO or insert "No". | If already considered in the CAISO TPP, indicate all of the year(s), not just the year of approval. | If not yet considered in the CAISO TPP, indicate year when it is expected to be considered in the CAISO TPP. | Insert active hyperlink to any TPP where project is considered or expected to be considered. | Insert ALL years when in any FERC rate case, any costs of this project went - or were expected to go - into ratebase. | Insert the year(s) and actual dollars included in rate base on the project for each year. This should include additional costs added to rate base in years after operation first occurred. | Include one of the following along with the corresponding date: Expected PEA Completion, PEA Deemed Complete, CEQA Draft Published, CEQA Final Published, Final Certified, TBD, N/A. | Examples include: IS/ND/MND, EIR, EIR/EIS, MND/EA/FONSI, CatEx, StatEx, no discretionary permit, Other, or N/A (If "Other" or "N/A," include explanation in the "Notes" data field.). | Examples include: CPUC, SWRCB, CSLC, Other, N/A etc. (If "Other" or "N/A," include explanation in the "Notes" data field.). | NOC Advice Letter, 851, PTC, CPCN, Other, or N/A (if Other or N/A include explanation). If Advice Letter (AL) include the number; If Application include number. | Insert "Year" if filed or insert "Not yet filed" with the expected filing date. | Insert "Approved", "Rejected", "To be Filed", "Filed and Under Review," "Other," or "N/A" (If Other or N/A, include explanation in the "Notes" data field.). | Insert Year this CPUC Status was determined. | Planning, Engineering less than 50% completed, Engineering more than 50% completed, Permitting, Construction (include percentage of construction completed), Operational, On Hold, Canceled, or Abandoned (if On Hold, Canceled, or Abandoned, include explanation in the "Notes" data field. If in Construction, please indicate percentage of completion at the time of this reporting). | The current Estimate Class in AACE International's Cost Estimate Classification System at the time of this report. | On what date did construction begin or is expected to begin? | For those projects already under construction, which will go into rate base in the current rate case or in the next rate case filing at FERC? | What was the expected in-service date when the project was first approved by the CAISO, or internally by the utility if not approved by the CAISO? This value should remain static across these reports. | As of the reporting of this dataset | If the current projected or actual in-service date varies more than six months from the original in-service date (i.e. slippage or advancement), please explain the reason for this variation. | Forecasted cost or forecasted cost range at time of CAISO, CPUC, and/or internal approval. This value can be a range of no more than $20 million for the public version of this report. For the confidential version this should be a specified amount. | FERC split ($) based on Op Plan | Insert Cost Cap on project if available, as well as the authority imposing the cost cap. This should include any maximum reasonable cost established in a CPUC proceeding. | Updated projected total or actual final cost of project. For projected cost, this value can be a range of no more than $10 million for the public version of this report. For the confidential version the projected final cost should be a specified amount. Actual cost should be the fully-loaded final cost after the entire project is operational. Operational projects and all data must remain in this report for at least 4 years. | [6 empty] | For the current year and future 4 years, provide the year-by-year forecasted capital expenditures for the project. | Actual Capital Expenditures ($000): These should be expressed year-by-year for the prior 4 years. |  |  |  |  | Fully-loaded final cost after the entire project is operational. Operational projects and all data must remain in this report for at least 4 years. | Corporate Overheads and AFUDC ($000) | Percentage (by current projected or actual cost) of project performed by outside developer having successfully bid on project, as opposed to the project being performed solely by the incumbent utility. | If the project is work requested by others, what percentage of cost has been - or is expected to be - passed onto ratepayers? If the dollar amount being passed onto ratepayers is fixed, then this number can be expressed as a dollar amount. | What is the C/B ratio if calculation performed? | Total amount of money that has been spent so far for the project through the last calendar year | List any project-specific transmission incentives granted under FERC Order No. 679. | Insert % of project cost recovered by high-voltage TAC. | Insert % of project cost recovered by low-voltage TAC. | Any additionally requested information or other needed details about the project that were not otherwise covered
GIDAP/ TPP | SRP ID | Project Name | Location 1 [See Note 3A] | Location 2 | Project Description | Project Description - What | Project Description - Action taken | Related Projects [See Note 8A] | Primary Purpose | Secondary Purpose | Last Inspection | Age of Asset | Types of Analyses [See Note 13A] | Alternative Solutions and Costs | CPUC Fire Threat Zone/Rating | Wildfire Related [See Note 16A] | Other Environmental Factors [See Note 17A] | Project Manager [See Note 18A] | Transmission Project Size (length in miles) [See Note 19A] | Substation Project Footprint (acres) [See Note 20A] | Transmission Voltage Level (kV) | Substation or Transformer Capacity (MVA and/or kV) | Utility Prioritization Code Rank (See Notes 23A & 23B) | Utility Unique ID #1 [See Note 24A] | Utility Unique ID #2 [See Note 25A] | Utility Unique ID #3 | Changes in Unique IDs [See Note 27A] | Utility Approval [See Notes 28A & 28B] | Year of Utility Internal Approval [See Note 29A & 29B] | Long term Transmission Investment Plan Inclusion [See Note 30A] | Process(es) for Utility Approval [See Note 31A] | CAISO Year | Year(s) when considered in CAISO TPP | Year when expected to be considered in CAISO TPP | Link to TPP where project has been considered, approved, and/or expected to be considered | FERC: Year(s) | FERC Dollars Rate Base ($000) | CEQA Status | CEQA/NEPA Document Type | CEQA/NEPA Lead Agency | CPUC Filing Type | CPUC Date Filed | CPUC Status | CPUC Status: Year | Project Status [See Note 45A] | AACE Class [See Note 46A] | Construction Start Date | In-Flight Projects [See Note 48A] | Original Planned In-Service Date | Current Projected or Actual In-Service Date | Reason for Change in In-Service Date | Original Projected Cost or Cost Range ($000) [See Note 52A] | FERC Split of the Original Projected Cost or Cost Range ($000) (See Note 52.1A) | Cost Cap ($000) [See Note 53A] | Current Projected Total or Actual Final Cost ($000) [See Note 54A & 54B] | 2023 | 2024 | 2025 | 2026 | 2027 | Thereafter | Projected Capital Expenditures ($000) [See Note 55A] | Prior | 2019 | 2020 | 2021 | 2022 | Actual Capital Expenditures ($000) [See Note 56A] | Corporate Overheads/ AFUDC ($000) | Percentage of Bid | Percentage of Work Requested by Others Passed onto Ratepayers | Cost-Benefit Analysis [See Note 59A] | Cost Spent on Construction Work in Progress ($000) [See Note 60A] | FERC Incentives | % Cost in High Voltage TAC | % Cost in Low Voltage TAC | Notes
N/A | PB-01 | Sylmar Convertor Station Capital Projects | 34.314, -118.493 | Not applicable at program level | Various Capital Projects corresponding to the HVDC PDCI Sylmar line which spans from the Sylmar Converter Station to the Nevada-Oregon Border. | Converter station | New/ Replace/ Repair/ Upgrade | Not applicable at program level | Other - See Notes | Other- See Notes | Performed by LADWP | Not applicable at program level | LADWP is the Operating Agent owner and driver of determining need and proposals of Capital projects, SCE performs engineering and cost analysis internally to verify need and cost validity of proposals. | Not applicable at program level | Not applicable at program level | See Note 16C | Not applicable at program level | Herbert Martinez, Substation Apparatus | Not applicable at program level | Not applicable at program level | 220 kV AC/230 kV AC/1000 kV DC | See Note 22A | See Note 23B | Not applicable at program level | CET-OT-OT-ME-313800 | 3138 | See Note 27A | Not applicable at program level | Not applicable at program level | Pre-2017 | Annual Capital Operating Plan Process, Contractual arrangement with third-party | No | N/A | N/A | N/A | Not applicable at program level | Not applicable at program level | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Not applicable at program level | See Note 46A | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 53A | Not applicable at program level | 4469.694 | 3663.695 | 925.365 | 971.633 | 1020.215 | Not Available | 11050.602 | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not applicable at program level | Not applicable at program level | See Note 57A | N/A | No project specific cost benefit performed. This activity largely performs reactive work in response to LADWP determinations. | See Note 60A | None | 100% | 0% | Column 2 & 3: This program operates in one location: 34.314, -118.493; Sylmar, Los Angeles County Column 9, 10: Varies (Work Requested by Others, Age/End of Life, Asset Condition) Column 22: 3220 MW
N/A | PB-01.01 | Sylmar/LADWP: Removal of old Sylmar Ground Return System | 34.314, -118.493 | Sylmar, Los Angeles County | Removal of the submarine portion of the old Sylmar Ground Return System | The existing Electrode line of the PDCI has been replaced to improve operation and reliability of the line. The Replacement was completed to Removal of submarine segment of the Sylmar Ground Return System (SGRS) | Removal/Replacement/Improvement | N/A | Infrastructure Replacement | Age/Condition | Performed by LADWP | 50+ years | LADWP is the Operating Agent owner and driver of determining need and proposals of Capital projects, SCE performs engineering and cost analysis internally to verify need and cost validity of proposals. | Did not perform alternative analysis because the project is initiated and being done by the Operating Agent of the PDCI (LADWP) | Tier 2 | See Note 16C | Risk of corrosion and earthquakes. | LADWP is the Operating Agent | See Note 19B | See Note 20B | See note 21A | N/A | See Note 23B | 903579416 | CET-OT-OT-ME-313803 | 3138 | See Note 27A | Yes | 2021 | 2021 | Annual Capital Operating Plan Process, Contractual arrangement with third-party | No | N/A | N/A | N/A | See Col. 37 | 2021 = 1,706 2022 = -280 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2021 | No | 2022 | 2021-12-05 | N/A | 4000 | 4000 | See Note 53A | 1426.7099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1706.2717 | -279.5617 | 1426.7099 | 0.09029 | See Note 57A | N/A | No project specific cost benefit performed. This activity largely performs reactive work in response to LADWP determinations. | 0 | None | 100% | 0% | Column 52: Represents SCE's portion of the project only (50%)- total project cost for all owners $8M
N/A | PB-02 | Pacific DC Intertie Trans Line Capital Additions | Not applicable at program level | Not applicable at program level | Replace approx. 80,000 old porcelain insulators pm ~432 miles of the PDCI with toughened glass insulators to support the planned voltage upgrade | Insulators | New/Replacement/Modification | Not applicable at program level | Infrastructure Replacement | Age/Condition | Not applicable at program level | Not applicable at program level | LADWP is the Operating Agent owner and driver of determining need and proposals of Capital projects, SCE performs engineering and cost analysis internally to verify need and cost validity of proposals. | Not applicable at program level | Not applicable at program level | See Note 16C | Not applicable at program level | Sony Mani, Grid Contract Management | Not applicable at program level | Not applicable at program level | 1000 kV DC line | See Note 22A | See Note 23B | Not applicable at program level | CET-OT-OT-ME-313801 | 3138 | See Note 27A | Not applicable at program level | Not applicable at program level | Pre-2017 | Annual Capital Operating Plan Process, Contractual arrangement with third-party | No | N/A | N/A | N/A | Not applicable at program level | Not applicable at program level | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Not applicable at program level | See Note 46A | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 53A | Not applicable at program level | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 0 | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not applicable at program level | Not applicable at program level | See Note 57A | N/A | No project specific cost benefit performed. This activity largely performs reactive work in response to LADWP determinations. | See Note 60A | None | 100% | 0% | Column 22: 3220 MW
N/A | PB-02.01 | Nevada Pacific DC Intertie Insulator Replacement | Various Locations | from CA- Nevada border to Nevada-Oregon border | Replace approx. 80,000 old porcelain insulators pm ~432 miles of the PDCI with toughened glass insulators to support the planned voltage upgrade | Insulators | New/Replacement/Modification | PB-02.02 | Infrastructure Replacement | Age/Condition | Performed by LADWP | 50 years old, originally installed in 1970 | LADWP is the Operating Agent owner and driver of determining need and proposals of Replace porcelain insulators to support voltage upgrade on PDCI projects, SCE performs engineering and cost analysis internally to verify need and cost validity of proposals. | Did not perform alternative analysis because the project is initiated and being done by the Operating Agent of the PDCI (LADWP) | Out of State | See Note 16C | High Wind Events, High Fire Risk Area, Extreme Temperature Conditions, Mudslide | LADWP is the Operating Agent | 145 | See Note 20B | 1000 kV DC line | 3220 MW | See Note 23B | 901994846 | CET-OT-OT-ME-313801 | 3138 | See Note 27A | Yes | 2017 | Pre-2017 | Annual Capital Operating Plan Process, Contractual arrangement with third-party | No | N/A | N/A | N/A | See Col. 37 | 2017= 336 2018 = 1,872 2019 = 1,783 2020 = 789 2021 = 201 2022 = 637 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2008-06-01 | No | 2017-09-15 | 2017-09-15 | N/A | 10500 | 10500 | See Note 53A | 5617.9515 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 2207.5608 | 1783.3566 | 788.9328 | 201.1682 | 636.9331 | 5617.9515 | 217.2527 | See Note 57A | N/A | No project specific cost benefit performed. This activity largely performs reactive work in response to LADWP determinations. | -1.4115e-12 | None | 100% | 0% | Column 52: Source= Unverified estimate, documents not readily available; Represents SCE's portion of the project only (50%)- total project cost for all owners $21M
N/A | PB-02.02 | PDCI Insulator Replacement | 34.314, -118.493 | Sylmar, Los Angeles County | Replace approx. 80,000 old porcelain insulators pm ~432 miles of the PDCI with toughened glass insulators to support the planned voltage upgrade | Insulators | New/Replacement/Modification | PB-02.01 | Infrastructure Replacement | Age/Condition | Performed by LADWP | 50 years old, originally installed in 1970 | LADWP is the Operating Agent owner and driver of determining need and proposals of Replace porcelain insulators to support voltage upgrade on PDCI projects, SCE performs engineering and cost analysis internally to verify need and cost validity of proposals. | Did not perform alternative analysis because the project is initiated and being done by the Operating Agent of the PDCI (LADWP) | Tier 2/Tier 3 | See Note 16C | High Wind Events, High Fire Risk Area, Extreme Temperature Conditions, Mudslide | LADWP is the Operating Agent | 168 | See Note 20B | 1000 kV DC line | 3220 MW | See Note 23B | 901994578 | CET-OT-OT-ME-313801 | 3138 | See Note 27A | Yes | 2017 | Pre-2017 | Annual Capital Operating Plan Process, Contractual arrangement with third-party | No | N/A | N/A | N/A | See Col. 37 | 2017 = 197 2018 = 1,097 2019 = 1,026 2020 = 666 2021 = 32 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2008-06-01 | No | 2017-09-15 | 2017-09-15 | N/A | 10500 | 10500 | See Note 53A | 3017.7788 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 1293.7424 | 1026.1867 | 666.1518 | 31.6978 | 0 | 3017.7788 | 1.0736 | See Note 57A | N/A | No project specific cost benefit performed. This activity largely performs reactive work in response to LADWP determinations. | 1.3388e-12 | None | 100% | 0% | Column 52: Source= Unverified estimate, documents not readily available; Represents SCE's portion of the project only (50%)- total project cost for all owners $21M
N/A | PB-02.03 | Pacific HVDC Intertie: Replacement of (3) PDCI Bowed Towers | 34.314, -118.493 | Sylmar, Los Angeles County | Emergent replacement of 3 PDCI bowed/deformed towers to avoid future failure, and possibly, cascading failure. | Replacement of deformed bowed towers due to high winds. | New/Replacement/Modification | N/A | Infrastructure Replacement | Age/Condition | Performed by LADWP | 50+ years | LADWP is the Operating Agent owner and driver of determining need and proposals of Capital projects, SCE performs engineering and cost analysis internally to verify need and cost validity of proposals. | Did not perform alternative analysis because the project is initiated and being done by the Operating Agent of the PDCI (LADWP) | Tier 2/Tier 3 | No | High Wind Events, High Fire Risk Area, Extreme Temperature Conditions, Mudslide | LADWP is the Operating Agent | Not applicable at program level | See Note 20B | 1000 kV DC line | 3220 MW | See Note 23B | 903417352 | CET-OT-OT-ME-313801 | 3138 | See Note 27A | Yes | 2021 | 2021 | Annual Capital Operating Plan Process, Contractual arrangement with third-party | No | N/A | N/A | N/A | See Col. 37 | 2021 = 1,557 2022 = 84 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2021-01-01 | No | 2021-03-30 | 2021-03-30 | N/A | 1500 | 1500 | See Note 53A | 1640.5957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1556.5191 | 84.0766 | 1640.5957 | 49.8566 | See Note 57A | N/A | No project specific cost benefit performed. This activity largely performs reactive work in response to LADWP determinations. | 1163.9368 | None | 100% | 0% | Column 52: Represents SCE's portion of the project only (50%)- total project cost for all owners $3M
N/A | PB-03 | Palo Verde Switchrack Capital Projects | Not applicable at program level | Not applicable at program level | Various capital projects related to the Arizona Nuclear Power Project (ANPP) High Voltage Switchyard, which includes but not limited to: disconnect switch repl, cable trench replacement, and fire protection enhancements | Switchyard (disconnect, trench, fire protection, etc.) | Replacement | Not applicable at program level | Other - See Notes | Age/Condition | Performed by Salt River Project (SRP) | Not applicable at program level | Salt River Project (SRP) operates and maintains, and makes/presents necessary additions or replacements to the ANPP HV Switchyard. SCE reviews and approves SRP's proposals. | Not applicable at program level | Non-HFRA | See Note 16C | Not applicable at program level | SRP is the Operating Agent | Not applicable at program level | Not applicable at program level | 500 kV | Not applicable at program level | See Note 23B | Not applicable at program level | CET-OT-OT-ME-465100 | 4651 | See Note 27A | Not applicable at program level | Not applicable at program level | Pre-2017 | Annual Capital Operating Plan Process, Contractual arrangement with third-party | No | N/A | N/A | N/A | Not applicable at program level | Not applicable at program level | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Not applicable at program level | See Note 46A | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 53A | Not applicable at program level | 1187.704 | 6276.855 | 4978.469 | 6843.629 | 648.179 | Not Available | 19934.836 | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not applicable at program level | Not applicable at program level | See Note 57A | N/A | No project specific cost benefit performed. This activity largely performs reactive work in response to SRP determinations. | See Note 60A | None | 100% | 0% | Column 9: Varies
N/A | PB-03.01 | Transmission Substation Fire Protection Enhancements: Palo Verde/Devers Reactors Fire Walls | 33.390, -112.862 | Wintersburg, Arizona | Capital project related to the ANPP High Voltage Switchyard Participation agreement. Salt River Project, as the ANPP Operating Agent, Transmission substation fire protection enhancements: Palo Verde/Devers Reactors Fire Wall | Enhancement of the Palo Verde/Devers Reactor fire wall between (R9A & R9B; R9A & Spare; R9B & R9C) and oil containment modifications. | Enhancement/Modification | Not applicable at program level | Infrastructure Replacement/Enhancement | Age/Condition | Performed by Salt River Project (SRP) | Not applicable at program level | Salt River Project (SRP) operates and maintains, and makes/presents necessary additions/modifications/replacements to the ANPP HV Switchyard. SCE reviews and approves SRP's proposals. | Did not perform alternative analysis because the project is initiated and being done by the Operating Agent of the ANPP/PV Switchyard (Salt River Project) | Not applicable - No HFRA | See Note 16B | Not applicable at program level | SRP is the Operating Agent | See Note 19B | N/A | See Note 21A | N/A | See Note 23B | 903040737 | CET-OT-OT-ME-465100 | 4651 | See Note 27A | Yes | 2019 | 2019 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2021 = 1,421 2022 = -72 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2020 | No | Q1 2021 | 2021-05-30 | N/A | 549 | 549 | See Note 53A | 1348.3639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 864.7595 | 555.7849 | -72.1804 | 1348.3639 | 69.1779 | See Note 57A | N/A | No project specific cost benefit performed. This activity largely performs reactive work in response to SRP determinations. | 4.6566e-13 | None | 100% | 0% | Column 52: Source= Unverified estimate, documents not readily available; Represents SCE's portion of the project only
N/A | PB-04 | Critical Infrastructure | Not applicable at program level | Not applicable at program level | In the normal course of operation, substation equipment may fail while in operation. While our system has redundancy to ensure reliability, these situations can reduce our system’s reliability level. Major substation equipment such as power transformers, circuit breakers, and disconnect switches is not readily available in the marketplace for procurement and delivery. In order to avoid or mitigate potential reductions in reliability, SC&M maintains a reserve inventory of such equipment. Activities include replacing failed equipment, obsolete or retired equipment, equipment rotation, and performing project support. | Circuit Breakers, Transformers, Disconnects, CCVTs, Mus, Bushings, Regulators | Spare Transformer Rotation | Not applicable at program level | Emergency Replacement | Age/Condition | Not applicable at program level | Not applicable at program level | For SCE to maintain Grid reliability, it must follow FERC regulations for all equipment 100kV and above. These major pieces of substation equipment such as power transformers, circuit breakers, and disconnect switches are not readily available in the marketplace for procurement and delivery. In order to avoid or mitigate potential reductions in reliability, SC&M maintains a reserve inventory of such equipment. Activities include replacing failed equipment, obsolete or retired equipment, equipment rotation, and performing project support. | Not applicable at program level | Not applicable at program level | See Note 16C | Not applicable at program level | Brandon Besch, Substation Construction & Maintenance | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 23B | Not applicable at program level | CET-PD-CI-CI-CRINSP | 3362 | See Note 27A | Not applicable at program level | Not applicable at program level | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | Not applicable at program level | Not applicable at program level | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Not applicable at program level | See Note 46A | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 53A | Not applicable at program level | 5033.806 | 0 | 7411.9645 | 0 | 7550.419 | Not Available | 19996.1896 | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not applicable at program level | Not applicable at program level | See Note 57A | N/A | Expedited cost of major substation equipment such as power transformers, circuit breakers, and disconnect switches is not readily available in the marketplace for procurement and delivery which could take 1yr or more. Also mitigates potential reductions in reliability | See Note 60A | None | 100% | 0% | Column 2: SCE has corrected the program name; previously reported in 12/2020 SRP as "FERC STEP- Critical Infrastructure" Column 23: This program is focused on maintaining a reserve of spares for critical equipment for use in emergency situations.
N/A | PB-04.01 | SC&M FERC STEP | See Note 3B | See Column 3 | STEP is a voluntary transformer sharing program put together to help mitigate the impact of a Terrorist Event that targets key substation equipment. The Sharing agreement is triggered by an act of sabotage on a utility substation. The impacted utility must use up its own available resource to mitigate the damage prior to call on the sharing agreement. Activities include replacing failed equipment, obsolete or retired equipment, equipment rotation, and performing project support. | Transformer voltage class 500kv-220kV and 220kV-115kV | Spare Transformer Rotation | None | Emergency Replacement | Age/Condition | Q1 2019 | Various - This project maintains spare equipment for needs across the system. | As a member of Edison Electric Institute (EEI), SCE has agreed to maintain 7 transformers in emergency equipment inventory as part of the Spare Transformer Equipment Program (STEP). Currently the equipment is rotated into service before warranty expiration or obsolesce. To monitor and track the health condition of the transformer while in inventory stock, a Dissolved Gas Analysis (DGA) is done each year. | N/A | See Column 3 | See Note 16C | See Column 3 | Brandon Besch, Substation Construction & Maintenance | See Note 19B | See Note 20B | Various | See Note 22A | See Note 23B | 700074 | CET-PD-CI-CI-CRINSP | 3362 | See Note 27A | Yes | 2012 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | See Column 3 | See Note 46A | See Column 3 | Not Applicable | See Column 3 | See Column 3 | N/A | See Column 3 | See Column 3 | See Note 53A | 76507.7265 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 42830.7085 | 10713.3021 | 7590.8563 | 11837.4588 | 3535.4009 | 76507.7265 | 0 | See Note 57A | N/A | Expedited cost of major substation power transformers and helps mitigate the impact of a terrorist event that targets key substation equipment. STEP program assists with lead time for transformers for lead times that could be 1yr or more. Also mitigates potential reductions in reliability | -9.5556e-11 | None | 100% | 0% | Column 21: Varies based on project (115kV to 500kV) Column 23: This project is focused on maintaining a reserve of spares for critical equipment for use in emergency situations.
N/A | PB-05 | Substation Unplanned Capital Maintenance | Not applicable at program level | Not applicable at program level | Substation Unplanned Capital Maintenance captures the labor, equipment, and other material costs to remove and replace assets not identified in other replacement programs, on a reactive basis. Activities are predominantly like-for-like replacements and maintenance. Reactive equipment replacements must be completed in a timely manner because substation equipment failures may lead to prolonged outages, unsafe operating conditions, or more costly reactive solutions. Examples of such work include unplanned replacement of failed PT's, CT's, as well as Circuit Breakers, B-Banks and Disconnects. | Substation Maintenance | Repair/ Replace | Not applicable at program level | Other - See Notes | Age/Condition | Not applicable at program level | Not applicable at program level | This is a reactive in which equipment replacements must be completed in a timely manner because substation equipment failures may lead to prolonged outages, unsafe operating conditions, or more costly reactive solutions. | Not applicable at program level | Not applicable at program level | See Note 16C | Not applicable at program level | Brandon Besch, Substation Construction & Maintenance | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 23B | Not applicable at program level | CET-PD-BM-SU-SUBSNW | 3363 | See Note 27A | Not applicable at program level | Not applicable at program level | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | Not applicable at program level | Not applicable at program level | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Not applicable at program level | See Note 46A | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 53A | Not applicable at program level | 6787.4655 | 7577.3368 | 7781.1937 | 7866.8934 | 7933.2088 | Not Available | 37946.0981 | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not applicable at program level | Not applicable at program level | See Note 57A | N/A | No project specific cost benefit performed. This activity largely performs reactive work in response to equipment failure and other factors. | See Note 60A | None | 100% | 0% | Column 9: Asset Condition Column 23: Reactive equipment replacements must be completed in a timely manner because substation equipment failures may lead to prolonged outages or unsafe operating conditions.
N/A | PB-05.01 | Devers Substation Transformer Replacement | 33.935, -116.578 | North Palm Springs, Riverside County | A Phase damaged during fault and must be replaced | Transformer | Repair/ Replace/New | PB-19.03 | Emergency Replacement | Age/Condition - Replace Transformers | 2018 | 14 Years old | N/A- unit failed in service | N/A | Non-HFRA | See Note 16C | Extreme Heat, Desert Area | Brandon Besch, Substation Construction & Maintenance | See Note 19B | 98 | See Note 21A | 83/110 MVA, 525/17.3kV | See Note 23B | 902414971 | CET-PD-BM-SU-SUBSSE | 3363 | See Note 27A | Yes | 2018 | 2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2021 = 2,676 2022 = 3 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2019-10-01 | No | 2020-03-31 | 2021-02-10 | Waiting on long lead-time items | 3500 | 3500 | See Note 53A | 2678.9831 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 3.8829 | 2402.6964 | 210.8939 | 58.7029 | 2.807 | 2678.9831 | 505.0675 | See Note 57A | N/A | No project specific cost benefit performed. This activity largely performs reactive work in response to equipment failure and other factors. | -1.8861e-12 | None | 100% | 0% | Column 52: Source= Unverified estimate, documents not readily available
N/A | PB-05.02 | Eagle Mountain: Replace the 5A Bank 220/161/66kV | 33.811428, -115.453552 | Desert City, Riverside County | Internal fault, bank must be replaced | Transformer | Repair/ Replace/New | PB-19.03 | Emergency Replacement | Age/Condition - Replace Transformers | 2018 | 18 | N/A- unit failed in service | N/A | Non-HFRA | See Note 16C | Extreme Heat, Desert Area | Brandon Besch, Substation Construction & Maintenance | See Note 19B | 11 | See Note 21A | 280 MVA, 220/161/12kV | See Note 23B | 902698648 | CET-PD-BM-SU-SUBSSE | 3363 | See Note 27A | Yes | 2019 | 2018 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2022 = 10,624 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2019-06-19 | Yes | 2021-08-01 | 2022-12-20 | Waiting on long lead-time items | Not readily available | Not Readily Available | See Note 53A | 10624.0605 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 0 | 506.1504 | 1474.5636 | 6339.0715 | 2304.2751 | 10624.0605 | 2109.0675 | See Note 57A | N/A | No project specific cost benefit performed. This activity largely performs reactive work in response to equipment failure and other factors. | -9.8476e-13 | None | 93.61% | 6.387%
N/A | PB-06 | Substation Planned Capital Maintenance | Not applicable at program level | Not applicable at program level | Substation Planned Capital Maintenance captures the labor, equipment, and other material costs to remove and replace assets not identified in other replacement programs. Activities are predominantly like-for-like replacements and maintenance which are identified and planned for in advance. Examples of such work include replacement of PT's, CT's, as well as Circuit Breakers, B-Banks and Disconnects that are not covered under another capital program. | Substation Maintenance | Repair / Replace / New | Not applicable at program level | Other - See Notes | Age/Condition | Not applicable at program level | Not applicable at program level | This is a programmatic approach that allows SCE to proactively plan work over a controlled schedule, perform any necessary engineering design activity, and allocate and manage resources effectively. | Not applicable at program level | Not applicable at program level | See Note 16B | Not applicable at program level | Brandon Besch, Substation Construction & Maintenance | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Upon inspection, subject matter expert review, or field input, the projects within this program are replaced or fixed on an as-needed basis. | Not applicable at program level | CET-PD-IR-SP-SUBSNW | 3363 | See Note 27A | Not applicable at program level | Not applicable at program level | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | Not applicable at program level | Not applicable at program level | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Not applicable at program level | See Note 46A | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 53A | Not applicable at program level | 5742.7258 | 4985.3064 | 5125.6863 | 5241.7529 | 5215.5797 | Not Available | 26311.051 | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not applicable at program level | Not applicable at program level | See Note 57A | N/A | No project specific cost benefit performed. This work is largely inspection-driven or performed ahead of asset failure to maintain the safety and reliability of the system. See Note 59A. | See Note 60A | None | 100% | 0% | Column 9: Planned maintenance for substation equipment for the purpose of Safety, Reliability and compliance Column 10: Compliance internal and external requirements, CAISO, NERC, WECC etc.
N/A | PB-06.02 | Serrano Substation Gas Monitoring System Upgrade | 33.830, -117.790 | Orange, Orange County | Upgrade existing SF-6 gas monitoring to ensure asset reliability; Remove bypass piping on all outdoor gas zones and all gas zones with >1,000 lbs of SF6. Replace existing analog gas density monitors with new hybrid gas density monitors on newly isolated compartments. Removal of bypass tubing reduces our emissions risk from a single incident from 1/3 of SCE’s annual limit to about 1/10. | Gas monitoring | Repair / Replace / New | None | Infrastructure Enhancement | Age/Condition | 2020-03-01 | 10-20 Years Old | Review of history of leakage issues. Knowing Serrano contains more than 100,000 Lbs. of SF6 gas (~5% of California’s total). 220kV jack bus leak issue was 22.4% of today’s CARB imposed annual emission limit on SCE. | See Note 14A | Tier 2 | See Note 16C | No significant environmental factors | Brandon Besch, Substation Construction & Maintenance | See Note 19B | 19.2 | 500/220 kV | 500 kV and 220 kV | See Note 23B | 902675199 | CET-PD-IR-SP-SUBSSE | 3363 | See Note 27A | Yes | 2019 | 2018 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2021 = 7,837 2022 = 1,762 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2019-10-01 | No | 2020-12-31 | 2021-10-01 | Not readily available | 5000 | 5000 | See Note 53A | 9599.2469 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 0 | 3780.0161 | 2799.7565 | 1257.6773 | 1761.7971 | 9599.2469 | 2076.4817 | See Note 57A | N/A | No project specific cost benefit performed. This activity largely performs reactive work in response to equipment failure and other factors. | 4.5184e-12 | None | 100% | 0% | Column 52: Source= Unverified estimate, documents not readily available
N/A | PB-07 | Substation Storm-Damaged Equipment Replacements | Not applicable at program level | Not applicable at program level | This activity includes costs associated with replacing substation electrical facilities, structures, or equipment damaged during storm events. Storm events are driven by weather and other environmental factors outside of SCE’s control. This is planned for year over year and based on a 5 year average. | Substation electrical facilities, structures, or equipment | Repair / Replace / New | Not applicable at program level | Safety | Emergency Response - Storm Related | Not applicable at program level | Not applicable at program level | Emergency Storm restoration at various substations. Forecast is based on 5 year average from storm restoration repairs/replacements. | Not applicable at program level | Not applicable at program level | See Note 16C | Not applicable at program level | Brandon Besch, Substation Construction & Maintenance | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 23B | Not applicable at program level | CET-PD-ST-SS-SUBSNW | 3363 | See Note 27A | Not applicable at program level | Not applicable at program level | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | Not applicable at program level | Not applicable at program level | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Not applicable at program level | See Note 46A | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 53A | Not applicable at program level | 4.4709 | 6.9945 | 7.2384 | 7.3176 | 7.3838 | Not Available | 33.4053 | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not applicable at program level | Not applicable at program level | See Note 57A | N/A | N/A - This activity largely performs reactive work in response to equipment failure and other factors | See Note 60A | None | 100% | 0% | Column 16: Potentially -- If repair/remediation work is performed in response to wildfire damage Column 23: Reactive equipment replacements must be completed in a timely manner because substation equipment failures may lead to prolonged outages or unsafe operating conditions
N/A | PB-07.01 | Windhub Substation Flash Flood Damage Repairs | 35.035, -118.281 | Mohave, Kern County | Due to flash flooding damages 10/27/15, this activity performed various work to remediate the impacts, including but not limited to: installing 1700 LF of 8'H emergency temporary fencing w/5-strands of barb wire, installing two 30' double gates; installing grounding for temp. fence; clearing path in concrete channel above substation to allow trapped water to flow through; clearing path inside sub in mud/rock dust for access. | Flood mitigation | Repair / Replace / New | SP-29 | Safety | Emergency Response - Storm Related | 2014 | N/A, see project description. | N/A - Storm response | N/A - Storm Response | Non-HFRA | See Note 16C | Flash flooding | Brandon Besch, Substation Construction & Maintenance | See Note 19B | 59.2 | See Note 21A | See Note 22A | See Note 23B | 901671463 | CET-PD-ST-SS-SUBSNW | 3363 | See Note 27A | Yes | 2005 | Pre-2017 | FRM/CRT | No | N/A | N/A | N/A | See Col. 37 | 2016 = 1692 2017 = 5 2018 = 732 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2015-09-19 | No | Basic finish date 12/31/2015 | 2016-06-17 | N/A | Not readily available | Not Readily Available | See Note 53A | 2428.6303 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 2428.6303 | 0 | 0 | 0 | 0 | 2428.6303 | 107.8815 | See Note 57A | N/A | N/A - This activity largely performs reactive work in response to equipment failure and other factors | 1.3453e-12 | None | 100% | 0% | Column 23: Reactive equipment replacements must be completed in a timely manner because substation equipment failures may lead to prolonged outages or unsafe operating conditions
N/A | PB-08 | Transmission Planned Capital Maintenance | Not applicable at program level | Not applicable at program level | Transmission Capital Maintenance includes the costs to remove, replace, and retire assets on a planned basis. Planned transmission capital maintenance is driven by regular equipment maintenance cycles; maintenance work identified and prioritized through overhead and underground inspection programs; maintenance identified through observations by field personnel, or other activities. | Transmission Maintenance | Repair/ Replace | Not applicable at program level | Other - See Notes | Age/Condition | Not applicable at program level | Not applicable at program level | •Visual inspection •Intrusive pole inspection • Pole Load Calculation | Not applicable at program level | Not applicable at program level | See Note 16B | Not applicable at program level | Arianna Armon, Transmission | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Planned transmission capital maintenance is largely driven by inspection results, infrastructure replacement activities, or field observations which can lead to projects to address emergent issues in a particular grid, equipment, or structure type. | Not applicable at program level | CET-PD-IR-TP-TRMETE | 3364 | See Note 27A | Not applicable at program level | Not applicable at program level | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | Not applicable at program level | Not applicable at program level | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Not applicable at program level | See Note 46A | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 53A | Not applicable at program level | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 0 | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not applicable at program level | Not applicable at program level | See Note 57A | N/A | No project specific cost benefit performed. This work is largely inspection-driven or performed ahead of asset failure to maintain the safety and reliability of the system. See Note 59A. | See Note 60A | None | 100% | 0% | Column 9: Asset Condition
N/A | PB-08.01 | Los Lomas Material Yard Construction | 33.718, -117.739 | Duarte, Los Angeles County | Construct a Transmission Material Storage Yard located on the Rio Hondo-Vincent 500kV and the Mira Loma-Vincent 500kV R/W North of the 210 Freeway and South of Huntington Drive in Duarte, CA. Construction will consist of addition 800' of eight foot chain link fence with 24' double swing gates, Five thousand eight hundred cubic yards of Number 2 road base over approximately 8.6 acres of fee owned property. Perimeter security lighting. | Material Storage Yard | New | None | Other - See Notes | Other- See Notes | New construction of storage facility. No existing assets replaced or upgraded. | New construction of storage facility. No existing assets replaced or upgraded. | No field testing required. | No alternative sites were available based on the needed space and accessibility required for heavy equipment. | Non-HFRA | See Note 16C | No significant environmental factors | Arianna Armon, Transmission | See Note 19B | 8.4 | See Note 21A | See Note 22A | See Note 23B | TD1343148 | CET-PD-IR-TP-TRMETE | 3364 | See Note 27A | Yes | 2017 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2018 = 1,104 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2017-12-05 | No | 2018-06-29 | 2018-05-15 | N/A | 715 | 715 | See Note 53A | 1103.7879 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 1103.7879 | 0 | 0 | 0 | 0 | 1103.7879 | 69.673 | See Note 57A | N/A | No project specific cost benefit performed. See Note 59A. | -2.3283e-13 | None | 100% | 0% | Column 9, 10: Material Storage Yard Column 52: Source= Unverified estimate, documents not readily available
N/A | PB-08.02 | Saugus-Rio Hondo Idle Tower Removal | 34.422, -118.575 / 34.105, -117.981 | Acton, Los Angeles County | Removal of 13 towers on Idle Saugus-Rio Hondo line. Removal of M29-T1 to M31-T3 220kv towers on Saugus-Rio Hondo Idle 220kv. | Towers | Removal | None | Other - See Notes | Age/Condition | The date of the last inspection precedes our internal records. | 13 towers installed in 1964 | No field testing required. | The primary alternative was to relocate assets, but they were ultimately not needed. | Tier 3 | See Note 16C | No significant environmental factors | Arianna Armon, Transmission | See Note 19B | See Note 20B | Idle-Prior 220kV | See Note 22A | See Note 23B | TD928757 | CET-PD-IR-TP-TRMETE | 3364 | See Note 27A | Yes | 2014 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2014 = 3,583 2015 = 17 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2014-11-05 | No | 2015-12-31 | 2014-12-10 | Extra contingency time was built in to original timeline due to location of work. Work completed as permits, environmental & resources were available. | 4787 | 4787 | See Note 53A | 3599.5713 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 3599.5713 | 0 | 0 | 0 | 0 | 3599.5713 | 274.93 | See Note 57A | N/A | No project specific cost benefit performed. This work is largely inspection-driven or performed ahead of asset failure to maintain the safety and reliability of the system. See Note 59A. | 0 | None | 100% | 0% | Column 9: Infrastructure Removal Column 23: Project involves removal of existing facilities Column 52: Source= Unverified estimate, documents not readily available
N/A | PB-08.03 | Lugo-Mohave EMT Tower Retrofit | 34.367, -117.369 / 35.148, -114.596 | Hesperia, San Bernardino County, Laughlin, Clark County | EMT high voltage 500kV towers retrofitted due to propensity to fail under high load, high wind conditions. | Retrofit | Modification/Upgrade | None | Infrastructure Replacement | T-Line Reliability | 2015 | 52 | Structural analysis were performed to determine engineering requirements to retrofit | Structure replacement | Non-HFRA, except Lugo Sub within Tier 2 | See Note 16C | High Wind Events, Extreme Temperature Conditions, Air particulate levels, High Seismic | Demetric Brown, MPO - Programs | See Note 19B | See Note 20B | 500 kV | See Note 22A | See Note 23B | 901677586 | CET-PD-IR-TP-789400 | 3364 | See Note 27A | Yes | 2016-05-12 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2019 = 8,013 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2017-06-12 | No | 2016-12-01 | 2019-09-25 | Scope Increase | 2820 | 2820 | See Note 53A | 8012.6307 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 7324.1245 | 688.5062 | 0 | 0 | 0 | 8012.6307 | 1672.6715 | See Note 57A | N/A | See Note 59A | -8.5209e-12 | None | 100% | 0% | Column 52: Source= PMWIF (v0 Project Summary)
N/A | PB-08.04 | Colorado River-Palo Verde EMT Tower Retrofit | 33.589, -114.814 / 33.390, -112.862 | Blythe, Riverside County | EMT high voltage 500kV towers retrofitted due to propensity to fail under high load, high wind conditions. | Retrofit | Modification/Upgrade | None | Infrastructure Replacement | Reliability of transmission line | 2017-04-04 | 38 | Structural analysis were performed to determine engineering requirements to retrofit | Structure replacement | Non-HFRA | See Note 16C | High Wind Events | Demetric Brown, MPO - Programs | See Note 19B | See Note 20B | 500 kV | See Note 22A | See Note 23B | 901674008 | CET-PD-IR-TP-789400 | 3364 | See Note 27A | Yes | 2015 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2017 = 1,429 2018 = 47 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2015-09-15 | No | 2017-12-01 | 2017-06-30 | N/A | 1155 | 1155 | See Note 53A | 1476.3149 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 1476.3149 | 0 | 0 | 0 | 0 | 1476.3149 | 278.6565 | See Note 57A | N/A | See Note 59A | -1.5552e-13 | None | 100% | 0% | Column 52: Source= PMWIF (v0 Proj Summary)
N/A | PB-08.05 | Midway-Vincent No.2 EMT Tower Retrofit | 35.404, -119.450 / 34.486, -118.118 | Kern, Ventura, Buttonwillow, Palmdale, Los Angeles County | EMT high voltage 500kV towers retrofitted due to propensity to fail under high load, high wind conditions. | Retrofit | Modification/Upgrade | None | Infrastructure Replacement | Reliability of transmission line | 2017-10-18 | 46 | Structural analysis were performed to determine engineering requirements to retrofit | Structure replacement | Non-HFRA/Tier 3 | See Note 16C | High Wind Events | Demetric Brown, MPO - Programs | See Note 19B | See Note 20B | 500 kV | See Note 22A | See Note 23B | 901690300 | CET-PD-IR-TP-789400 | 3364 | See Note 27A | Yes | 2016 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2018 = 1,110 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2017-08-28 | No | 2017-12-01 | 2018-01-25 | Environmental Conditions | 642 | 642 | See Note 53A | 1110.4826 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 1110.4826 | 0 | 0 | 0 | 0 | 1110.4826 | 144.803 | See Note 57A | N/A | See Note 59A | -8.5265e-16 | None | 100% | 0% | Column 52: Source= PMWIF (v0 Proj Summary)
N/A | PB-09 | Transmission Deteriorated Pole Program | Not applicable at program level | Not applicable at program level | Through its Deteriorated Pole Program, SCE replaces poles that fail intrusive inspection, have visual defects or do not meet pole loading requirements and are not included in the Pole Loading Program. See A.19-08-013, SCE-02, Vol. 5 | Transmission Poles | Replacement and restoration | Not applicable at program level | Safety | Targeted Line Reliability | Not applicable at program level | Not applicable at program level | Pole Loading Calculations, 3rd Party Loading Failures, Visual, Aerial, & Intrusive Inspections | Not applicable at program level | Not applicable at program level | See Note 16B | Not applicable at program level | Arman Nehzati, Distribution Program Management | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Based on GO95 Rule 18 prioritization. It is based on Safety Factor and location relative to High Fire Threat Districts in the case of pole loading replacements. Prioritization is based on levels of deterioration in the case of intrusive pole inspection replacements. | Not applicable at program level | CET-PD-IR-TR-TRSJAC | 3364 | See Note 27A | Not applicable at program level | Not applicable at program level | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | Not applicable at program level | Not applicable at program level | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Not applicable at program level | See Note 46A | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 53A | Not applicable at program level | 6506.6142 | 7561.0792 | 6491.134 | 6517.2632 | 6590.1681 | Not Available | 33666.2588 | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not applicable at program level | Not applicable at program level | See Note 57A | N/A | N/A - Compliance with General Order 95 | See Note 60A | None | 100% | 0%
N/A | PB-10 | Transmission Storm-Damaged Equipment Replacements | Not applicable at program level | Not applicable at program level | This activity includes costs associated with replacing transmission electrical facilities, structures, or equipment damaged during storm events. Storm events are driven by weather and other environmental factors outside of SCE’s control. | Transmission equipment, facilities, or structures | Various Actions (New, Replace, Maintenance) | Not applicable at program level | Safety | Emergency Response - Storm Related | Not applicable at program level | Not applicable at program level | N/A - Storm response | Not applicable at program level | Not applicable at program level | See Note 16C | Not applicable at program level | Arianna Armon, Transmission | Not applicable at program level | Not applicable at program level | Various | Not applicable at program level | See Note 23B | Not applicable at program level | CET-PD-ST-TS-TREAST; CET-PD-ST-TS-TRSJAC | 3367 | See Note 27A | Not applicable at program level | Not applicable at program level | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | Not applicable at program level | Not applicable at program level | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Not applicable at program level | See Note 46A | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 53A | Not applicable at program level | 4267.4745 | 4205.8572 | 4250.7668 | 4280.5751 | 4332.5284 | Not Available | 21337.2021 | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not applicable at program level | Not applicable at program level | See Note 57A | N/A | N/A - This activity largely performs reactive work in response to equipment failure and other factors | See Note 60A | None | 100% | 0% | Column 16: Potentially -- If repair/remediation work is performed in response to wildfire damage Column 23: Reactive equipment replacements must be completed in a timely manner because transmission equipment failures may lead to prolonged outages or unsafe operating conditions
N/A | PB-10.01 | Sayre Fire Civil Repairs | 34.221, -118.187 / 34.314, -118.493 | City of Sylmar, Los Angeles County | SAYRE FIRE CRIB WALL DAMAGED 11/15/08 Excessive erosion due to post fire run off caused damage to access roads. Site #1 - Construct retaining wall to protect the footings of tower M8-T5 on the Chatsworth-MacNeil-Newhall-San Fernando 66KV line. Construct retaining wall to repair and support access road to the same structure. Site #2 - Construct retaining wall to replace crib wall that was damaged during the Sayer Fire that supports the footings of steel tower M1-T4 on the Gould-Sylmar 220KV line. Site #3 – Construct a retaining wall on side of access road to protect road from land sliding on to roadway. Road used to access towers on the Gould-Sylmar 220KV line Site #4 – Repair drainage pipe that crosses under access road and recontour road to protect from erosion. Road used to access towers on the Gould-Sylmar 220KV line Site #5 – Install drainage pipe under access road, recontour and stabilize downhill slope on side of road. Widen road at same location to re-establish vehicle access. Road used to access towers on the Gould-Sylmar 220KV line Site #6 – Repair washed out spur road to tower M1-T6 on the Gould Sylmar 220KV line. Construct a concrete wet crossing on road. Construct bin wall on side of road to protect road from collapsing in to ravine. Install road side drain to protect road from erosion. Recontour road for proper drainage. | Site #1 New retaining wall. Site #2 Crib Wall Replacement Site #3 New retaining wall Site #4 Replace drainage pipe Site #5 New drainage pipe and slope stabilization Site #6 New concrete wet crossing, new bin wall & drain | Replacement | None | Infrastructure replacement | Emergency Response - Storm Related | 2020-07-02 | Unknown | NA | Unknown | HFTD Tier 3 | See Note 16D | High Wind Events, High Fire Risk Area, Extreme Temperature Conditions, Mudslide | Arianna Armon, Transmission | 0 miles | See Note 20A | 220kV | See Note 22A | See Note 23B | 800475947 | CET-PD-ST-TS-TRNCST-I | 3367 | See Note 27A | Yes | 2010 | Pre-2018 | See Note 31A | No | N/A | N/A | N/A | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Construction more than 50% completed | See Note 46A | 2021-09-20 | Yes | 2010-12-31 | 2023-12-28 | Environmental Factors | 1800 | 1800 | See Note 53A | 2699.0379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1253.1473 | 122.2222 | 131.9988 | 692.481 | 499.1886 | 2699.0379 | 924.399 | See Note 57A | N/A | N/A - This activity largely performs reactive work in response to equipment failure and other factors | 2699.0379 | None | 100% | 0% | Column 52: Source= Project Manager
N/A | PB-10.02 | Colorado River-Palo Verde - Replace Towers due to Wind Storm | 33.5807073;-114.8170621 | Vicksburg AZ; La Paz County; | Replace (5) Towers due to Wind | Replace 5 towers | Replacement | None | Emergency Replacement | Emergency Response - Storm Related | 2021-03-14 | 41 | NA | Temporary structures were installed to re-energize the circuit. Final repairs are scheduled to start 4th quarter of 2022, completion scheduled for 1st quarter of 2023 | Not applicable - Out of State | See Note 16B | High Wind Events, Extreme Temperature Conditions | Arianna Armon, Transmission | 2 miles | See Note 20A | 500kV | See Note 22A | See Note 23B | 903505233 | CET-PD-ST-TS-TREAST | 3367 | See Note 27A | NA | NA | 2020 | See Note 31A | No | N/A | N/A | N/A | See Col. 37 | 2023 = 16,913 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2022-10-19 | Yes | 2022-12-30 | 2023-02-15 | N/A | See note | See note | See Note 53A | 16912.5649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5105.5749 | 11806.9899 | 16912.5649 | 3266.7602 | See Note 57A | N/A | N/A - This activity largely performs reactive work in response to equipment failure and other factors | 9835.1152 | None | 100% | 0% | Column 52: No project estimate for emergency projects such as this
N/A | PB-11 | Circuit Breaker Replacements - 220 kV & above | Not applicable at program level | Not applicable at program level | This program contains projects that proactively replace Bulk Circuit Breakers. | Not applicable at program level | Replacement | Not applicable at program level | Infrastructure Replacement | Age/Condition | Not applicable at program level | Not applicable at program level | The main analysis used to inform the health of the asset is the Health Index developed from the MDT (Maintenance Decision Tool). The health index is developed using specific data from the assets including fault interruption history, age, maintenance data etc… In addition to the health index, decisions are influenced by a Weibull analysis and subject matter input for conditions not included in the MDT, e.g. possible leaks. | Not applicable at program level | Not applicable at program level | See Note 16B | Not applicable at program level | Demetric Brown, MPO - Programs | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 23B | Not applicable at program level | CET-ET-IR-CB-421100 | 4211 | See Note 27A | Not applicable at program level | Not applicable at program level | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | Not applicable at program level | Not applicable at program level | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Not applicable at program level | See Note 46A | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 53A | Not applicable at program level | 5902.943 | 4274.925 | 2605.943 | 3143.165 | 0 | Not Available | 15926.976 | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not applicable at program level | Not applicable at program level | See Note 57A | N/A | No project specific cost benefit performed. The Sub IR program for CB and transformers is reliability based with a Weibull curve analysis determining the appropriate number of annual replacements. The justification for the program is described in SCE general rate case submissions. See Note 59A. | See Note 60A | None | 100% | 0%
N/A | PB-11.01 | Vincent Substation Circuit Breaker Replacement | 34.486, -118.116 | Palmdale, Los Angeles County | Vincent Substation: Replace (9) 220kV CBs (CB's 452, 512, 522, 572, 612, 622, 632, 652, and 672 lines) | Circuit Breaker | Replacement | PB-16.18, PB-11.03, PB-16.04, PB-19.01, PB-18.01 | Infrastructure Replacement | Age/Condition | CB# 452 - 12/09/2013, CB# 512 - 12/09/2013, CB# 522 - 12/09/2013, CB# 572 - 12/09/2013, CB# 612 - 12/09/2013, CB# 622 - 03/03/2014, CB# 632 - 12/04/2014, CB# 652 - 12/09/2013, CB# 672 - 03/20/2014 | CB# 452 - 28 Years, CB# 512 - 28 Years, CB# 522 - 28 Years, CB# 572 - 28 Years, CB# 612 - 29 Years, CB# 622 - 29 Years, CB# 632 - 28 Years, CB# 652 - 29 Years, CB# 672 - 29 Years | The main analysis used to inform the health of the asset is the Health Index developed from the MDT (Maintenance Decision Tool). The health index is developed using specific data from the assets including fault interruption history, age, maintenance data etc… In addition to the health index, decisions are influenced by a Weibull analysis and subject matter input for conditions not included in the MDT, e.g. possible leaks. | See Note 14A | Tier 3 | See Note 16B | The asset’s service life can be affected by the following environmental factors; high corrosive soils, weather climates, airborne contamination, and pollution. | Demetric Brown, MPO - Programs | See Note 19B | 49.4 | See Note 21A | 500/220kV | See Note 23B | 900566753 | CET-ET-IR-CB-421100 | 4211 | See Note 27A | Yes | 2012 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2014 = 4,968 2015 = 19 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | Not Available | No | 2013-12-31 | 2014-12-18 | Outage Constraints (TIF 4555) | 3150 | 3150 | See Note 53A | 4987.6431 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 4987.6431 | 0 | 0 | 0 | 0 | 4987.6431 | 946.8306 | See Note 57A | N/A | No project specific cost benefit performed. The Sub IR program for CB and transformers is reliability based with a Weibull curve analysis determining the appropriate number of annual replacements. The justification for the program is described in SCE general rate case submissions. See Note 59A. | -2.4933e-12 | None | 100% | 0% | Column 52: Source= Unverified system estimate
N/A | PB-11.02 | Serrano Substation Circuit Breaker Replacement | 33.828, -117.791 | Orange, Orange County | Serrano Substation: Replace (4) 13.8kV CBs (#313, 314, 321, 322) Replace six (6) LED lighting fixtures on tertiary bus support structures Install ten (10) LED lighting fixtures on 220kV dead support structures | Circuit Breakers | Replacement | None | Infrastructure Replacement | Age/Condition | CB# 313 - 07/26/2016, CB# 314 - 12/07/2016, CB# 321 - 07/26/2016, CB# 322 - 07/27/2016 | CB# 313 - 16 Years, CB# 314 - 16 Years, CB# 321 - 17 Years, CB# 322 - 19 Years | The main analysis used to inform the health of the asset is the Health Index developed from the MDT (Maintenance Decision Tool). The health index is developed using specific data from the assets including fault interruption history, age, maintenance data etc… In addition to the health index, decisions are influenced by a Weibull analysis and subject matter input for conditions not included in the MDT, e.g. possible leaks. | See Note 14A | Tier 2 | See Note 16B | Fairly temperate climate and is subject to occasional annual storms. | Demetric Brown, MPO - Programs | See Note 19B | 19.2 | See Note 21A | 13.8 kV | See Note 23B | 901333444 | CET-ET-IR-CB-421100 | 4211 | See Note 27A | Yes | 2014 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2016 = 798 2017 = 3 2018 = 268 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | Not Available | No | 2016-12-31 | 2016-07-26 | N/A | 208 | 208 | See Note 53A | 1068.7902 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 1068.8062 | -0.01603 | 0 | 0 | 0 | 1068.7902 | 242.7127 | See Note 57A | N/A | No project specific cost benefit performed. The Sub IR program for CB and transformers is reliability based with a Weibull curve analysis determining the appropriate number of annual replacements. The justification for the program is described in SCE general rate case submissions. See Note 59A. | -6.0447e-13 | None | 100% | 0% | Column 52: Source= Unverified estimate; documents not readily available
N/A | PB-11.03 | Vincent Substation ABB Reactor Circuit Breaker Replacement | 34.486, -118.116 | Palmdale, Los Angeles County | Vincent 500/220 Sub: Replace ABB reactor circuit breakers No. R11, R12, R13, R14, R41, R42, R43, R44 (8 circuit breaker) | Circuit Breaker | Replacement | PB-16.18, PB-11.01, PB-16.04, PB-19.01, PB-18.01 | Infrastructure Replacement | Age/Condition | CB# R11 - 11/28/2016, CB# R12 - 11/28/2016, CB# R13 - 11/30/2016, CB# R14 - 12/20/2016, CB# R41 - 11/09/2016, CB# R42 - 11/09/2016, CB# R43 - 11/16/2016, CB# R44 - 11/16/2016 | CB# R11 - 19 Years, CB# R12 - 19 Years, CB# R13 - 19 Years, CB# R14 - 19 Years, CB# R41 - 19 Years, CB# R42 - 19 Years, CB# R43 - 19 Years, CB# R44 - 19 Years | The main analysis used to inform the health of the asset is the Health Index developed from the MDT (Maintenance Decision Tool). The health index is developed using specific data from the assets including fault interruption history, age, maintenance data etc… In addition to the health index, decisions are influenced by a Weibull analysis and subject matter input for conditions not included in the MDT, e.g. possible leaks. | See Note 14A | Tier 3 | See Note 16B | The asset’s service life can be affected by the following environmental factors; high corrosive soils, weather climates, airborne contamination, and pollution. | Demetric Brown, MPO - Programs | See Note 19B | 49.4 | See Note 21A | 500/220kV | See Note 23B | 901613741 | CET-ET-IR-CB-421100 | 4211 | See Note 27A | Yes | 2015 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2016 = 1,624 2017 = 44 2018 = 13 2019 = 2 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | Not Available | No | 2016-12-31 | 2016-11-18 | N/A | 960 | 960 | See Note 53A | 1682.7715 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 1680.7496 | 2.0218 | 0 | 0 | 0 | 1682.7715 | 236.3188 | See Note 57A | N/A | No project specific cost benefit performed. The Sub IR program for CB and transformers is reliability based with a Weibull curve analysis determining the appropriate number of annual replacements. The justification for the program is described in SCE general rate case submissions. See Note 59A. | -2.5301e-12 | None | 100% | 0% | Column 52: Source= Unverified system estimate
N/A | PB-11.04 | Mohave Substation Circuit Breaker Install | 35.148, -114.592 | Laughlin, Clark County, Nevada | Mohave Substation: Install (2) 500kV CBs (#732 and 832) | Circuit Breaker | Replacement | PB-16.09, PB-16.10 | Infrastructure Replacement | Age/Condition | CB# 732 - 12/11/2018, CB# 832 - 09/26/2018 | CB# 732 - 35 Years, CB# 832 - 35 Years | The main analysis used to inform the health of the asset is the Health Index developed from the MDT (Maintenance Decision Tool). The health index is developed using specific data from the assets including fault interruption history, age, maintenance data etc… In addition to the health index, decisions are influenced by a Weibull analysis and subject matter input for conditions not included in the MDT, e.g. possible leaks. | See Note 14A | Out of State | See Note 16C | Extreme heat and sandy conditions | Brent Gokbudak, MPO-Project Development & Execution | See Note 19B | 11.5 | See Note 21A | 500kV | See Note 23B | 902409388 | CET-ET-IR-CB-421100 | 4211 | See Note 27A | Yes | 2016 | 2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2019 = 3,647 2020 = -167 2021 = 33 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2019-01-08 | No | 2018-12-31 | 2019-02-01 | Delays in Agreement Regarding Customer Cost Responsibility | 2769 | 2769 | See Note 53A | 3512.966 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 3352.4175 | 294.5898 | -167.3772 | 33.336 | 0 | 3512.966 | 546.3501 | See Note 57A | N/A | No project specific cost benefit performed. The Sub IR program for CB and transformers is reliability based with a Weibull curve analysis determining the appropriate number of annual replacements. The justification for the program is described in SCE general rate case submissions. See Note 59A. | -7.0317e-13 | None | 100% | 0% | Column 52: Source= Unverified estimate, documents not readily available
N/A | PB-11.05 | Mohave Substation: Lugo 500 kV Line Reactor Switcher Replacement | 34.367, -117.370 | Laughlin, Clark County, Nevada | Mohave Substation: Replace Lugo 500kV Line Reactor Switcher with SCU CB, install new lighting in surrounding area of future SCU CB, replace existing homerun cables(control, current) and control panels as required. | Circuit Breaker | Replacement | PB-19.02, PB-18.08 | Infrastructure Replacement | Age/Condition | Annual | 31 (Equipment deactivated on 2/26/2019) | The main analysis used to inform the health of the asset is the Health Index developed from the MDT (Maintenance Decision Tool). The health index is developed using specific data from the assets including fault interruption history, age, maintenance data etc… In addition to the health index, decisions are influenced by a Weibull analysis and subject matter input for conditions not included in the MDT, e.g. possible leaks. | See Note 14A | Out of State | See Note 16C | High Wind Events, Extreme Temperature Conditions, Air particulate levels, High Seismic | Brent Gokbudak, MPO-Project Development & Execution | See Note 19B | 11.5 | 500 kV | 500kV | See Note 23B | 901458035 | CET-ET-IR-CB-421106 | 4211 | See Note 27A | Yes | 2016 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2020 = 2,370 2021 = 21 2022 = 8 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2020-05-26 | No | 2017-12-31 | 2020-10-21 | Outage Restrictions | 284 | 284 | See Note 53A | 2398.4489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 983.3854 | 118.0935 | 1268.5684 | 20.5539 | 7.8477 | 2398.4489 | 390.8689 | See Note 57A | N/A | No project specific cost benefit performed. The Sub IR program for CB and transformers is reliability based with a Weibull curve analysis determining the appropriate number of annual replacements. The justification for the program is described in SCE general rate case submissions. See Note 59A. | 1.1982e-12 | None | 100% | 0% | Column 52: Source= PMWIF (v3 Proj Summary)
N/A | PB-11.06 | Eldorado Substation Line Reactor Switcher Replacement | 35.794, -115.006 | Boulder City, Clark County, Nevada | Eldorado Substation: Replace 500kV Line Reactor Switcher (Lugo 500kV Line Reactor Switcher) | Circuit Breaker | Replacement | PB-11.06, PB-17.05, PB-17.06, PB.18.02, PB-18.04 | Infrastructure Replacement | Age/Condition - Replace Reactors | Annual | 40 years (1980) | The main analysis used to inform the health of the asset is the Health Index developed from the MDT (Maintenance Decision Tool). The health index is developed using specific data from the assets including fault interruption history, age, maintenance data etc… In addition to the health index, decisions are influenced by a Weibull analysis and subject matter input for conditions not included in the MDT, e.g. possible leaks. | See Note 14A | Out of State | See Note 16C | Eldorado substation can experience extreme heat and sandy conditions. | Brent Gokbudak, MPO-Project Development & Execution | See Note 19B | 86.7 | 500 kV | 500kV | See Note 23B | 901884770 | CET-ET-IR-CB-421100 | 4211 | See Note 27A | Yes | 2016 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2020 = 1,656 2021 = 9 2022 = 7 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2020-02-24 | No | 2018-12-31 | 2020-06-15 | Outage Restrictions | 550 | 550 | See Note 53A | 1671.9242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.7252 | 453.9878 | 1100.3908 | 8.6292 | 7.1912 | 1671.9242 | 230.8452 | See Note 57A | N/A | No project specific cost benefit performed. The Sub IR program for CB and transformers is reliability based with a Weibull curve analysis determining the appropriate number of annual replacements. The justification for the program is described in SCE general rate case submissions. See Note 59A. | 4.1535e-13 | None | 100% | 0% | Column 52: Source= PMWIF (v0 Proj Summary)
N/A | PB-11.07 | Vincent Substation CB Replacement | 34.486169;-118.118391 | Palmdale, Los Angeles County | Replace (2) 13.8kV Reactor CBs, (2) 500kV SWs, (3) 500kV CBs | Circuit Breakers & Reactor Circuit Breakers | Replacement | NA | Infrastructure Replacement | Age/Condition - Replace 230/115/70/60 kV Breakers | 2022-05-12 | 500 kV CB #852 - 27 yrs/ 500 kV CB # 862 - 28 yrs/ 500 kV CB #952 - 30 yrs/ 500 kV CAPS CB#716 - 21 yrs/ 500 kV CAPS CB#726 - 21 yrs/ 13.8 kV CB#24 - 11 yrs/ 13.8 kV CB#19 | Replacement due to criticality, age, spare part availability and known equipment issues | See Note 14A | HFTD Tier 3 | See Note 16B | High Wind Events, Extreme Temperature Conditions, High Seismic | Demetric Brown, MPO - Programs | See Note 19B | 46 | See Note 21A | 220 kV | See Note 23B | 902820063 | CET-ET-IR-CB-421100 | 4211 | See Note 27A | Yes | 2019 | 2019 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Construction more than 50% completed | See Note 46A | 2023-02-01 | Yes | 2023-12-31 | 2023-12-29 | N/A | 522 | 522 | See Note 53A | 9624.7291 | 3107.409 | 1652 | 0 | 0 | 0 | 0 | 4759.409 | 0 | 4.4019 | 313.736 | 3050.7637 | 1496.4185 | 4865.3201 | 707.8808 | See Note 57A | N/A | No project specific cost benefit performed. The Sub IR program for CB and transformers is reliability based with a Weibull curve analysis determining the appropriate number of annual replacements. The justification for the program is described in SCE general rate case submissions. See Note 59A. | 4599.4948 | None | 100% | 0% | Column 52: Source = PMWIF (09/08/2019 Investment Summary)
N/A | PB-11.08 | Devers Substation: Replace (2) 500kV CBs | 33.934, -116.578 | North Palm Springs, Riverside County | Devers 500/220kV -Replace (2) 500kV CBs Devers 500/220kV - Replace (2) 500kV CBs (#812 and 922). PIN 4211 ATP received 7/6/20. | Circuit Breaker | Replacement | None | Infrastructure Replacement | Age/Condition | 2022-12-10 | 31 | Replacement due to criticality and age | See Note 14A | Non HFRA | See Note 16C | High Wind Events, Extreme Temperature Conditions | Demetric Brown, MPO - Programs | See Note 19B | 98 | See Note 21A | 500kV, 220kV, 115kV | See Note 23B | 903127976 | CET-ET-IR-CB-421100 | 4211 | See Note 27A | Yes | 2020 | 2021 | Annual Capital Operating Plan Process | N/A | N/A | N/A | N/A | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Construction more than 50% completed | See Note 46A | 2023-01-09 | No | 2022-12-31 | 2024-01-20 | Coordination with other projects and outage constraints | 1658 | 1658 | See Note 53A | 2448.9959 | 966.517 | 60 | 0 | 0 | 0 | 0 | 1026.517 | 0 | 0 | 14.3699 | 30.5678 | 1377.5411 | 1422.4789 | 179.7908 | See Note 57A | N/A | See Note 59A | 1346.9511 | None | 100% | 0% | Column 52: Source= PMWIF (06/16/2020 Investment Summary)
0: N/A; Project Description 1: PB-11.09; Project Description 2: Mira Loma 500/220kV - Replace (5) 13.8kV reactor CBs; Project Description 4: Ontario, San Bernardino County; Project Description 5: Mira Loma-Repl CB R11, R12, R15, R21,R22 Mira Loma 500/220kV Sub: Replace reactor CB R11, R12, R15, R21, R22 PIN 4211 ATP received 9/10/2020.; Project Description 6: Circuit Breaker; Project Description 7: Replacement; Project Description (Cont.) 24: 903171518; Project Description (Cont.) 25: CET-ET-IR-CB-421100; Project Description (Cont.) 26: 4211; Project Status 45: Operational; Project Status 50: 2021-11-05; Costs 52: 468; Costs 52.1: 468; Costs 54: 427.1625 | [16 empty] | Column 52: Source= C55
0: N/A; Project Description 1: PB-11.10; Project Description 2: Lugo 500/220kV - Replace (8) 13.8kV reactor CBs; Project Description 4: Hesperia, San Bernardino County; Project Description 5: Replace (8) 13.8 kV Reactor CBs; Project Description 6: Reactor Circuit Breakers; Project Description 7: Replacement; Project Description (Cont.) 24: 903428435; Project Description (Cont.) 25: CET-ET-IR-CB-421100; Project Description (Cont.) 26: 4211; Project Status 45: Operational; Project Status 50: 2022-11-08; Costs 52: 615.84; Costs 52.1: 615.84; Costs 54: 806.9366 | [16 empty] | Column 52: Source = PMWIF (04/26/2021 Investment Summary)
0: N/A; Project Description 1: PB-11.11; Project Description 2: Devers 500/17.3kV-Replace CB's; Project Description 4: North Palm Springs, Riverside County; Project Description 5: Replace (3) 13.8 kV Reactor CBs; Project Description 6: Reactor Circuit Breakers; Project Description 7: Replacement; Project Description (Cont.) 24: 902760306; Project Description (Cont.) 25: CET-ET-IR-CB-421100; Project Description (Cont.) 26: 4211; Project Status 45: Construction less than 50% completed; Project Status 50: 2024-03-29; Costs 52: 1272.024; Costs 52.1: 1272.024; Costs 54: 1334.4726 | [16 empty] | Column 52: Source = PMWIF (06/27/2019 Investment Summary)
0: N/A; Project Description 1: PB-11.12; Project Description 2: Mira Loma 500/220kV - Replace (2) 500kV CBs; Project Description 4: Ontario, San Bernardino County; Project Description 5: Replace (2) 500 kV CBs; Project Description 6: Circuit Breakers; Project Description 7: Replacement; Project Description (Cont.) 24: 903700154; Project Description (Cont.) 25: CET-ET-IR-CB-421100; Project Description (Cont.) 26: 4211; Project Status 45: Engineering more than 50% Completed; Project Status 50: 2024-06-01; Costs 52: 1699.519; Costs 52.1: 1699.519; Costs 54: 2750.031 | [16 empty] | Column 52: Source = PMWIF (03/23/2022 Investment Summary)
N/A | PB-11.14 | Moorpark 220/66kV - Moorpark 220/66kV: Replace (2) 220kV CB #39 & #51 | 34.281, -118.903 | Moorpark, Ventura County | Moorpark 220/66kV: Replace (2) 220kV CB #39 & #51 • Replace Ormond Beach No.1 CB#39/4082 (Pos 8) • Replace Ormond Beach No.4 CB#51/ 4112 (Pos 11) | Bulk Circuit Breaker | Replacement | None | Infrastructure Replacement | Age/Condition - Replace Other Substation Equipment | 2022-03-05 | 54 | Replacement due to criticality, age, spare part availability and known equipment issues | See Note 14A | Tier 3 | See Note 16B | No Significant Environmental Factors | Demetric Brown, MPO - Programs | See Note 19B | 40 | See Note 21A | 220kV/66kV/12kV | See Note 23B | 903456915 | CET-ET-IR-CB-421100 | 4211 | See Note 27A | Yes | 2021 | 2022 | Annual Capital Operating Plan Process | N/A | N/A | N/A | N/A | See Col. 37 | 2022 = 1,284 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2022-04-01 | Yes | 2022-12-31 | 2022-06-15 | N/A | 587 | 587 | See Note 53A | 1283.6588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.6169 | 1217.0419 | 1283.6588 | 285.6533 | See Note 57A | N/A | See Note 59A | 3.1094e-13 | None | 100% | 0% | Column 52: Source = PMWIF (06/01/2021 Investment Summary)
0: N/A; Project Description 1: PB-11.15; Project Description 2: Vincent 500/220kV - Vincent 500/220kV: Replace (7) 13.8kV Reactor CBs; Project Description 4: Palmdale, Los Angeles County; Project Description 5: Vincent 500/220kV: Replace (8) Reactor 13.8kV CBs (#11, 12, 13, 14, 41, 42, 43 & 44) REACTOR 11 13.8KV CB - #R11 REACTOR 12 13.8KV CB- #R12 REACTOR 14 13.8KV CB - #R13 REACTOR 14 13.8KV CB - #R14 REACTOR 41 13.8KV CB - #R41 REACTOR 42 13.8KV CB - #R42 REACTOR 43 13.8KV CB - #R43 REACTOR 44 13.8KV CB - #R44; Project Description 6: Bulk Circuit Breaker; Project Description 7: Replacement; Project Description (Cont.) 24: IWP003006.32F-01; Project Description (Cont.) 25: CET-ET-IR-CB-421100; Project Description (Cont.) 26: 4211; Project Status 45: Planning; Project Status 50: 2026-06-11; Costs 52: 4444; Costs 52.1: 4444; Costs 54: 4555.311 | [16 empty] | Column 52: Source = Investment Summary dated 05/18/2023
N/A | PB-12 | Non-Bulk Circuit Breaker Replacement - 115 kV & Below | Not applicable at program level | Not applicable at program level | This program contains projects that proactively replace non-bulk CBs. | Circuit Breakers | Replacement | Not applicable at program level | Infrastructure Replacement | Age/Condition - Replace 230/115/70/60 kV Breakers | Not applicable at program level | Not applicable at program level | The main analysis used to inform the health of the asset is the Health Index developed from the MDT (Maintenance Decision Tool). The health index is developed using specific data from the assets including fault interruption history, age, maintenance data etc… In addition to the health index, decisions are influenced by a Weibull analysis and subject matter input for conditions not included in the MDT, e.g. possible leaks. | Not applicable at program level | Not applicable at program level | See Note 16C | Not applicable at program level | Demetric Brown, MPO - Programs | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 23B | Not applicable at program level | CET-ET-IR-CB-432911 | 4329 | See Note 27A | Not applicable at program level | Not applicable at program level | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | Not applicable at program level | Not applicable at program level | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Not applicable at program level | See Note 46A | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 53A | Not applicable at program level | 0 | 0 | 0 | 0 | 0 | Not Available | 0 | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not applicable at program level | Not applicable at program level | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | See Note 60A | None | 0% | 100%
N/A | PB-13 | Sub Relay Replacement Program (SRRP) - 115kV & below | Not applicable at program level | Not applicable at program level | This program replaces aged and obsolete electromechanical protective relays with new IED for added functionality and improved system reliability. | Substation Relay Protection | Replacement | Not applicable at program level | Other - See Notes | Age/Condition | Multiple equipment covered under this program . Inspections vary base on type of equipment and voltage application (6 years or 12 years interval) | Not applicable at program level | The main analysis used to inform the health of the asset is the Health Index developed from the MDT (Maintenance Decision Tool). The health index is developed using specific data from the assets including fault interruption history, age, maintenance data etc… In addition to the health index, decisions are influenced by a Weibull analysis and subject matter input for conditions not included in the MDT, e.g. possible leaks. | Not applicable at program level | Not applicable at program level | See Note 16B | Not applicable at program level | Demetric Brown, MPO - Programs | Not applicable at program level | Not applicable at program level | 115kV, 66kV, 55kV | Not applicable at program level | See Note 23B | Not applicable at program level | CET-ET-IR-RP-434301 | 4343 | See Note 27A | Not applicable at program level | Not applicable at program level | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | Not applicable at program level | Not applicable at program level | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Not applicable at program level | See Note 46A | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 53A | Not applicable at program level | 46.815 | 0 | 0 | 0 | 0 | Not Available | 46.815 | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not applicable at program level | Not applicable at program level | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | See Note 60A | None | 100% | 0% | Column 9: Asset Condition Column 12: Generally these assets being replaced are > 30 Years
N/A | PB-13.01 | Laguna Bell Substation Relay Replacement | 33.976, -118.148 | Commerce, Los Angeles County | Replace 18 220kV relays at Laguna Bell Substation | Replace LBFB Relays | Replace LBFB Relays | None | Infrastructure Replacement | Age/Condition | 2020-03-10 | 27.0603 | Replacement due to criticality, age, spare part availability and known equipment issues | Bundled with other work at substation; Also see Note 14A | Non-HFRA | See Note 16C | No significant environmental factors | Demetric Brown, MPO - Programs | See Note 19B | 25.2 | 220 kV, 66 kV | 220 kV, 66 kV | See Note 23B | 900994658 | CET-ET-IR-RP-434300 | 4343 | See Note 27A | Yes | 2012 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2019 = 5,273 2020 = -97 2021 = -1 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2018-05-15 | No | 2015-12-31 | 2019-05-14 | Due to the number of relays replaced and the difficulty of installation | 1310 | 1310 | See Note 53A | 5175.0973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4151.0889 | 1122.3813 | -97.3383 | -1.0345 | 0 | 5175.0973 | 948.4073 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | 1.5621e-13 | None | 100% | 0% | Column 23: Age Index utilized Column 52: Source= PMWIF (v0 Proj Summary)
N/A | PB-13.02 | Inyo SCE Substation: Replace the existing KD & JBCG relays | 37.342267;-118.440875 | Inyokern, Inyo County | Replace the existing KD and JBCG relays with one (1). SEL-311L relay for Line Differential and Backup protection functions (21/67G/87L). Replace the existing HCB relays with one (1) GE L90 relay for Line Differential and Backup protection functions | Relay Protection | Replacement | NA | Infrastructure Replacement | Age/Condition - Replace Relays | 05/05/2021 | JBCG-54 - 19 years/JBCG-99 - 21 Years/KD-4 - 21 Years/ KD-10 - 15 years | Replacement due to criticality, age, spare part availability and known equipment issues | See Note 14A | HFTD Tier 2 | See Note 16B | Extreme Temperature Conditions | Demetric Brown, MPO - Programs | See Note 19B | 1.53 | See Note 21A | 220kV/115kV | See Note 23B | 902661408 | CET-ET-IR-RP-434301 | 4343 | See Note 27A | Yes | 2019 | 2019 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2021 = 1,050 2022 = 25 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2021-06-07 | No | 2020-12-31 | 2021-10-18 | Coordination with Other Work and Scope Increase | 167.439 | 167.439 | See Note 53A | 1074.843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.3423 | 185.6733 | 773.2847 | 24.5426 | 1074.843 | 232.8043 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | -3.0045e-13 | None | 100% | 0% | Column 52: Source = PMWIF (03/28/2019 Investment Summary)
N/A | PB-14 | Substation Automation System Infrastructure Replacements | Not applicable at program level | Not applicable at program level | Replacement of legacy first generation Substation Automation Systems (SA-1) and legacy Remote Terminal Units (RTU) and Programmable Logic Controllers (PLC) in non-SA-1 stations | Replacement of legacy first generation Substation Automation Systems (SA-1) and legacy Remote Terminal Units (RTU) and Programmable Logic Controllers (PLC) in non-SA-1 stations | Replacement | Not applicable at program level | Infrastructure Replacement | Age/Condition | Not applicable at program level | Not applicable at program level | Equipment failure rate and obsolescence. Evaluation of SCE's ability to replace equipment that has reached end of life, Manufacturer support and availability. | Not applicable at program level | Not applicable at program level | See Note 16C | Not applicable at program level | Demetric Brown, MPO - Programs | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 23B | Not applicable at program level | CET-ET-IR-RP-483701 | 4837 | See Note 27A | Not applicable at program level | Not applicable at program level | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | Not applicable at program level | Not applicable at program level | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Not applicable at program level | See Note 46A | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 53A | Not applicable at program level | 1228.357 | 0 | 0 | 6000 | 7000 | Not Available | 14228.357 | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not applicable at program level | Not applicable at program level | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | See Note 60A | None | 100% | 0%
0: N/A; Project Description 1: PB-14.01; Project Description 2: Rector Substation: Replace Systems Northwest IR8600 RTU(3) 'RECTOR', 'RECTOR B', 'RECTOR C' & PLC W/; Project Description 4: Visalia, Tulare County; Project Description 5: Replacement of legacy first generation Substation Automation Systems (SA-1) and legacy Remote Terminal Units (RTU) and Programmable Logic Controllers (PLC) in non-SA-1 stations; Project Description 6: RTUs; Project Description 7: Replacement; Project Description (Cont.) 24: 902577763; Project Description (Cont.) 25: CET-ET-IR-RP-483701; Project Description (Cont.) 26: 4837; Project Status 45: Canceled; Project Status 50: Canceled; Costs 52: 522; Costs 52.1: 522; Costs 54: 0 | [16 empty] | Column 52: Source= PMWIF (v1 Project Summary)
N/A | PB-14.02 | Pastoria Substation: Replace existing rack annunciator | 34.935, -118.843 | Grapevine, Kern County | Replace existing 2 rack annunciator with 1 rack annunciator | Rack Annunciator | Replacement | None | Infrastructure Replacement | Age/Condition - Replace Other Substation Equipment | 11/03/2021 | 21 | Replacement due to criticality, age, spare part availability and known equipment issues | See Note 14A | Non HFRA | See Note 16C | Extreme Temperature Conditions, Landslide, High Seismic | Demetric Brown, MPO - Programs | See Note 19B | 4.6 | See Note 21A | 220 kV | See Note 23B | 902471000 | CET-ET-IR-RP-483701 | 4837 | See Note 27A | Yes | 2018 | 2020 | Annual Capital Operating Plan Process | N/A | N/A | N/A | N/A | See Col. 37 | 2022 = 1,183 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2021-11-24 | Yes | 2020-12-31 | 2022-02-25 | Coordination with other projects and Scope Increase | 472.496 | 472.496 | See Note 53A | 1183.4336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.6426 | 216.1847 | 600.1908 | 357.4156 | 1183.4336 | 273.6852 | See Note 57A | N/A | See Note 59A | 3.6823e-13 | None | 100% | 0% | Column 52: Source = PMWIF (Project Summary V.0)
N/A | PB-14.04 | Magunden 500/220 (T): RPL Systems Northwest IR8600 RTU(1) 'MAGUNDEN' & PLC W/ the latest standards | 35.361, -118.922 | Bakersfield, Kern County | Magunden 500/220 (T): Replace Systems Northwest IR8600 RTU(1) 'MAGUNDEN' and PLC with the latest standards. Note: There are 2 RTUs at MAGUNDEN MAGUNDEN (SNW CDC 80’s vintage RTU) – mounted in cubicle style enclosure. MAGUNDEN_B (DAQ DNP Late Model RTU ) – mounted in cubicle style enclosure. | Substation Monitoring & Control System (SAS) | Replacement | None | Infrastructure Replacement | Age/Condition - Replace Other Substation Equipment | 09/17/2021 | 33 | Replacement due to criticality, age, spare part availability and known equipment issues | See Note 14A | Non HFRA | See Note 16C | High Fire Area, Flooding, Moderate Seismic | Demetric Brown, MPO - Programs | See Note 19B | 15.3 | See Note 21A | 220 kV, 66 kV | See Note 23B | 902894696 | CET-ET-IR-RP-483701 | 4837 | See Note 27A | Yes | 2019 | 2021 | Annual Capital Operating Plan Process | N/A | N/A | N/A | N/A | See Col. 37 | 2023 = 1,637 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2021-10-04 | Yes | 2021-12-31 | 2023-06-28 | Coordination with other projects and scope increase | 300 | 300 | See Note 53A | 1673.2818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125.0242 | 696.7392 | 851.5184 | 1673.2818 | 360.5041 | See Note 57A | N/A | See Note 59A | 1292.3215 | None | 100% | 0% | Column 52: Source = PMWIF (11/25/2019 Investment Summary)
N/A | PB-15 | Coupling Capacitor Voltage Transformer Replacements | Not applicable at program level | Not applicable at program level | This program addresses replacement needs for coupling capacitor voltage transformers, which are used for stepping down high voltage to low voltage signals for metering or relay inputs. | Not applicable at program level | Replacement | Not applicable at program level | Infrastructure Replacement | Age/Condition | Not applicable at program level | Not applicable at program level | replacement due to criticality, age, spare part availability and known equipment issues | Not applicable at program level | Not applicable at program level | See Note 16C | Not applicable at program level | Brent Gokbudak, MPO-Project Development & Execution | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 23B | Not applicable at program level | CET-ET-IR-ME-448400 | 4484 | See Note 27A | Not applicable at program level | Not applicable at program level | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | Not applicable at program level | Not applicable at program level | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Not applicable at program level | See Note 46A | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 53A | Not applicable at program level | 0 | 0 | 0 | 0 | 0 | Not Available | 0 | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not applicable at program level | Not applicable at program level | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | See Note 60A | None | 48.23% | 51.77% | Column 23: Work is scheduled based on review of age, service life, and results of inspections
N/A | PB-15.01 | Kramer Substation CCVT Replacement | 34.989, -117.541 | Kramer, San Bernardino County | Kramer Substation: Replace (1) set of 220kV CCVTs (South 220kV Bus); Replace (4) sets of 115kV CCVTs (No.1A Bank 115kV, No.2A Bank 115kV, Sungen 115kV Line, Tortilla 115kV Line); Replace (6) total 115kV bus PTs (North and South Bus); Replace (24) total 220kV lightning arresters (North and South Bus) | CCVTs | Replacement | None | Infrastructure Replacement | Age/Condition | 2016 | 19 | Replacement due to criticality, age, spare part availability and known equipment issues | Emergent replacement after equipment failure | Non-HFRA | See Note 16C | Heat | Demetric Brown, MPO - Programs | See Note 19B | 20.6 | 230 | 220kV, 115kV | See Note 23B | 901115642 | CET-ET-IR-ME-448400 | 4484 | See Note 27A | Yes | 2014 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2017 = 1,369 2018 = 2 2019 = 48 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2016-05-16 | No | 2016-12-31 | 2017-01-24 | N/A | 1350 | 1350 | See Note 53A | 1419.6091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1371.1612 | 48.4986 | -0.050701 | 0 | 0 | 1419.6091 | 289.6381 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | -8.495e-13 | None | 48.23% | 51.77% | Column 23: Work is scheduled based on review of age, service life, and results of inspections Column 52: Source= Unverified estimate; documents not readily available
N/A | PB-16 | Substation Miscellaneous Equipment Additions & Betterment | Not applicable at program level | Not applicable at program level | This activity involves planned maintenance that is typically driven by substation inspection and maintenance programs to indicate imminent equipment failure or possible safety issues. | Substation Maintenance | Replacement | Not applicable at program level | Infrastructure Replacement | Age/Condition | Not applicable at program level | Not applicable at program level | Replacement due to criticality, age, spare part availability and known equipment issues | Not applicable at program level | Not applicable at program level | See Note 16C | Not applicable at program level | Demetric Brown, MPO - Programs | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 23B | Not applicable at program level | CET-ET-IR-ME-475600 | 4756 | See Note 27A | Not applicable at program level | Not applicable at program level | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | Not applicable at program level | Not applicable at program level | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Not applicable at program level | See Note 46A | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 53A | Not applicable at program level | 8022.3476 | 10798.693 | 12883.459 | 2930 | 0 | Not Available | 34634.4996 | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not applicable at program level | Not applicable at program level | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | See Note 60A | None | 100% | 0% | Column 23: This activity involves planned maintenance that is typically driven by substation inspection and maintenance programs to indicate imminent equipment failure or possible safety issues. All equipment classes, including the major equipment categories (circuit breakers, transformers and relays) can be replaced for reactive reasons in this category. These replacements are predominantly like-for-like replacement with limited engineering. Equipment that is identified as requiring replacement must be replaced in a timely manner because substation equipment failures may lead to prolonged outages, unsafe operating conditions, or more expensive reactive solutions.
N/A | PB-16.01 | Pardee Substation Disconnect Replacement (1) | 34.440, -118.578 | Valencia, Los Angeles County | Pardee Substation: Replace (10) set of 220kV disconnects associated with Pos. 5 and 6 including ground disconnect (Bus and line discs w/grounds to CB 4052 and 4062, bus and line discs to CB 6052 and 6062, line and line discs to CB 5062) | Disconnect Switch | Replacement | PB-16.03, PB-16.22 | Infrastructure Replacement | Age/Condition | 2015-09-30 | Exact age is presently unknown; however, based on vintage, the age is likely ~50 years | Replacement due to criticality, age, spare part availability and/or known equipment issues; See Note 14A | Replacement due to criticality, age, spare part availability and/or known equipment issues; See Note 14A | Tier 3 | See Note 16C | Substation can be impacted by temperature extremes and seismic activity. | Demetric Brown, MPO - Programs | See Note 19B | 29.4 | See Note 21A | 220 kV | See Note 23B | 900994810 | CET-ET-IR-ME-475600 | 4756 | See Note 27A | Yes | 2014 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2015 = 2,755 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2015-05-13 | No | 2015-12-31 | 2015-10-20 | N/A | 2145 | 1868.0741 | See Note 53A | 2755 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 2755 | 0 | 0 | 0 | 0 | 2755 | 564.5543 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | 3.1305e-12 | None | 100% | 0% | Column 23: This activity involves planned maintenance that is typically driven by substation inspection and maintenance programs to indicate imminent equipment failure or possible safety issues. All equipment classes, including the major equipment categories (circuit breakers, transformers and relays) can be replaced for reactive reasons in this category. These replacements are predominantly like-for-like replacement with limited engineering. Equipment that is identified as requiring replacement must be replaced in a timely manner because substation equipment failures may lead to prolonged outages, unsafe operating conditions, or more expensive reactive solutions Column 52: Source= Unverified estimate; documents not readily available
N/A | PB-16.02 | Pisgah Substation Disconnect Replacement | 34.781, -116.384 | Ludlow, San Bernardino County | Pisgah 220/220(T): Replace 220kV Line Disconnects connected to CB 642, CB 442, CB 452, CB 652 (8 Sets of Disconnects) | Line Disconnect | Replacement | None | Infrastructure Enhancement | Age/Condition | 2015 | Exact age is presently unknown | Replacement due to criticality, age, spare part availability and known equipment issues | Emergent replacement after equipment failure; See Note 14A | Non-HFRA | See Note 16C | High Wind Events, Extreme Temperature Conditions, Air particulate levels, High Seismic | Demetric Brown, MPO - Programs | See Note 19B | 1.6 | 230 | 220kV | See Note 23B | 901385762 | CET-ET-IR-ME-475600 | 4756 | See Note 27A | Yes | 2014 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2015 = 1,674 2016 = 42 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2015-07-06 | No | 2015-12-31 | 2015-08-26 | N/A | 1386 | 1386 | See Note 53A | 1715.931 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 1715.931 | 0 | 0 | 0 | 0 | 1715.931 | 135.9807 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | 2.1771e-13 | None | 100% | 0% | Column 23: This activity involves planned maintenance that is typically driven by substation inspection and maintenance programs to indicate imminent equipment failure or possible safety issues. All equipment classes, including the major equipment categories (circuit breakers, transformers and relays) can be replaced for reactive reasons in this category. These replacements are predominantly like-for-like replacement with limited engineering. Equipment that is identified as requiring replacement must be replaced in a timely manner because substation equipment failures may lead to prolonged outages, unsafe operating conditions, or more expensive reactive solutions. Column 52: Source= Unverified system estimate
N/A | PB-16.03 | Pardee Substation Disconnect Replacement (2) | 34.440, -118.578 | Valencia, Los Angeles County | Pardee Substation: Replace (28) sets of 220kV disconnects associated with Pos. 7, 9, 10, 15, and 19 including ground disconnect (220kV Disconnects associated with Pos. 7, 9, 10, 15 and 19 including ground disconnect) | Disconnect Switch | Replacement | PB-16.01, PB-16.22 | Infrastructure Replacement | Age/Condition | 2017-08-10 | Exact age is presently unknown; however, based on vintage, the age is likely ~50 years | Replacement due to criticality, age, spare part availability and/or known equipment issues | Emergent replacement after equipment failure; See Note 14A | Tier 3 | See Note 16C | Substation can be impacted by temperature extremes and seismic activity. | Demetric Brown, MPO - Programs | See Note 19B | 29.4 | See Note 21A | 220 kV | See Note 23B | 901531606 | CET-ET-IR-ME-475600 | 4756 | See Note 27A | Yes | 2015 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2017 = 4,682 2018 = 29 2019 = 8 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2017-03-27 | No | 2017-12-31 | 2017-08-28 | N/A | 6663 | 5802.7867 | See Note 53A | 4718.8161 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 4710.799 | 8.0171 | -2.0955e-13 | 0 | 0 | 4718.8161 | 938.8992 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | 1.8476e-12 | None | 100% | 0% | Column 23: This activity involves planned maintenance that is typically driven by substation inspection and maintenance programs to indicate imminent equipment failure or possible safety issues. All equipment classes, including the major equipment categories (circuit breakers, transformers and relays) can be replaced for reactive reasons in this category. These replacements are predominantly like-for-like replacement with limited engineering. Equipment that is identified as requiring replacement must be replaced in a timely manner because substation equipment failures may lead to prolonged outages, unsafe operating conditions, or more expensive reactive solutions. Column 52: Source= Unverified estimate; documents not readily available
N/A | PB-16.04 | Vincent Substation Protection System Upgrade | 34.486, -118.116 | Palmdale, Los Angeles County | Vincent 500/220 (T)(Phase 1/2): Upgrade/Replace the protection system for the Midway No. 1 & No. 2 series capacitor (2 protection systems) | Series Capacitor Protection System Replacement | Replacement/Upgrade | PB-16.18, PB-11.03, PB-11.01, PB-19.01, PB-18.01 | Infrastructure Replacement | Age/Condition | 2017-11-18 | 18 | Replacement due to criticality, age, spare part availability and/or known equipment issues | Emergent replacement after equipment failure; See Note 14A | Tier 3 | See Note 16C | The asset’s service life can be affected by the following environmental factors; high corrosive soils, weather climates, airborne contamination, and pollution. | Demetric Brown, MPO - Programs | See Note 19B | 49.4 | 500 | 500/220kV | See Note 23B | 901613911 | CET-ET-IR-ME-475600 | 4756 | See Note 27A | Yes | 2016 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2018 = 8,985 2019 = 928 2020 = 8 2021 = 14 2022 = 11 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2017-11-22 | No | 2017-12-31 | 2018-10-09 | Added Phase 2 Scope to Phase 1 | 13087 | 13087 | See Note 53A | 9946.2046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8985.1085 | 927.9575 | 7.9776 | 14.0313 | 11.1297 | 9946.2046 | 1083.7951 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | -1.4094e-11 | None | 100% | 0% | Column 23: This activity involves planned maintenance that is typically driven by substation inspection and maintenance programs to indicate imminent equipment failure or possible safety issues. All equipment classes, including the major equipment categories (circuit breakers, transformers and relays) can be replaced for reactive reasons in this category. These replacements are predominantly like-for-like replacement with limited engineering. Equipment that is identified as requiring replacement must be replaced in a timely manner because substation equipment failures may lead to prolonged outages, unsafe operating conditions, or more expensive reactive solutions Column 52: Source= Unverified estimate; documents not readily available
N/A | PB-16.05 | Midway Substation Protection System Replacement | 35.402, -119.453 | Buttonwillow, Kern County | Midway 500/220 (F)(Phase 3/4): Upgrade/Replace the protection system for the Vincent No. 1 series capacitor & Whirlwind series capacitor (2 protection systems) | Series Capacitor Protection System | Replacement | PB-16.06 | Infrastructure Replacement | Age/Condition | 2016 | 19 | Replacement due to criticality, age, spare part availability and/or known equipment issues | Emergent replacement after equipment failure; See Note 14A | Non-HFRA | See Note 16C | The asset’s service life can be affected by the following environmental factors; high corrosive soils, weather climates, airborne contamination, and pollution. | Demetric Brown, MPO - Programs | See Note 19B | 93.8 | 500 | 500 kV | See Note 23B | 901819252 | CET-ET-IR-ME-475600 | 4756 | See Note 27A | Yes | 2016 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2019 = 9,943 2020 = 1,460 2021 = 238 2022 = 11 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2019-01-08 | No | 2019-01-08 | 2019-08-01 | Scope Increase | 13276 | 13276 | See Note 53A | 11652.0611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4252.9959 | 5689.7077 | 1460.4952 | 237.6305 | 11.2318 | 11652.0611 | 1621.64 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | 9.9908e-13 | None | 100% | 0% | Column 23: This activity involves planned maintenance that is typically driven by substation inspection and maintenance programs to indicate imminent equipment failure or possible safety issues. All equipment classes, including the major equipment categories (circuit breakers, transformers and relays) can be replaced for reactive reasons in this category. These replacements are predominantly like-for-like replacement with limited engineering. Equipment that is identified as requiring replacement must be replaced in a timely manner because substation equipment failures may lead to prolonged outages, unsafe operating conditions, or more expensive reactive solutions. Column 52: Source= Unverified estimate; documents not readily available
N/A | PB-16.06 | Midway Substation Disconnect Replacement | 35.402, -119.453 | Buttonwillow, Kern County | Midway 500/220 (F): Replace 2 sets of disconnects for the Vincent #1 series capacitor Replace 2 sets of disconnects for the Whirlwind series capacitor | Disconnects | Replacement | PB-16.05 | Infrastructure Replacement | Age/Condition | 2016 | exact age is unknown, based on vintage age is about 60 years | Replacement due to criticality, age, spare part availability and/or known equipment issues | Emergent replacement after equipment failure; See Note 14A | Non-HFRA | See Note 16C | High Seismic Area | Demetric Brown, MPO - Programs | See Note 19B | 93.8 | 500 | 500 kV | See Note 23B | 902099218 | CET-ET-IR-ME-475600 | 4756 | See Note 27A | Yes | 2017 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2019 = 2,719 2020 = 37 2021 = 2 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2018-08-14 | No | 2018-12-31 | 2019-06-06 | N/A | 1438 | 1438 | See Note 53A | 2758.0828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1220.8498 | 1498.2404 | 36.8836 | 2.109 | 0 | 2758.0828 | 594.0299 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | -4.0643e-12 | None | 100% | 0% | Column 23: This activity involves planned maintenance that is typically driven by substation inspection and maintenance programs to indicate imminent equipment failure or possible safety issues. All equipment classes, including the major equipment categories (circuit breakers, transformers and relays) can be replaced for reactive reasons in this category. These replacements are predominantly like-for-like replacement with limited engineering. Equipment that is identified as requiring replacement must be replaced in a timely manner because substation equipment failures may lead to prolonged outages, unsafe operating conditions, or more expensive reactive solutions Column 52: Source= C55
N/A | PB-16.07 | Mira Loma Substation Disconnect Replacement | 34.006, -117.560 | Ontario, San Bernardino County | Mira Loma 500/220 (T) – Replace (23) sets of 220kV group-operated disconnects | Disconnects | Replacement | PB-19.05, PB-18.09 | Infrastructure Replacement | Age/Condition | 2019-05-11 | 30 | Replacement due to criticality, age, spare part availability and/or known equipment issues | Emergent replacement after equipment failure; See Note 14A | Non-HFRA | See Note 16C | Fairly temperate climate; subject to occasional annual storms | Demetric Brown, MPO - Programs | See Note 19B | 102.1 | 220 | 220 kV | See Note 23B | 902419335 | CET-ET-IR-ME-475600 | 4756 | See Note 27A | Yes | 2018-06-13 | 2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2020 = 4,436 2021 = -2 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2019-06-17 | No | 2020-06-01 | 2020-02-25 | N/A | 3001 | 3001 | See Note 53A | 4434.0171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.6306 | 3857.917 | 486.0238 | -1.5544 | 0 | 4434.0171 | 610.1518 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | 1.5975e-12 | None | 100% | 0% | Column 23: This activity involves planned maintenance that is typically driven by substation inspection and maintenance programs to indicate imminent equipment failure or possible safety issues. All equipment classes, including the major equipment categories (circuit breakers, transformers and relays) can be replaced for reactive reasons in this category. These replacements are predominantly like-for-like replacement with limited engineering. Equipment that is identified as requiring replacement must be replaced in a timely manner because substation equipment failures may lead to prolonged outages, unsafe operating conditions, or more expensive reactive solutions. Column 52: Source= Unverified system estimate
N/A | PB-16.08 | Eldorado Substation Line Reactor Replacement | 35.794, -115.006 | Boulder City, Clark County, Nevada | Eldorado Substation: Replace Lugo 500kV Line Reactor | Line Reactor | Replacement | PB-11.06, PB-17.05, PB-17.06, PB.18.02, PB-18.04 | Infrastructure Replacement | Age/Condition | 2020-02-08 | 30 | Replacement due to criticality, age, spare part availability and/or known equipment issues | Emergent replacement after equipment failure; See Note 14A | Out of State | See Note 16C | Eldorado substation can experience extreme heat and sandy conditions. | Brent Gokbudak, MPO-Project Development & Execution | See Note 19B | 86.7 | 500 | 500 kV | See Note 23B | 902146489 | CET-ET-IR-ME-475600 | 4756 | See Note 27A | Yes | 2017-05-25 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2020 = 7,995 2021 = 29 2022 = 5 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2020-02-24 | No | 2019-12-31 | 2020-06-15 | Refinement of schedule for this project | 1744 | 1744 | See Note 53A | 8029.0919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160.8753 | 3042.3915 | 4791.5123 | 29.2143 | 5.0985 | 8029.0919 | 859.9897 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | 4.6058e-12 | None | 100% | 0% | Column 23: This activity involves planned maintenance that is typically driven by substation inspection and maintenance programs to indicate imminent equipment failure or possible safety issues. All equipment classes, including the major equipment categories (circuit breakers, transformers and relays) can be replaced for reactive reasons in this category. These replacements are predominantly like-for-like replacement with limited engineering. Equipment that is identified as requiring replacement must be replaced in a timely manner because substation equipment failures may lead to prolonged outages, unsafe operating conditions, or more expensive reactive solutions. Column 52: Source= PMWIF (v0 Proj Summary)
N/A | PB-16.09 | Mohave Substation Line Reactor Replacement (1) | 35.148, -114.592 | Laughlin, Clark County, Nevada | Mohave 12/500 (G) - Replace Lugo 500kV Line Reactor | Line Reactor | Replacement | PB-11.04, PB-16.10 | Infrastructure Replacement | Age/Condition | 2020-05-14 | 22 | Replacement due to criticality, age, spare part availability and/or known equipment issues | Emergent replacement after equipment failure; See Note 14A | Out of State | See Note 16C | Extreme heat and sandy conditions | Brent Gokbudak, MPO-Project Development & Execution | See Note 19B | 11.5 | 500 | 500 kV | See Note 23B | 902141769 | CET-ET-IR-ME-475600 | 4756 | See Note 27A | Yes | 2017-05-23 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2020 = 7,606 2021 = -109 2022 = 61 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2020-05-26 | No | 2018-12-31 | 2020-10-20 | Refinement of schedule for this project | 1744 | 1744 | See Note 53A | 7557.9048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188.1212 | 2457.8617 | 4959.8637 | -108.6246 | 60.6829 | 7557.9048 | 797.2778 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | -1.6391e-11 | None | 100% | 0% | Column 23: This activity involves planned maintenance that is typically driven by substation inspection and maintenance programs to indicate imminent equipment failure or possible safety issues. All equipment classes, including the major equipment categories (circuit breakers, transformers and relays) can be replaced for reactive reasons in this category. These replacements are predominantly like-for-like replacement with limited engineering. Equipment that is identified as requiring replacement must be replaced in a timely manner because substation equipment failures may lead to prolonged outages, unsafe operating conditions, or more expensive reactive solutions. Column 52: Source= PMWIF (v0 Proj Summary)
N/A | PB-16.10 | Lugo Substation: Replace UPR Relays | 34.367, -117.370 | Hesperia, San Bernardino County | Lugo 500/200kV: Replace (8) 13.8kV UPR Relays associated with Neutral Reactors | Line Reactor | Replacement | PB-11.04, PB-16.09 | Infrastructure Replacement | Age/Condition | 2018-09-23 | 10 | Replacement due to criticality, age, spare part availability and/or known equipment issues | See Note 14A | Non-HFRA | See Note 16C | High Wind Events, Extreme Temperature Conditions, Air particulate levels, High Seismic | Brent Gokbudak, MPO-Project Development & Execution | See Note 19B | 46 | 500 | 500 kV | See Note 23B | 900994818 | CET-ET-IR-ME-475601 | 4756 | See Note 27A | Yes | 2013-12-11 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2019 = 1,097 2020 = 8 2021 = -35 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2018-09-24 | No | 2015-12-31 | 2019-12-16 | Outage Restrictions | 480 | 480 | See Note 53A | 1070.0081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 799.9327 | 296.73 | 8.2457 | -34.9003 | 0 | 1070.0081 | 214.1216 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | -6.6833e-13 | None | 100% | 0% | Column 2: SCE has corrected the project name. Previously listed as "Mohave Substation Line Reactor Replacement" Column 23: This activity involves planned maintenance that is typically driven by substation inspection and maintenance programs to indicate imminent equipment failure or possible safety issues. All equipment classes, including the major equipment categories (circuit breakers, transformers and relays) can be replaced for reactive reasons in this category. These replacements are predominantly like-for-like replacement with limited engineering. Equipment that is identified as requiring replacement must be replaced in a timely manner because substation equipment failures may lead to prolonged outages, unsafe operating conditions, or more expensive reactive solutions. Column 52: Source= Unverified system estimate
N/A | PB-16.11 | Center Substation 220 kV Disconnect Replacement | 33.929, -118.105 | Norwalk, Los Angeles County | Center 220/66 (S): RPL various sets of 220kV disconnects. Disconnects to be replaced: Olinda North & | Disconnects | Replacement | None | Infrastructure Replacement | Age/Condition - Replace Other Substation Equipment | 10/03/2022 | 62+ | Replacement due to criticality, age, spare part availability and/or known equipment issues | See Note 14A | Non HFRA | See Note 16C | High Seismic | Demetric Brown, MPO - Programs | See Note 19B | 25.5 | See Note 21A | 220kV/66kV/12kV | See Note 23B | 902527401 | CET-ET-IR-ME-475600 | 4756 | See Note 27A | Yes | 2018 | 2020 | Annual Capital Operating Plan Process | N/A | N/A | N/A | N/A | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Construction more than 50% completed | See Note 46A | 2022-10-24 | Yes | 2020-12-31 | 2023-12-29 | Coordination with other projects | 2013 | 2013 | See Note 53A | 1629.9125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.4758 | 789.2489 | 139.0908 | 649.097 | 1629.9125 | 409.3918 | See Note 57A | N/A | See Note 59A | 1540.7358 | None | 100% | 0% | Column 52: Source = PMWIF (Project Summary V.0)
0: N/A; Project Description 1: PB-16.12; Project Description 2: Eldorado Substation Upgrades; Project Description 4: Boulder City, Clark County, Nevada; Project Description 5: Eldorado 550/220 (T):Eldorado - Moenkopi 500 kV Line High Voltages The following work needs to be completed •Insulation coordination ($50K) •Arrester rating ($100K) •CCVT’s in SCE 500 kV system cannot withstand 600 kV rms overvoltage. 500kV CCVT’s have a; Project Description 6: Arrestors and CCVTs; Project Description 7: Replacement; Project Description (Cont.) 24: 903027474; Project Description (Cont.) 25: CET-ET-IR-ME-475600; Project Description (Cont.) 26: 4756; Project Status 45: Canceled; Project Status 50: Canceled; Costs 52: 2354; Costs 52.1: 2354; Costs 54: 35.3571 | [16 empty] | Column 52: Source= PMWIF (C55)
N/A | PB-16.13 | Rector Substation SVC Control System Upgrade | 36.305, -119.245 | Visalia, Tulare County | Rector 220/66 (S): Upgraded SVC control system, HMI and grounding point as needed | Controls and HMI | Replacement | None | Infrastructure Replacement | Age/Condition | 05/09/2023 | 16 | Replacement due to criticality, age, spare part availability and/or known equipment issues | See Note 14A | Non HFRA | See Note 16C | Extreme Temperature Conditions, Air Particulate Levels | Demetric Brown, MPO - Programs | See Note 19B | 31.7 | See Note 21A | 220kV/66kV/12kV | See Note 23B | 902573181 | CET-ET-IR-ME-475600 | 4756 | See Note 27A | Yes | 2019 | 2020 | Annual Capital Operating Plan Process | N/A | N/A | N/A | N/A | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Engineering more than 50% completed | See Note 46A | 2023-10-30 | No | 2021-12-31 | 2025-03-01 | Schedule adjusted to provide for competitive bid process | 2238 | 2238 | See Note 53A | 18783.2729 | 3084.62 | 7698.693 | 6703.459 | 0 | 0 | 0 | 17486.772 | 0 | 132.7361 | 93.0574 | 197.0407 | 873.6666 | 1296.5008 | 344.8933 | See Note 57A | N/A | See Note 59A | 1268.6239 | None | 100% | 0% | Column 52: Source = PMWIF (Project Summary V.0)
0: N/A; Project Description 1: PB-16.14; Project Description 2: Eldorado Substation Control & Protection Upgrade; Project Description 4: Boulder City, Clark County, Nevada; Project Description 5: Eldorado 500/220 (T): Replace and upgrade current control and protection (Moenkopi Series Capacitor); Project Description 6: Relays; Project Description 7: Replacement; Project Description (Cont.) 24: 903027829; Project Description (Cont.) 25: CET-ET-IR-ME-475600; Project Description (Cont.) 26: 4756; Project Status 45: Planning; Project Status 50: 2025-05-16; Costs 52: 6756; Costs 52.1: 6756; Costs 54: 78.6858 | [16 empty] | Column 52: Source= PMWIF (C55)
N/A | PB-16.15 | Capacitor Substation (CA) Control & Protection Upgrade | 33.672, -115.559 | Desert Center, Riverside County | Capacitor Cal 500/220(T): Replace and upgrade current control and protection (Devers-Redbluff1) | Substation Current Control and Protection Upgrade/Replacement | Replacement | None | Infrastructure Enhancement | Age/Condition | 2019 | 15 | OEM no longer manufactures existing C&P. Recommended to replace to match service life of Series Capacitors from same OEM. | N/A | Non-HFRA | See Note 16C | High Seismic | Demetric Brown, MPO - Programs | See Note 19B | 3.6 | 500kV | 500kV, 220kV | See Note 23B | 902752379 | CET-ET-IR-ME-475600 | 4756 | See Note 27A | Yes | 2017 | 2018 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2021 = 4,751 2022 = 27 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2020-11-10 | No | 2020-12-31 | 2021-02-08 | Outage Restrictions | 2547 | 2547 | See Note 53A | 4777.8661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.6005 | 3653.3985 | 1048.8169 | 27.0504 | 4777.8661 | 525.1155 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | -2.1689e-12 | None | 100% | 0% | Column 2: SCE has corrected the project name to align with internal nomenclature- formerly reported as "Red Bluff Substation Control & Protection Upgrade" Column 52: Source= PMWIF (v0 Proj Summary); WO#902752379 replaced WO#902450696; therefore, the approved original cost is the same as the initial WO. SCE provided in its Feb SRP Supplement an estimate of $2.464 was the first available cost under the new WO#; however, consistent with the methodology for the July SRP, SCE provides the original estimate from the PMWIF (v0 Proj Summary).
N/A | PB-16.16 | Capacitor Substation (AZ) Control & Protection Upgrade | 33.51764, -113.74308 | Quartzsite, La Paz County, Arizona | Capacitor Az12/500 (G):Replace & UPG current control & protection (Palo Verde-Devers Series Cap EPC | Substation Current Control and Protection Upgrade/Replacement | Replacement | PB-16.25 | Infrastructure Enhancement | Age/Condition | 2019 | 15 | OEM no longer manufactures existing C&P. Recommended to replace to match service life of Series Capacitors from same OEM. | N/A | Out of State | See Note 16C | High Seismic | Demetric Brown, MPO - Programs | See Note 19B | 1.6 | 500kV | 500kV | See Note 23B | 902752277 | CET-ET-IR-ME-475600 | 4756 | See Note 27A | Yes | 2017 | 2018 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2022 = 5,316 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2021-10-04 | Yes | 2020-12-31 | 2022-05-26 | Outage Restrictions and Material Delays | 2551 | 2551 | See Note 53A | 5315.813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.0374 | 2801.0069 | 1551.5387 | 943.23 | 5315.813 | 960.2637 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | 6.1086e-12 | None | 100% | 0% | Column 2: SCE has corrected the project name to align with internal nomenclature- formerly reported as "Palo Verde Substation Control & Protection Upgrade" Column 45: Engineering is completed, but construction has not yet started (pending drawings) Column 52: Source= PMWIF (v0 Proj Summary); WO#902752277 replaced WO#902450675; therefore, the approved original cost should be the same as the initial WO.
N/A | PB-16.17 | Antelope Substation Disconnect Replacement | 34.687704;-118.299875 | Lancaster, Los Angeles County | Replace (8) sets of 66kV disconnects, (4) sets 220kV disconnects & (3) 220kV CCVT's | Disconnects | Replacement | NA | Infrastructure Replacement | Age/Condition - Replace Other Substation Equipment | 2021-09-05 | Exact age is presently unknown | Replacement due to criticality, age, spare part availability and known equipment issues | See Note 14A | Not applicable - No HFRA | See Note 16C | High Wind Events, Extreme Temperature Conditions, High Seismic | Demetric Brown, MPO - Programs | See Note 19B | 86.2 | See Note 21A | 500kV, 220kV | See Note 23B | 902757343 | CET-ET-IR-ME-475600 | 4756 | See Note 27A | Yes | 2019 | 2019 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2022 = 1,982 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2021-09-20 | Yes | 2021-12-31 | 2022-06-17 | Scope Increase, Material Delays, and Outage Restrictions | 1307 | 1307 | See Note 53A | 1981.9833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.5022 | 404.6776 | 690.2082 | 865.5954 | 1981.9833 | 348.9172 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | -6.6484e-13 | None | 100% | 0% | Column 52: Source = PMWIF (06/25/2019 Investment Summary)
N/A | PB-16.18 | Vincent Substation Disconnect Replacement | 34.486169;-118.118391 | Palmdale, Los Angeles County | Replace (6) sets of 500kV disconnects and (29) sets of 220kV disconnects. | Disconnects | Replacement | NA | Infrastructure Replacement | Age/Condition - Replace Other Substation Equipment | 2022-03-15 | Exact age is presently unknown | Replacement due to criticality, age, spare part availability and known equipment issues | See Note 14A | HFTD Tier 3 | See Note 16C | High Wind Events, Extreme Temperature Conditions, High Seismic | Demetric Brown, MPO - Programs | See Note 19B | 46 | See Note 21A | 500kV, 220kV | See Note 23B | 902820062 | CET-ET-IR-ME-475600 | 4756 | See Note 27A | Yes | 2019 | 2019 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Construction more than 50% completed | See Note 46A | 2021-10-04 | No | 2023-12-31 | 2024-05-31 | N/A | 6472 | 6472 | See Note 53A | 11780.3952 | 2394.631 | 1250 | 0 | 0 | 0 | 0 | 3644.631 | 0 | 6.5477 | 891.1045 | 2735.4435 | 4502.6686 | 8135.7643 | 1229.521 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | 7426.1436 | None | 100% | 0% | Column 52: Source = PMWIF (09/08/2019 Investment Summary)
N/A | PB-16.19 | Big Creek 3 Substation Capacitor Bank Replacement | 37.301847;-118.531901 | Shaverlake, Fresno County | Replace the No.1 220kV capacitor bank including relay upgrade to latest standard. Replace 220kV disconnect and ground switch. | Disconnects, Capacitor Bank, and Relay Protection | Replacement | NA | Infrastructure Replacement | Age/Condition - Replace Other Substation Equipment | 2022-05-12 | Exact age is presently unknown | Replacement due to criticality, age, spare part availability and known equipment issues | See Note 14A | HFTD Tier 2 | See Note 16C | High Fire Area | Demetric Brown, MPO - Programs | See Note 19B | 2.29 | See Note 21A | 220kV/12kV | See Note 23B | 902831695 | CET-ET-IR-ME-475601 | 4756 | See Note 27A | Yes | 2019 | 2019 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Construction more than 50% completed | See Note 46A | 2023-01-23 | Yes | 2021-12-31 | 2023-10-30 | Creek Fire, Resource and Outage Restrictions | 2105 | 2105 | See Note 53A | 1418.1741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.0625 | 622.6042 | 371.61 | 409.8976 | 1418.1741 | 316.1412 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | 1320.2978 | None | 100% | 0% | Column 52: Source = PMWIF (09/03/2019 Investment Summary)
N/A | PB-16.20 | Inyo Substation Disconnect Replacement | 37.342267;-118.440875 | Inyokern, Inyo County | Breakdown of project scope: Replace (1) set of 220 kV line disconnects with new group-operated disconnects - High-side No.1A Bank Position: Replace (2) sets of 220kV disconnects with new group-operated disconnects - Low-side No.1A Bank Position: Replace (2) sets of 115kV disconnects with new group-operated disconnects | Disconnects | Replacement | NA | Infrastructure Replacement | Age/Condition - Replace Other Substation Equipment | 05/05/2021 | Exact age is presently unknown | Replacement due to criticality, age, spare part availability and known equipment issues | See Note 14A | HFTD Tier 2 | See Note 16C | "High Wind Events Extreme Temperature Conditions (Snow)" | Brent Gokbudak, MPO-Project Development & Execution | See Note 19B | 1.53 | See Note 21A | 220kV/33kV | See Note 23B | 903060628 | CET-ET-IR-ME-475600 | 4756 | See Note 27A | Yes | 2020 | 2020 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2021 = 1,304 2022 = 9 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2021-05-10 | No | 2021-12-31 | 2021-11-02 | N/A | 1037 | 1037 | See Note 53A | 1313.2123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 322.6127 | 981.1361 | 9.4636 | 1313.2123 | 248.0668 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | -6.9849e-13 | None | 100% | 0% | Column 52: Source = PMWIF (04/13/2020 Investment Summary)
N/A | PB-16.21 | Vincent Substation: Update existing station light and power to allow for an ATS to be installed. | 34.486, -118.118 | Palmdale, Los Angeles County | Update existing station light and power to allow for an ATS to be installed. An additional 12kV switchboard is required to perform the work safely | Station Light & Power | Replacement/Upgrade | None | Infrastructure Replacement | Substation Reliability | 2020-06-11 | 8 | Load Flow | N/A | Tier 3 | See Note 16C | The asset’s service life can be affected by the following environmental factors; high corrosive soils, weather climates, airborne contamination, and pollution. | Demetric Brown, MPO - Programs | See Note 19B | 49.5 | See Note 21A | 13.8 kV, 12 kV, 750 kVA | See Note 23B | 902157707 | CET-ET-IR-ME-475600 | 4756 | See Note 27A | Yes | 2017 | 2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2021 = 5,481 2022 = -462 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2020-06-22 | No | 2019-12-31 | 2021-02-02 | Other - See Notes | 329 | 329 | See Note 53A | 5018.453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 250.4156 | 4417.3945 | 683.0321 | -462.3892 | 5018.453 | 588.2355 | See Note 57A | N/A | See Note 59A | -6.0449e-13 | None | 100% | 0% | Column 20: Based on measured area of boundary shown in SCE GeoView Column 52: Source= PMWIF (v0 Project Summary) Column 51: Change in in-service date due to vendor drawing and material delays, increased wiring scope and cable delivery delays which required multiple outage reschedules
N/A | PB-16.22 | Pardee 220/220 (T): Replace existing emergency generator | 34.440, -118.582 | Valencia, Los Angeles County | Pardee 220/220 (T): Replace existing emergency generator with (1) 500kW generator, install (2) 1600A ATS and (2) 400A ATS as part of Substation Infrastructure Replacement. Major Equipment: - (1) 500kW Generator - (2) 1600A Three Phase ATS - (2) 400A Single Phase ATS | Emergency Generator | Replacement | SP-36.02 | Infrastructure Replacement | Substation Reliability | 2020-03-14 | 19 | Age and condition of equipment | N/A | Zone 1 | See Note 16C | High Seismic, High Fire Area | Demetric Brown, MPO - Programs | See Note 19B | 26.2 | See Note 21A | 220kV | See Note 23B | 902262930 | CET-ET-IR-ME-475601 | 4756 | See Note 27A | Yes | 2017 | 2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2020 = 2,127 2021 = 29 2022 = 3 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2020-03-23 | No | 2019-12-31 | 2020-10-20 | Other - See Notes | 4451 | 4451 | See Note 53A | 2159.0691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.1657 | 582.4448 | 1521.1497 | 29.4403 | 2.8686 | 2159.0691 | 286.4849 | See Note 57A | N/A | See Note 59A | 7.1651e-13 | None | 100% | 0% | Column 20: Based on measured area of boundary shown in SCE GeoView Column 51: Multiple delays due resource constraints, delayed vendor drawings, and quality issues. Column 52: Source= PMWIF (v0 Project Summary)
N/A | PB-16.23 | Serrano 500/220 kV: Install New 2000A ATS and new 66A ATS Reconnect | 33.82955;-117.789488 | Orange, Orange County | Install (2) new 2000A ATS and (2) new 600A ATS. Reconnect existing emergency generator to new ATS’s as part of Substation Infrastructure Replacement. | ATS Reconnect | Upgrade | NA | Infrastructure Replacement | Age/Condition - Replace Other Substation Equipment | 2022-02-09 | NA | Replacement due to criticality, age, spare part availability and known equipment issues | See Note 14A | HFTD Tier 2 | See Note 16C | No significant environmental factors | Demetric Brown, MPO - Programs | See Note 19B | 19.2 | See Note 21A | 500kV, 220kV | See Note 23B | 902267293 | CET-ET-IR-ME-475601 | 4756 | See Note 27A | Yes | 2017 | 2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Construction more than 50% completed | See Note 46A | 2022-02-14 | No | 2019-12-31 | 2024-12-30 | Material and Vendor Drawings Delays, and Resource Restrictions | 1951 | 1951 | See Note 53A | 2773.8117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131.9342 | 384.1613 | 210.8086 | 634.8548 | 1412.0528 | 2773.8117 | 629.3132 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | 2630.5565 | None | 100% | 0% | Column 52: Source = PMWIF (12/07/2017 Investment Summary)
0: N/A; Project Description 1: PB-16.24; Project Description 2: Devers 500/220(T): Upgrade HMI, DFR and PLC; Project Description 4: North Palm Springs, Riverside County; Project Description 5: Devers 500/220(T): Upgrade HMI, DFR and PLC as required for the Devers SVC; Project Description 6: Substation HMI, DFR, and PLC upgrade; Project Description 7: Replacement; Project Description (Cont.) 24: 903237509; Project Description (Cont.) 25: CET-ET-IR-ME-475600; Project Description (Cont.) 26: 4756; Project Status 45: Planning; Project Status 50: 2026-12-09; Costs 52: 1614; Costs 52.1: 1614; Costs 54: 10441.1085 | [16 empty] | Column 52: Source= PMWIF (C55)
N/A | PB-16.25 | Series Capacitor AZ: Replace disconnects | 33.51764, -113.74308 | Quartzsite, La Paz County, Arizona | Replace motor operated disconnect motor for MOD 797 and 799 (2 MOD) | Disconnects | Replacement | NA | Infrastructure Replacement | Age/Condition - Replace Other Substation Equipment | 2021-09-19 | Exact age is presently unknown | Replacement due to criticality, age, spare part availability and known equipment issues | See Note 14A | Not applicable - Out of State | See Note 16C | Extreme Temperature Conditions | Demetric Brown, MPO - Programs | See Note 19B | 1.59 | See Note 21A | 500kV | See Note 23B | 902752276 | CET-ET-IR-ME-475600 | 4756 | See Note 27A | Yes | 2019 | 2018 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2022 = 3,903 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2021-10-04 | Yes | 2021-06-01 | 2022-05-26 | Construction and material delay | 935 | 935 | See Note 53A | 3902.6485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.9375 | 564.5786 | 1942.2613 | 1370.871 | 3902.6485 | 997.8174 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | -8.4538e-13 | None | 100% | 0%
N/A | PB-16.26 | Devers 500/220 (T): Replace existing emergency generator | 33.934947;-116.577878 | North Palm Springs, Riverside County | Replace existing 350 kW emergency generator with 1000 kVA generator equipped with 2000A, 3-pol B for three-phase, 240V | Emergency Generator | Upgrade | NA | Infrastructure Replacement | Age/Condition - Replace Other Substation Equipment | 05/03/2021 | Exact age is presently unknown | Replacement due to criticality, age, spare part availability and known equipment issues | See Note 14A | Not applicable - No HFRA | See Note 16C | Extreme Temperature Conditions, Extreme Temperature Conditions, High Wind Events | Demetric Brown, MPO - Programs | See Note 19B | 98 | See Note 21A | 500kV, 220kV, 115kV | See Note 23B | 902298942 | CET-ET-IR-ME-475600 | 4756 | See Note 27A | Yes | 2017 | 2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2021 = 2,343 2022 = 261 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2021-05-17 | No | 2019-12-31 | 2021-09-29 | Material and Vendor Drawings Delays and Outage Restrictions | 5419.832 | 4552.6589 | See Note 53A | 2603.7251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.5373 | 375.1085 | 27.3191 | 1882.0477 | 260.7125 | 2603.7251 | 393.7332 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | -3.5037e-12 | None | 100% | 0% | Column 52: Source = PMWIF (01/05/2018 Investment Summary)
0: N/A; Project Description 1: PB-16.27; Project Description 2: MIRA LOMA -REPLACE A; Project Description 4: Ontario, San Bernardino County; Project Description 5: Mira Loma 500/220kV - Replace auto transfer switchgear and main 3 phase and single phase AC panels.; Project Description 6: Substation; see "Project description; Project Description 7: Replacement; Project Description (Cont.) 24: 903287574; Project Description (Cont.) 25: CET-ET-IR-ME-475601; Project Description (Cont.) 26: 4756; Project Status 45: Pre-construction; Project Status 50: 2024-12-31; Costs 52: 1045; Costs 52.1: 888.25; Costs 54: 3665.2539 | [16 empty] | 49 and 52 Origination = Verified PMWIF PMWIF Approval Date = 12/29/2020 Latest Approved Investment Summary Version = Pulled on 10/23/2023
N/A | PB-17 | Trans Line Relay Replacements - 220 kV & above | Not applicable at program level | Not applicable at program level | Replacement of aged and obsolete electromechanical protective bulk substation (500 and 220 kW) relays with new IEDs for added functionality and improved system reliability. | Relay Protection | Replacement | Not applicable at program level | Other - See Notes | Age/Condition - Replace Relays | Multiple equipment covered under this program. Inspections vary base on type of equipment and voltage application (6 years or 12 years interval) | Not applicable at program level | Age based analysis using data on when the equipment was manufactured and number of years equipment has been in-service. Known equipment life cycle, availability of spare parts, and cost associated with maintenance, . Generally, electromechanical relays were expected to last 30years, solid state relays can be expected to last 20 years and Microprocessor based relays can be expected to last 12 to 15 years. Pushing any of the equipment past the end of life increases the likelihood of failure | Not applicable at program level | Not applicable at program level | See Note 16B | Not applicable at program level | Demetric Brown, MPO - Programs | Not applicable at program level | Not applicable at program level | 500kV, 220kV,161KV | Not applicable at program level | See Note 23B | Not applicable at program level | CET-ET-IR-RP-508900 | 5089 | See Note 27A | Not applicable at program level | Not applicable at program level | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | Not applicable at program level | Not applicable at program level | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Not applicable at program level | See Note 46A | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 53A | Not applicable at program level | 2378.985 | 2298.589 | 1892.046 | 4840.21 | 5200 | Not Available | 16609.83 | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not applicable at program level | Not applicable at program level | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | See Note 60A | None | 100% | 0% | Column 9: Asset Condition Column 12: Generally these assets being replaced are > 30 Years
N/A | PB-17.01 | Lugo-Vincent No.1 Substation Relay Replacement | 34.367, -117.369 | Hesperia, San Bernardino County | Lugo Substation: Replace Lugo -Vincent No. 1 500kV line obsolete protection scheme with advance digital communication aided IED relays. Remove wave trap and replace the CCVT, one per phase. | Relay Protection | Replacement | PB-17.02 | Other - See Notes | Age/Condition - Replace Relays | 2014 | > 30 Years | Age based analysis using data on when the equipment was manufactured and number of years equipment has been in-service verses the known equipment life cycle. Generally ,electromechanical relays were expected to last 30years, solid state relays can be expected to last 20 years and Microprocessor based relays can be expected to last 12 to 15 years. Pushing any of the equipment past the end of life increases the likelihood of failure | Emergent replacement after equipment failure | Tier 2 | See Note 16B | No significant environmental factors | Brent Gokbudak, MPO-Project Development & Execution | See Note 19B | 46 | 500kV | 500kV | See Note 23B | 900455009 | CET-ET-IR-RP-508900 | 5089 | See Note 27A | Yes | 2011 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2015 = 1,324 2016 = 64 2018 = 1 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2014-07-09 | No | 2013-12-31 | 2015-12-22 | Resource and Space Constraints | 400 | 400 | See Note 53A | 1388.1917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1388.1917 | 0 | 0 | 0 | 0 | 1388.1917 | 320.261 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | 1.1292e-12 | None | 100% | 0% | Column 9: Asset Condition Column 52: Source= v0 Project Summary
N/A | PB-17.02 | Lugo-Vincent No.2 Substation Relay Replacement | 34.367, -117.369 | Hesperia, San Bernardino County | Lugo Substation: Replace Lugo -Vincent No. 2 500kV line obsolete protection scheme with advance digital communication aided IED relays. Remove wave trap and install new CCVTs, one per phase | Relay Protection | Replacement | PB-17.01 | Other - See Notes | Age/Condition - Replace Relays | 2015 | > 30 Years | Age based analysis using data on when the equipment was manufactured and number of years equipment has been in-service verses the known equipment life cycle. Generally ,electromechanical relays were expected to last 30years, solid state relays can be expected to last 20 years and Microprocessor based relays can be expected to last 12 to 15 years. Pushing any of the equipment past the end of life increases the likelihood of failure | Emergent replacement after equipment failure | Tier 2 | See Note 16B | No significant environmental factors | Brent Gokbudak, MPO-Project Development & Execution | See Note 19B | 46 | 500kV | 500kV | See Note 23B | 900455012 | CET-ET-IR-RP-508900 | 5089 | See Note 27A | Yes | 2011 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2015 = 1,403 2016 = 25 2018 = -27 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2014-10-14 | No | 2013-12-31 | 2015-05-30 | Resource and Space Constraints | 400 | 400 | See Note 53A | 1400.7389 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 1400.7389 | 0 | 0 | 0 | 0 | 1400.7389 | 307.0511 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | -1.2273e-12 | None | 100% | 0% | Column 9: Asset Condition Column 52: Source= v0 Project Summary
N/A | PB-17.03 | Serrano Substation Relay Replacement (1) | 33.830, -117.790 | Orange, Orange County | Serrano Substation: Replace obsolete LBFB Relays (SBCs) (500kV CBs 722, 732, 812, 822, 832, and 912 ) | Relay Protection | Replacement | None | Infrastructure Replacement | Age/Condition - Replace Relays | 2018 | 29 | Aged Based Analysis | Emergent replacement after equipment failure | Tier 2 | See Note 16B | No significant environmental factors | Demetric Brown, MPO - Programs | See Note 19B | 19.2 | 500kV | 500kV | See Note 23B | 900955575 | CET-ET-IR-RP-508900 | 5089 | See Note 27A | Yes | 2013 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2015 = 2,003 2016 = 4 2017 = 8 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2014-04-21 | No | 2014-12-31 | 2015-02-01 | N/A | 720 | 720 | See Note 53A | 2015.3297 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 2015.3297 | 0 | 0 | 0 | 0 | 2015.3297 | 597.9977 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | 3.3556e-12 | None | 100% | 0% | Column 52: Source= PMWIF (v0 Proj Summary)
N/A | PB-17.04 | Alamitos Substation Relay Replacement | 33.772, -118.101 | Long Beach, Los Angeles County | Alamitos Substation: Replace (9) 220kV LBFB Relays (CHC/SAM) (220kV CBs 4052, 4072, 4102, 4122, 4142, 6052, 6072, 6122, 6142). Segregate Alamitos Substation DC System from Alamitos Generating Station. Install new battery & charger. Note, this does not include LBFB in Positions 2, 4, 6, 8, 11, and 13 Customer owned. | Relay Protection | Replacement | None | Infrastructure Replacement | Age/Condition - Replace Relays | 2018 | >30 Years | LBFB relays are critical to prevent wide area outages if a high voltage CB was to fail. Due to the critical nature of this type of relays, SCE replaces older technology electromechanical relays with microprocessor relays that offer high speed fault detection to improve system reliability and stability. Protection coordination studies may be conducted | Emergent replacement after equipment failure | Non-HFRA | See Note 16C | No significant environmental factors | Demetric Brown, MPO - Programs | See Note 19B | 22.5 | 220kV | 220kV | See Note 23B | 901103540 | CET-ET-IR-RP-508900 | 5089 | See Note 27A | Yes | 2014 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2018 = 1,380 2019 = 839 2020 = 9 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2018-08-15 | No | 2016-12-31 | 2018-10-31 | Coordination with Other Work at Alamitos | 975 | 476.4738 | See Note 53A | 3022.0953 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 2174.6649 | 838.6241 | 8.8063 | 0 | 0 | 3022.0953 | 476.752 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | -3.6853e-12 | None | 100% | 0% | Column 52: Source= v0 Project Summary
N/A | PB-17.05 | Eldorado Substation Relay Replacement (1) | 35.798, -115.008 | Boulder City, Clark County, Nevada | Eldorado Substation: Replace the Moenkopi line reactor protection; Provide automatic CB control and upgrade protection scheme for the Moenkopi 500kV line reactor | Relay Protection | Replacement | PB-16.08, PB-11.06 | Infrastructure Replacement | Age/Condition - Replace Relays | 2018 (new relays) | >20 years | Existing reactor protection lacked the capability required to perform automation functions. | Emergent replacement after equipment failure | Non-HFRA | See Note 16C | No significant environmental factors | Demetric Brown, MPO - Programs | See Note 19B | 86.7 | 500kV | 500kV | See Note 23B | 901459161 | CET-ET-IR-RP-508900 | 5089 | See Note 27A | Yes | 2016 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2018 = 2.125 2019 = 5 2020 = 95 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2017-08-28 | No | 2018-12-31 | 2018-01-19 | Construction done early to avoid outages during the later part of the year | 525 | 525 | See Note 53A | 2225.4505 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 2125.2689 | 5.0217 | 95.16 | 0 | 0 | 2225.4505 | 270.7676 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | -2.0632e-12 | None | 100% | 0% | Column 9: Result of Power Flow Analysis Column 52: Source= PMWIF (v0 Project Summary); SCE provided in its Dec 2020 SRP an original cost estimate of $240k which represents a later estimate (v2 Proj Summary). For consistency with the methodology used to populate the July SRP, SCE lists the original cost from PWIMF (v0 Proj Summary)
N/A | PB-17.06 | Eldorado Substation Relay Replacement (2) | 35.798, -115.008 | Boulder City, Clark County, Nevada | Eldorado Substation: 100% SCE - Replace (2) 220kV LBFB Relays (CBs 4092, 4102) | Relay Protection | Replacement | None | Infrastructure Replacement | Age/Condition - Replace Relays | 2017 (New equipment) | > 30 Years | LBFB relays are critical to prevent wide area outages if a high voltage CB was to fail. Due to the critical nature of this type of relays, SCE replaces older technology electromechanical relays with microprocessor relays that offer high speed fault detection to improve system reliability and stability. Protection coordination studies are conducted | This protective relay project is designed by internal standard. While we continuously evaluate new products and designs, we do not redesign projects already in motion to avoid complexities, confusion, and cost of redesign. | Non-HFRA | See Note 16C | No significant environmental factors | Brent Gokbudak, MPO-Project Development & Execution | See Note 19B | 86.7 | 500kV | 220kV | See Note 23B | 901635607 | CET-ET-IR-RP-508900 | 5089 | See Note 27A | Yes | 2014 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2017 = 1,803 2018 = 247 2019 = 123 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2017-02-06 | No | 2016-12-31 | 2017-04-25 | N/A | 282 | 282 | See Note 53A | 2173.3513 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 2050.4469 | 122.9045 | 0 | 0 | 0 | 2173.3513 | 413.4516 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | -6.285e-13 | None | 100% | 0% | Column 52: Source= PMWIF
N/A | PB-17.08 | Hinston Relay Replacement | 33.818, -118.222 | Long Beach, Los Angeles County | Upgrade Line Relay related to Hinson-Lighthipe: 2 Relay | Relay Protection | Replacement | None | Other - See Notes | Age/Condition - Replace Relays | 2014 | 15 | Age based. The Transformer had reached end of life. The transformer protection relays were as old as the transformer and had reached obsolescence. It was prudent to replace the relay during the transformer replacement outage rather than wire new transformer to the obsolete relay and have to take another extended transformer outage to replace the relay at a later date. The obsolete relays did not meet SCE current Bulk Transformer protection standards | This protective relay project is designed by internal standard. While we continuously evaluate new products and designs, we do not redesign projects already in motion to avoid complexities, confusion, and cost of redesign. | Non-HFRA | See Note 16C | Saltwater Corrosion, Flooding & Tsunami | Demetric Brown, MPO - Programs | See Note 19B | 12.2 | 220kV | 220kV/66kV, 280MVA | See Note 23B | 901886780 | CET-ET-IR-RP-508900 | 5089 | See Note 27A | Yes | 2014 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2019 = 1,577 2020 = 60 2021 = -3 2022 = -78 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2019-03-20 | No | 2017-12-31 | 2019-10-12 | Additional Scope and Coordination with Other Work | 360 | 360 | See Note 53A | 1555.9459 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 1006.4008 | 570.4138 | 60.3755 | -3.1668 | -78.0773 | 1555.9459 | 291.7939 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | -9.0178e-13 | None | 100% | 0% | Column 9: Asset Condition Column 2: SCE has corrected the project name. Formerly "Hinson Substation Transformer Bank Replacement (1)" Column 9: Asset Condition Column 52: Source= v0 Project Summary
N/A | PB-17.09 | Center Relay Replacement | 33.929, -118.105 | Norwalk, Los Angeles County | Center Substation: Replace SHPM relay related to Center-Olinda ABC PH:2 Relays | Relay Protection | Replacement | None | Infrastructure Replacement | Age/Condition - Replace Other Substation Equipment | 10/03/2022 | 36 | Age based. The Transformer had reached end of life. The transformer protection relays were as old as the transformer and had reached obsolescence. It was prudent to replace the relay during the transformer replacement outage rather than wire new transformer to the obsolete relay and have to take another extended transformer outage to replace the relay at a later date. The obsolete relays did not meet SCE current Bulk Transformer protection standards | See Note 14A | Non HFRA | See Note 16C | High Seismic | Demetric Brown, MPO - Programs | See Note 19B | 25.5 | See Note 21A | 220kV/66kV/12kV | See Note 23B | 902157775 | CET-ET-IR-RP-508900 | 5089 | See Note 27A | Yes | 2017 | 2018 | Annual Capital Operating Plan Process | N/A | N/A | N/A | N/A | See Col. 37 | 2022 = 1,564 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2022-10-10 | Yes | 2019-12-31 | 2022-12-17 | Coordination with other projects | 371 | 371 | See Note 53A | 1563.5803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1454 | 135.7256 | 171.4527 | 111.7727 | 1134.4839 | 1563.5803 | 405.8888 | See Note 57A | N/A | See Note 59A | 1.3606e-12 | None | 100% | 0% | Column 2: SCE has corrected the project name. Formerly "Center Substation Transformer Bank Replacement (1)" in Dec 2020 SRP Column 52: Source= PMWIF (v1 Proj Summary); SCE provided in its Dec 2020 SRP an original cost estimate of $673k which represents the total project cost for 2 separate WOs. For consistency with the methodology used to populate the July SRP, SCE lists the original cost from PWIMF (v1 Proj Summary)
N/A | PB-17.10 | Lugo 500/22 (T): 220 kV LBFB Replacement – Pos. 3 and 5 | 34.36786, -117.37019 | Hesperia, San Bernardino County | Lugo Substation Replace (6) LBFB relays | Relay Protection | Replacement | None | Infrastructure Replacement | Age/Condition - Replace Relays | 2020-05-10 | 41 years | LBFB relays are critical to prevent wide area outages if a high voltage CB was to fail. Due to the critical nature of this type of relays, SCE replaces older technology electromechanical relays with microprocessor relays that offer high speed fault detection to improve system reliability and stability. Protection coordination studies are conducted | This protective relay project is designed by internal standard. While we continuously evaluate new products and designs, we do not redesign projects already in motion to avoid complexities, confusion, and cost of redesign. | Tier 2 | See Note 16B | No significant environmental factors | Demetric Brown, MPO - Programs | See Note 19B | 46 | See Note 21A | 220kV | See Note 23B | 901606517 | CET-ET-IR-RP-508900 | 5089 | See Note 27A | Yes | 2015 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2020 = 1,300 2021 = 24 2022 = 2 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2020-06-01 | No | 2018-12-31 | 2020-11-16 | N/A | 108 | 108 | See Note 53A | 1325.6381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.21 | 466.9122 | 724.5864 | 24.1599 | 1.7695 | 1325.6381 | 353.9968 | See Note 57A | N/A | See Note 59A | 1.9879e-12 | None | 100% | 0% | Column 52: Source= Unverified system estimate
N/A | PB-17.11 | Big Creek No.2 Sub: Upgrade Big Creek No.1-Big Creek No.2 220 kV line relay | 37.1990, -119.3065 | Big Creek, Fresno County | Big Creek No.2 Sub: Upgrade Big Creek No.1-Big Creek No.2 220 kV line relays | Relay Protection | Replacement | PB-17.13 | Infrastructure Replacement | Age/Condition - Replace Relays | 01/06/2021 | 30 to 37 years | LBFB relays are critical to prevent wide area outages if a high voltage CB was to fail. Due to the critical nature of this type of relays, SCE replaces older technology electromechanical relays with microprocessor relays that offer high speed fault detection to improve system reliability and stability. Protection coordination studies are conducted | This protective relay project is designed by internal standard. While we continuously evaluate new products and designs, we do not redesign projects already in motion to avoid complexities, confusion, and cost of redesign. | Tier 3 | See Note 16B | High Fire Area, Moderate Seismic Area | Demetric Brown, MPO - Programs | See Note 19B | 2.07 | See Note 21A | 220kV | See Note 23B | 901583568 | CET-ET-IR-RP-508900 | 5089 | See Note 27A | Yes | 2015 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2019 = 1,181 2021 = -2 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2018-07-23 | No | 2017-12-31 | 2019-01-28 | Bundled with RTU Replacement Project | 281 | 281 | See Note 53A | 1178.6189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 805.468 | 375.637 | -0.16203 | -2.3241 | 0 | 1178.6189 | 148.0539 | See Note 57A | N/A | See Note 59A | 7.5116e-13 | None | 100% | 0% | Column 52: Source= PMWIF (v1 Project Summary)
N/A | PB-17.12 | Vista Substation: Replace 220kV LBFB Relays | 34.0408, -117.3197 | Highgrove, San Bernardino County | Vista Substation: Replace (14) 220kV LBFB Relays (220kV CBs 41X2, 4012, 4032, 4042, 4052, 4082, 4102, 61X2, 6012, 6032, 6042, 6052, 6082, 6102) | Relay Protection | Replacement | None | Infrastructure Replacement | Age/Condition - Replace Relays | Annual | 16 to 48 years | LBFB relays are critical to prevent wide area outages if a high voltage CB was to fail. Due to the critical nature of this type of relays, SCE replaces older technology electromechanical relays with microprocessor relays that offer high speed fault detection to improve system reliability and stability. Protection coordination studies are conducted | This protective relay project is designed by internal standard. While we continuously evaluate new products and designs, we do not redesign projects already in motion to avoid complexities, confusion, and cost of redesign. | Tier 2 | See Note 16B | High Seismic, High Fire Area | Demetric Brown, MPO - Programs | See Note 19B | 29.3 | See Note 21A | 220kV | See Note 23B | 901454155 | CET-ET-IR-RP-508900 | 5089 | See Note 27A | Yes | 2012 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2018 = 3,838 2019 = 2 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2017-06-07 | No | 2017-12-31 | 2018-03-03 | Outage Restrictions | 1379 | 1379 | See Note 53A | 3839.192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3837.509 | 1.583 | 0.1 | 0 | 0 | 3839.192 | 819.0302 | See Note 57A | N/A | See Note 59A | -1.6048e-12 | None | 100% | 0% | Column 52: Source= PMWIF (v1 Project Summary)
N/A | PB-17.13 | Big Creek No.1 Sub: Upgrade Big Creek No.1-Big Creek No.2 220 kV line relay | 37.2044, -119.2395 | Big Creek, Fresno County | Big Creek No.1 Sub: Upgrade Big Creek No.1-Big Creek No.2 220 kV line relays | Relay Protection | Replacement | PB-17.11 | Infrastructure Replacement | Age/Condition - Replace Relays | 01/13/2021 | 30 to 33 years | LBFB relays are critical to prevent wide area outages if a high voltage CB was to fail. Due to the critical nature of this type of relays, SCE replaces older technology electromechanical relays with microprocessor relays that offer high speed fault detection to improve system reliability and stability. Protection coordination studies are conducted | This protective relay project is designed by internal standard. While we continuously evaluate new products and designs, we do not redesign projects already in motion to avoid complexities, confusion, and cost of redesign. | Tier 3 | See Note 16B | High Fire Area, Moderate Seismic Area | Demetric Brown, MPO - Programs | See Note 19B | 1.41 | See Note 21A | 220kV | See Note 23B | 901583569 | CET-ET-IR-RP-508900 | 5089 | See Note 27A | Yes | 2015 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2019 = 1,399 2021 = -3 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2018-06-11 | No | 2017-12-31 | 2019-02-11 | Bundled with RTU Replacement Project | 379 | 379 | See Note 53A | 1396.1671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 756.248 | 642.678 | 0 | -2.7589 | 0 | 1396.1671 | 301.1341 | See Note 57A | N/A | See Note 59A | -2.7296e-12 | None | 100% | 0% | Column 52: Source= PMWIF (v1 Project Summary)
N/A | PB-17.14 | Johanna: Replace line relay | 33.713594;-117.851743 | Santa Ana, Orange County | Upgrade Line Relay related to Johanna-Santiago:(1 Relay) | Relay Protection | Replacement | NA | Infrastructure Replacement | Age/Condition - Replace Other Substation Equipment | 2018-10-07 | 15 Years | Replacement due to criticality, age, spare part availability and known equipment issues | See Note 14A | Not applicable - No HFRA | See Note 16C | No significant environmental factors | Demetric Brown, MPO - Programs | See Note 19B | 9.9 | See Note 21A | 280 MVA 220kV/66kV | See Note 23B | 901886783 | CET-ET-IR-RP-508900 | 5089 | See Note 27A | Yes | 2016 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2021 = 1,339 2022 = 6 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2018-10-08 | No | 2018-12-31 | 2021-05-27 | Coordination with Other Work, Scope Increase, and Outage Restrictions | 295 | 295 | See Note 53A | 1344.7258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 501.4962 | 53.4891 | 97.7681 | 685.8015 | 6.1709 | 1344.7258 | 293.7774 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | 1.0805e-12 | None | 100% | 0% | Column 52: Source = PMWIF (08/08/2016 Investment Summary)
N/A | PB-17.15 | Walnut-Replace 220kV line position | 34.008, -117.950 | City of Industry, Los Angeles County | Walnut 220/66 (S) Replace 220kV line position 8 (Olinda) protection relays | Substation Relay Protection | Replacement | None | Infrastructure Replacement | Age/Condition - Replace Other Substation Equipment | 07/11/2022 | 23 | Bank Capacity, Power Flow, Short Circuit Duty, Dynamic Stability, SCE Subtransmission Planning Criteria and Guidelines | See Note 14A | Non HFRA | See Note 16C | High Seismic | Demetric Brown, MPO - Programs | See Note 19B | 14.3 | See Note 21A | 220kV/66kV/12kV | See Note 23B | 903228609 | CET-ET-IR-RP-508900 | 5089 | See Note 27A | Yes | 2020 | 2022 | Annual Capital Operating Plan Process | N/A | N/A | N/A | N/A | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Construction more than 50% completed | See Note 46A | 2022-08-01 | Yes | 2022-12-31 | 2023-12-29 | Scope Increase | 1076.068 | 1076.068 | See Note 53A | 1238.8567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | 47.6874 | 1188.9693 | 1238.8567 | 171.2317 | See Note 57A | N/A | See Note 59A | 1189.7348 | None | 100% | 0% | Column 52: Source= PMWIF (12/2/2020 Investment Summary)
0: N/A; Project Description 1: PB-17.16; Project Description 2: Eldorado Substation: Replace LCB-II relays on the Eldorado-Merchant No.1 220kV Line; Project Description 4: Boulder City, Clark County, Nevada; Project Description 5: Replace LCB-II relays on the Eldorado-Merchant No.1 220KV Line (2 relays); Project Description 6: Relays; Project Description 7: Replacement; Project Description (Cont.) 24: 902994496; Project Description (Cont.) 25: CET-ET-IR-RP-508900; Project Description (Cont.) 26: 5089; Project Status 45: Operational; Project Status 50: 2022-11-10; Costs 52: 525.364; Costs 52.1: 525.364; Costs 54: 0 | [16 empty] | Column 52: Source = PMWIF (02/19/2020 Investment Summary)
N/A | PB-17.17 | Serrano Substation: Replace Line Relays on Serrano-Valley 500KV Line | 33.82955;-117.789488 | Romoland, Riverside County | Replace 500kV Serrano-Valley Line Relays and associated CCVTs | Relays | Replacement | None | Infrastructure Replacement | Age/Condition - Replace Other Substation Equipment | 2019-11-04 | 15 Years | Replacement due to criticality, age, spare part availability and known equipment issues | See Note 14A | HFTD Tier 2 | See Note 16B | No significant environmental factors | Demetric Brown, MPO - Programs | See Note 19B | 19.2 | See Note 21A | 500kV, 220kV | See Note 23B | 902897164 | CET-ET-IR-RP-508900 | 5089 | See Note 27A | Yes | 2019 | 2019 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2022 = 1,084 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2019-11-22 | Yes | 2021-12-31 | 2022-03-04 | N/A | 878.576 | 878.576 | See Note 53A | 1083.8282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51.3027 | 1016.605 | 15.9205 | 1083.8282 | 215.4341 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | 4.6566e-13 | None | 100% | 0% | Column 52: Source = PMWIF (12/02/2019 Investment Summary)
0: N/A; Project Description 1: PB-17.18; Project Description 2: Redondo 2, La Fresa–Lighthipe, La Fresa–Mesa Relay Replacement; Project Description 4: Torrance, Los Angeles County; Project Description 5: Redondo #1 Remove HCB, D60, SEL 311L New Lighthipe - Install L90, SEL-411L Redondo #2 Remove 311L, L90 - New Mesa - Install L90, SEL-411L; Project Description 6: Relays; Project Description 7: Replacement; Project Description (Cont.) 24: 903452066; Project Description (Cont.) 25: CET-ET-IR-RP-508900; Project Description (Cont.) 26: 5089; Project Status 45: On Hold; Project Status 50: 2024-12-31; Costs 52: 263.084; Costs 52.1: 263.084; Costs 54: 1070.275 | [16 empty] | Column 52: Source = PMWIF (06/03/2021 Investment Summary)
N/A | PB-17.19 | Kramer Bulk Relay Replacement | 34.989484;-117.54298 | Kramer, San Bernardino County | Upgrade Line Relay related to Kramer-LSP:(1 Relay) | Relays | Replacement | None | Infrastructure Replacement | Age/Condition - Replace Other Substation Equipment | 2018-09-07 | 15 Years | Replacement due to criticality, age, spare part availability and known equipment issues | See Note 14A | Not applicable - No HFRA | See Note 16C | Extreme Temperature Conditions | Demetric Brown, MPO - Programs | See Note 19B | 20.6 | See Note 21A | 220kV, 115kV | See Note 23B | 902129010 | CET-ET-IR-RP-508900 | 5089 | See Note 27A | Yes | 2017 | Pre-2018 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2023 = 1,497 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2018-09-10 | Yes | 2018-12-31 | 2023-05-26 | Customer Delays | 360 | 360 | See Note 53A | 1497.144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 716.4201 | 382.2159 | 134.1499 | 139.9917 | 124.3663 | 1497.144 | 595.0829 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | 1404.0024 | None | 100% | 0% | Column 52: Source = PMWIF (05/01/2017 Investment Summary)
N/A | PB-17.20 | Lighthipe: Upgrade Line Relay related to Hinson-Lighthipe | 33.879928;-118.175518 | Long Beach, Los Angeles County | Upgrade Line Relay related to Hinson-Lighthipe:(1 Relay) | Relays | Replacement | None | Infrastructure Replacement | Age/Condition - Replace Other Substation Equipment | 2019-08-16 | 13 Years | Replacement due to criticality, age, spare part availability and known equipment issues | See Note 14A | Not applicable - No HFRA | See Note 16C | Saltwater Corrosion, Flooding & Tsunami | Demetric Brown, MPO - Programs | See Note 19B | 20.2 | See Note 21A | 280 MVA 220kV/66kV | See Note 23B | 901886781 | CET-ET-IR-RP-508900 | 5089 | See Note 27A | Yes | 2015 | Pre-2018 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2019 = 1,021 2020 = 121 2021 = -4 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2019-09-05 | No | 2018-12-31 | 2019-10-14 | Delays in permitting | 295 | 295 | See Note 53A | 1138.2868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 362.095 | 658.7867 | 121.0902 | -3.6851 | 0 | 1138.2868 | 215.8731 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | 3.5476e-13 | None | 100% | 0% | Column 52: Source = PMWIF (08/08/2016 Investment Summary)
N/A | PB-17.23 | Moorpark: Replace (10) 220kV LBFB Relays (CHC/SAM) | 34.281, -118.903 | Moorpark, Ventura County | Moorpark Substation: Replace (10) 220kV LBFB Relays (CHC/SAM) (220kV CBs 4132, 5082, 5092, 5112, 5122, 5132, 6082, 6082, 6112, and 6122) | Substation Relay Replacement | Replacement | None | Infrastructure Replacement | Age/Condition - Replace Other Substation Equipment | 2017-12-06 | 15-16 | Replacement due to criticality, age, spare part availability and known equipment issues | See Note 14A | Tier 3 | See Note 16B | No Significant Environmental Factors | Demetric Brown, MPO - Programs | See Note 19B | 40 | See Note 21A | 220kV/66kV/12kV | See Note 23B | 901454153 | CET-ET-IR-RP-508900 | 5089 | See Note 27A | Yes | 2015 | Pre-2017 | Annual Capital Operating Plan Process | N/A | N/A | N/A | N/A | See Col. 37 | 2018 = 1,253 2019 = 7 2020 = -8 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2018-01-02 | No | 2017-12-31 | 2018-12-08 | Coordination with Other Work | 750 | 750 | See Note 53A | 1252.0213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1252.896 | 6.74 | -7.6119 | -0.00269 | 0 | 1252.0213 | 382.6005 | See Note 57A | N/A | See Note 59A | 1.8686e-13 | None | 100% | 0% | Column 52: Source = PMWIF (Project Summary V.0)
N/A | PB-17.25 | Santiago: Upgrade Line Relay related to Johanna-Santiago (1 relay). Replace analog ammeter | 33.665, -117.768 | Irvine, Orange County | Santiago Sub: Upgrade Line Relay related to Johanna-Santiago (1 relay) | Bulk Power 500kV Line Relay Replacement | Replacement | 901886783 | Infrastructure Replacement | Age/Condition - Replace Other Substation Equipment | 2018-09-25 | 34+ | Replacement due to criticality, age, spare part availability and known equipment issues | See Note 14A | Non HFRA | See Note 16C | No Significant Environmental Factors | Demetric Brown, MPO - Programs | See Note 19B | 18.1 | See Note 21A | 230 kV | See Note 23B | 901886782 | CET-ET-IR-RP-508900 | 5089 | See Note 27A | Yes | 2016 | 2017 | Annual Capital Operating Plan Process | N/A | N/A | N/A | N/A | See Col. 37 | 2021 = 1,065 2022 = -10 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2018-10-08 | No | 2018-12-31 | 2021-05-24 | Coordination with Other Work | 360 | 360 | See Note 53A | 1055.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 466.2822 | 22.3306 | 59.6459 | 517.0222 | -9.681 | 1055.6 | 247.4272 | See Note 57A | N/A | See Note 59A | -7.3294e-13 | None | 100% | 0% | Column 52: Source = PMWIF (Project Summary V.1)
N/A | PB-17.26 | Olinda: Rpl Center 220kV SHPM Relay to 1-SEL 311L & 1-D60 relay, CCVT & Install Pedestal & OIC Cab | 33.946, -117.921 | La Habra, Los Angeles County | Olinda 220/66 (S): Replace SHPM relay related to Center ABC PH: (1 Relay) | Bulk Power 500kV Line Relay Replacement | Replacement | 902157775 | Infrastructure Replacement | Age/Condition - Replace Other Substation Equipment | 07/12/2022 | 4 | Replacement due to criticality, age, spare part availability and known equipment issues | See Note 14A | Tier 2 | See Note 16C | No Significant Environmental Factors | Demetric Brown, MPO - Programs | See Note 19B | 11.5 | See Note 21A | 220kV, 115kV and 12kV | See Note 23B | 902157776 | CET-ET-IR-RP-508900 | 5089 | See Note 27A | Yes | 2017 | 2018 | Annual Capital Operating Plan Process | N/A | N/A | N/A | N/A | See Col. 37 | 2022 = 1,305 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2022-08-10 | Yes | 2019-12-31 | 2022-12-21 | Coordination with Other Work | 371 | 371 | See Note 53A | 1305.3883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121.8109 | 212.3425 | 36.7214 | 35.444 | 899.0695 | 1305.3883 | 262.3624 | See Note 57A | N/A | See Note 59A | 1.2069e-12 | None | 100% | 0% | Column 52: Source = PMWIF (Project Summary V.1)
N/A | PB-17.27 | Lugo Sub: Replace (6) 220kV LBFB Relays | 34.367, -117.369 | Hesperia, San Bernardino County | Lugo 500/220 (T): Replace (6) 220kV LBFB Relays (CHC/SAM) related to 220kV CB's 422, 522, 622, 462, 562, 662 (6 Relays) | Bulk Power 500kV Line Relay Replacement | Replacement | None | Infrastructure Replacement | Age/Condition - Replace Other Substation Equipment | 05/21/2023 | 4 | Replacement due to criticality, age, spare part availability and known equipment issues | See Note 14A | Tier 2 | See Note 16C | High Wind Events, Extreme Temperature Conditions, High Seismic | Brent Gokbudak, MPO-Project Development & Execution | See Note 19B | 46 | See Note 21A | 500/220 kv | See Note 23B | 902157821 | CET-ET-IR-RP-508900 | 5089 | See Note 27A | Yes | 2017 | 2018 | Annual Capital Operating Plan Process | N/A | N/A | N/A | N/A | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Construction more than 50% completed | See Note 46A | 2023-05-09 | Yes | 2020-05-11 | 2023-10-27 | Coordination with Other Work | 768 | 768 | See Note 53A | 1149.3691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2956 | 10.0384 | 168.3216 | 296.6819 | 669.0316 | 1149.3691 | 316.3309 | See Note 57A | N/A | See Note 59A | 1124.9215 | None | 100% | 0% | Column 52: Source = PMWIFed on 07/27/2017 but document could not be located
0: N/A; Project Description 1: PB-17.29; Project Description 2: Vincent 500/220kV - Vincent Midway #1/2 Line Relay Replacement; Project Description 4: Palmdale, Los Angeles County; Project Description 5: Replace relays on Midway No.1 and Midway No.2 500kV lines at Vincent Substation; Project Description 6: Bulk Power 500kV Line Relay Replacement; Project Description 7: Replacement; Project Description (Cont.) 24: 903793760; Project Description (Cont.) 25: CET-ET-IR-RP-508901; Project Description (Cont.) 26: 5089; Project Status 45: Construction less than 50% completed; Project Status 50: 2024-05-31; Costs 52: 1050; Costs 52.1: 1050; Costs 54: 1637.7326 | [16 empty] | Column 52: Source = PMWIF (06/21/2022 Investment Summary)
N/A | PB-18 | Substation Transformer Bank Replacement Program | Not applicable at program level | Not applicable at program level | This program contains projects that proactively replace AA and A bank transformers. | Not applicable at program level | Replacement | Not applicable at program level | Infrastructure Replacement | Age/Condition | Not applicable at program level | Not applicable at program level | The main analysis used to inform the health of the asset is the Health Index developed from the MDT (Maintenance Decision Tool). The health index is developed using specific data from the assets including fault interruption history, age, maintenance data etc… In addition to the health index, decisions are influenced by a Weibull analysis and subject matter input for conditions not included in the MDT, e.g. possible leaks. | Not applicable at program level | Not applicable at program level | See Note 16C | Not applicable at program level | Demetric Brown, MPO - Programs | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 23B | Not applicable at program level | CET-ET-IR-TB-521001 | 5210 | See Note 27A | Not applicable at program level | Not applicable at program level | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | Not applicable at program level | Not applicable at program level | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Not applicable at program level | See Note 46A | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 53A | Not applicable at program level | 16.235 | 7615.357 | 3247.211 | 179.452 | 2834.328 | Not Available | 13892.583 | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not applicable at program level | Not applicable at program level | See Note 57A | N/A | No project specific cost benefit performed. The Sub IR program for CB and transformers is reliability based with a Weibull curve analysis determining the appropriate number of annual replacements. The justification for the program is described in SCE general rate case submissions. | See Note 60A | None | 100% | 0%
N/A | PB-18.01 | Vincent Substation Transformer Bank Replacement (1) | 34.486, -118.118 | Palmdale, Los Angeles County | Vincent - Replace #3 AA Bank (all three phases). | Transformer | Replacement | PB-16.18, PB-11.03, PB-11.01, PB-19.01, PB-16.04 | Infrastructure Replacement | Age/Condition | A Phase - 05/28/2014, B Phase - 05/28/2014, C Phase - 05/28/2014 | A Phase - 33 Years, B Phase - 39 Years, C Phase - 39 Years | The main analysis used to inform the health of the asset is the Health Index developed from the MDT (Maintenance Decision Tool). The health index is developed using specific data from the assets including fault interruption history, age, maintenance data etc… In addition to the health index, decisions are influenced by a Weibull analysis and subject matter input for conditions not included in the MDT, e.g. possible leaks. | Replacement due to criticality, age, spare part availability and/or known equipment issues; See Note 14A | Tier 3 | See Note 16C | The asset’s service life can be affected by the following environmental factors; high corrosive soils, weather climates, airborne contamination, and pollution. | Demetric Brown, MPO - Programs | See Note 19B | 49.4 | See Note 21A | 500/220 kV, 1120 MVA | See Note 23B | 900379951 | CET-ET-IR-TB-521001 | 5210 | See Note 27A | Yes | 2010 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2014 = 20,533 2015 = -10 2017 = -1 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2012-06-28 | No | 2013-12-31 | 2014-05-31 | N/A | 250 | 250 | See Note 53A | 20522.468 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 20522.468 | 0 | 0 | 0 | 0 | 20522.468 | 3190.6603 | See Note 57A | N/A | No project specific cost benefit performed. The Sub IR program for CB and transformers is reliability based with a Weibull curve analysis determining the appropriate number of annual replacements. The justification for the program is described in SCE general rate case submissions. | -3.1829e-11 | None | 100% | 0% | Column 52: Source= PMWIF (v0 Proj Summary)
N/A | PB-18.02 | Eldorado Substation Transformer Bank Replacement (1) | 35.798, -115.008 | Boulder City, Clark County, Nevada | Eldorado Substation: Replace No. 3AA Bank 500/220kV Bank (all three phases). | Transformer | Replacement | PB-16.14, PB-16.08, PB-17.05, PB.11.06, PB-18.04 | Infrastructure Replacement | Age/Condition | A Phase - 02/10/2016, B Phase - 02/10/2016, C Phase - 02/10/2016 | A Phase - 19 Years, B Phase - 47 Years, C Phase - 47 Years | The main analysis used to inform the health of the asset is the Health Index developed from the MDT (Maintenance Decision Tool). The health index is developed using specific data from the assets including fault interruption history, age, maintenance data etc… In addition to the health index, decisions are influenced by a Weibull analysis and subject matter input for conditions not included in the MDT, e.g. possible leaks. | Replacement due to criticality, age, spare part availability and/or known equipment issues; See Note 14A | Out of State | See Note 16C | Eldorado substation can experience extreme heat and sandy conditions. | Demetric Brown, MPO - Programs | See Note 19B | 86.7 | See Note 21A | 500kV - 220kV, 498 MVA | See Note 23B | 900454965 | CET-ET-IR-TB-521001 | 5210 | See Note 27A | Yes | 2011 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2016 = 14,975 2017 = 95 2018 = 5 2019 = 7 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2015-09-01 | No | 2013-12-31 | 2016-03-22 | Coordination with Other Work at Eldorado | 17200 | 17200 | See Note 53A | 15083.0653 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 15075.8386 | 7.2267 | 1.1369e-16 | 0 | 0 | 15083.0653 | 1490.7398 | See Note 57A | N/A | No project specific cost benefit performed. The Sub IR program for CB and transformers is reliability based with a Weibull curve analysis determining the appropriate number of annual replacements. The justification for the program is described in SCE general rate case submissions. | -2.6601e-11 | None | 100% | 0% | Column 52: Source= PMWIF (v0 Proj Summary)
N/A | PB-18.03 | Kramer Substation Transformer Bank Replacement | 34.989, -117.543 | Boron, Kern County | Kramer Substation: Replace No. 1A Bank with (1) 280 MVA bank. | Transformer | Replacement | None | Infrastructure Replacement | Age/Condition | 2014-06-10 | 50 | The main analysis used to inform the health of the asset is the Health Index developed from the MDT (Maintenance Decision Tool). The health index is developed using specific data from the assets including fault interruption history, age, maintenance data etc… In addition to the health index, decisions are influenced by a Weibull analysis and subject matter input for conditions not included in the MDT, e.g. possible leaks. | Replacement due to criticality, age, spare part availability and/or known equipment issues; See Note 14A | Non-HFRA | See Note 16C | Extreme heat and sandy conditions | Brent Gokbudak, MPO-Project Development & Execution | See Note 19B | 20.6 | See Note 21A | 220kV - 115kV, 250 MVA | See Note 23B | 900454966 | CET-ET-IR-TB-521001 | 5210 | See Note 27A | Yes | 2011 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2014 = 5,923 2015 = 78 2016 = -23 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2013-10-03 | No | 2013-12-31 | 2014-05-23 | N/A | 5000 | 5000 | See Note 53A | 5978.922 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 5978.922 | 0 | 0 | 0 | 0 | 5978.922 | 856.0005 | See Note 57A | N/A | No project specific cost benefit performed. The Sub IR program for CB and transformers is reliability based with a Weibull curve analysis determining the appropriate number of annual replacements. The justification for the program is described in SCE general rate case submissions. | 4.2577e-12 | None | 71.16% | 28.84% | Column 52: Source= PMWIF (v0 Proj Summary)
N/A | PB-18.04 | Eldorado Substation Transformer Bank Replacement (2) | 35.798, -115.008 | Boulder City, Clark County, Nevada | Eldorado Substation: Replace No. 4AA Bank 500/220kV (all three phases) | Transformer | Replacement | PB-16.08, PB-17.05, PB.18.02, PB-11.06 | Infrastructure Replacement | Age/Condition | A Phase - 07/14/2016, B Phase - 07/14/2016, C Phase - 07/14/2016 | A Phase - 65 Years, B Phase - 45 Years, C Phase - 34 Years | The main analysis used to inform the health of the asset is the Health Index developed from the MDT (Maintenance Decision Tool). The health index is developed using specific data from the assets including fault interruption history, age, maintenance data etc… In addition to the health index, decisions are influenced by a Weibull analysis and subject matter input for conditions not included in the MDT, e.g. possible leaks. | Replacement due to criticality, age, spare part availability and/or known equipment issues; See Note 14A | Out of State | See Note 16C | Eldorado substation can experience extreme heat and sandy conditions. | Demetric Brown, MPO - Programs | See Note 19B | 86.7 | See Note 21A | 500kV - 220kV, 498 MVA | See Note 23B | 901103711 | CET-ET-IR-TB-521001 | 5210 | See Note 27A | Yes | 2011 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2016 = 13,900 2017 = 21 2019 = 4 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2016-03-28 | No | 2016-12-31 | 2016-07-01 | N/A | 16200 | 16200 | See Note 53A | 13925.319 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 13921.4562 | 3.8628 | -1.1369e-16 | 0 | 0 | 13925.319 | 1154.323 | See Note 57A | N/A | No project specific cost benefit performed. The Sub IR program for CB and transformers is reliability based with a Weibull curve analysis determining the appropriate number of annual replacements. The justification for the program is described in SCE general rate case submissions. | 2.1326e-11 | None | 100% | 0% | Column 52: Source= PMWIF (v2 Proj Summary)
N/A | PB-18.05 | Serrano Transformer Bank Replacement | 33.830, -117.790 | Orange, Orange County | Serrano Substation: Replace No.2AA Bank 500/220kV, all three phases | Transformer | Replacement | PB-19.04, PB-18.10 | Infrastructure Replacement | Age/Condition | A Phase - 04/26/2018, B Phase - 04/26/2018, C Phase - 04/26/2018 | A Phase - 35 Years, B Phase - 35 Years, C Phase - 35 Years | The main analysis used to inform the health of the asset is the Health Index developed from the MDT (Maintenance Decision Tool). The health index is developed using specific data from the assets including fault interruption history, age, maintenance data etc… In addition to the health index, decisions are influenced by a Weibull analysis and subject matter input for conditions not included in the MDT, e.g. possible leaks. | replacement due to criticality, age, spare part availability and/or known equipment issues; See Note 14A | Tier 2 | See Note 16C | Fairly temperate climate; subject to occasional annual storms | Demetric Brown, MPO - Programs | See Note 19B | 19.2 | See Note 21A | 500/220 kV, 1120 MVA | See Note 23B | 901355248 | CET-ET-IR-TB-521001 | 5210 | See Note 27A | Yes | 2014 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2018 = 21,375 2019 = 713 2020 = 342 2021 = 328 2022 = 100 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2017-10-30 | No | 2017-12-31 | 2018-04-06 | N/A | 15059 | 15059 | See Note 53A | 22857.912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21375.3774 | 712.937 | 342.3974 | 327.6739 | 99.5262 | 22857.912 | 3268.6813 | See Note 57A | N/A | No project specific cost benefit performed. The Sub IR program for CB and transformers is reliability based with a Weibull curve analysis determining the appropriate number of annual replacements. The justification for the program is described in SCE general rate case submissions. | 4.9324e-12 | None | 100% | 0% | Column 52: Source= v1 Project Summary
N/A | PB-18.06 | Hinson Substation Transformer Bank Replacement (2) | 33.818, -118.222 | Long Beach, Los Angeles County | Hinson Substation: Replace No. 1A Bank 220/66kV with (1) 280 MVA bank. Extend existing control room. | Transformer | Replacement | None | Infrastructure Replacement | Age/Condition | 2018-12-19 | 52 Years | The main analysis used to inform the health of the asset is the Health Index developed from the MDT (Maintenance Decision Tool). The health index is developed using specific data from the assets including fault interruption history, age, maintenance data etc… In addition to the health index, decisions are influenced by a Weibull analysis and subject matter input for conditions not included in the MDT, e.g. possible leaks. | Replacement due to criticality, age, spare part availability and/or known equipment issues; See Note 14A | Non-HFRA | See Note 16C | Hinson substation is a coastal substation and can experience corrosive conditions due to salty air. | Demetric Brown, MPO - Programs | See Note 19B | 12.2 | See Note 21A | 220kV/66kV, 280MVA | See Note 23B | 901363201 | CET-ET-IR-TB-521001 | 5210 | See Note 27A | Yes | 2014 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2018 = 1,757 2019 = 610 2020 = 294 2021 = 19 2022 = 13 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2018-06-18 | No | 2017-12-31 | 2018-12-19 | Additional Scope and Coordination with Other Work | 5150 | 1046.1787 | See Note 53A | 2693.4899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1757.087 | 610.1374 | 294.1228 | 19.4837 | 12.659 | 2693.4899 | 319.0416 | See Note 57A | N/A | No project specific cost benefit performed. The Sub IR program for CB and transformers is reliability based with a Weibull curve analysis determining the appropriate number of annual replacements. The justification for the program is described in SCE general rate case submissions. | 3.3391e-12 | None | 100% | 0% | Column 52: Source= v0 Project Summary
N/A | PB-18.07 | Center Substation Transformer Bank Replacement (2) | 33.928, -118.106 | Norwalk, Los Angeles County | Center Substation: 1. Replace No. 2A and 3A Banks 220/66 kV with (2) 280 MVA bank. 2. Replace the No. 2A ground bank and install new ground bank 66 kV Disconnects. 3. Verify and upgrade the transformer fan: CB, Panel, and Secondary Cable related to 2A, 3A, 4A Bank (3 Bank).4. Connect the alarms to in-service the existing loss of "A" bank scheme. | Transformer | Replacement | None | Infrastructure Replacement | Age/Condition | 2A Bank - 01/17/2018, 3A Bank - 06/18/2017 | 2A Bank - 51 Years, 3A Bank - 53 Years | The main analysis used to inform the health of the asset is the Health Index developed from the MDT (Maintenance Decision Tool). The health index is developed using specific data from the assets including fault interruption history, age, maintenance data etc… In addition to the health index, decisions are influenced by a Weibull analysis and subject matter input for conditions not included in the MDT, e.g. possible leaks. . | Replacement due to criticality, age, spare part availability and/or known equipment issues; See Note 14A | Non-HFRA | See Note 16C | Center is in a fairly temperate climate and is subject to occasional annual storms. | Demetric Brown, MPO - Programs | See Note 19B | 25.5 | See Note 21A | 220kV/66kV, 560MVA | See Note 23B | 901363476 | CET-ET-IR-TB-521001 | 5210 | See Note 27A | Yes | 2014 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2017 = 1,261 2018 = 35 2019 = 37 2020 = 7 2021 = -14 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2017-04-10 | No | 2017-12-31 | 2017-12-13 | N/A | 10000 | 903.0619 | See Note 53A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | See Note 57A | N/A | No project specific cost benefit performed. The Sub IR program for CB and transformers is reliability based with a Weibull curve analysis determining the appropriate number of annual replacements. The justification for the program is described in SCE general rate case submissions. | 0 | None | 100% | 0% | Column 52: Source= v0 Project Summary
N/A | PB-18.08 | Lugo Transformer Bank Replacement | 34.367, -117.369 | Hesperia, San Bernardino County | Lugo 500/220 (T) - Replace the No. 2AA Bank 500/220 kV (all three phases) | Transformer | Replacement | PB-19.02, PB-11.05 | Infrastructure Replacement | Age/Condition | A Phase - 06/26/2018, B Phase - 11/07/2018, C Phase - 07/05/2019 | A Phase - 32 Years, B Phase - 32 Years, C Phase - 32 Years | The main analysis used to inform the health of the asset is the Health Index developed from the MDT (Maintenance Decision Tool). The health index is developed using specific data from the assets including fault interruption history, age, maintenance data etc… In addition to the health index, decisions are influenced by a Weibull analysis and subject matter input for conditions not included in the MDT, e.g. possible leaks. | Replacement due to criticality, age, spare part availability and/or known equipment issues; See Note 14A | Tier 2 | See Note 16C | Extreme Rain / Flooding, Extreme Temperature Conditions | Demetric Brown, MPO - Programs | See Note 19B | 46 | See Note 21A | 500kV-220kV, 1120 MVA | See Note 23B | 901884961 | CET-ET-IR-TB-521001 | 5210 | See Note 27A | Yes | 2016 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2020 = 5,823 2021 = 204 2022 = 24 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2018-12-03 | No | 2020-12-31 | 2020-02-12 | N/A | 23575 | 23575 | See Note 53A | 6051.5999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10992.1354 | -5882.0996 | 712.8543 | 204.2928 | 24.4169 | 6051.5999 | 3008.6193 | See Note 57A | N/A | No project specific cost benefit performed. The Sub IR program for CB and transformers is reliability based with a Weibull curve analysis determining the appropriate number of annual replacements. The justification for the program is described in SCE general rate case submissions. | 6.0118e-12 | None | 100% | 0% | Column 52: Source= v0 Project Summary
N/A | PB-18.09 | Mira Loma Substation Transformer Bank Replacement | 34.010, -117.565 | Ontario, San Bernardino County | Replace No. 1AA Bank 500/220kV, all three phases | Transformer | Replacement | PB-16.07, PB-19.05 | Infrastructure Replacement | Age/Condition | 2019-03-22 | A Phase - 35 Years, B Phase - 32 Years, C Phase - 35 Years | The main analysis used to inform the health of the asset is the Health Index developed from the MDT (Maintenance Decision Tool). The health index is developed using specific data from the assets including fault interruption history, age, maintenance data etc… In addition to the health index, decisions are influenced by a Weibull analysis and subject matter input for conditions not included in the MDT, e.g. possible leaks. | Replacement due to criticality, age, spare part availability and/or known equipment issues; See Note 14A | Non-HFRA | See Note 16C | High Wind Events, Extreme Temperature Conditions | Demetric Brown, MPO - Programs | See Note 19B | 102.1 | 500 kV, 220 kV, 66 kV | 500/220 kV, 1120 MVA | See Note 23B | 901460465 | CET-ET-IR-TB-521000 | 5210 | See Note 27A | Yes | 2015 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2019 = 17,631 2020 = 14 2021 = 37 2022 = 8 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2018-10-30 | No | 2018-12-31 | 2019-04-03 | N/A | 21113 | 21113 | See Note 53A | 17690.9855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14216.192 | 3414.9912 | 14.2155 | 37.2254 | 8.3613 | 17690.9855 | 2421.0833 | See Note 57A | N/A | No project specific cost benefit performed. The Sub IR program for CB and transformers is reliability based with a Weibull curve analysis determining the appropriate number of annual replacements. The justification for the program is described in SCE general rate case submissions. | 2.6484e-12 | None | 100% | 0% | Column 52: Source= PMWIF
N/A | PB-18.10 | Serrano Substation Transformer Bank Replacement (2) | 33.830, -117.790 | Orange, Orange County | Replace 1AA Bank 500/220 kV (All three phases). Install three (3) relays. Install fire wall extension to existing 1AA, 2AA and 1AA/2AA spare transformers. Replace existing GIS grating | Transformer | Replacement | PB-19.04, PB-18.05 | Infrastructure Replacement | Age/Condition | 2019-04-17 | A Phase - 31 Years, B Phase - 32 Years, C Phase - 32 Years | The main analysis used to inform the health of the asset is the Health Index developed from the MDT (Maintenance Decision Tool). The health index is developed using specific data from the assets including fault interruption history, age, maintenance data etc… In addition to the health index, decisions are influenced by a Weibull analysis and subject matter input for conditions not included in the MDT, e.g. possible leaks. | Replacement due to criticality, age, spare part availability and/or known equipment issues; See Note 14A | Tier 2 | See Note 16C | Fairly temperate climate; subject to occasional annual storms | Demetric Brown, MPO - Programs | See Note 19B | 19.2 | 500 kV, 220 kV | 500/220 kV, 1120 MVA | See Note 23B | 901559414 | CET-ET-IR-TB-521000 | 5210 | See Note 27A | Yes | 2015 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2019 = 24,578 2020 = 64 2021 = 100 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2018-10-29 | No | 2019-12-31 | 2019-05-01 | Outage Restrictions | 23717 | 23717 | See Note 53A | 24741.7593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20049.4737 | 4529.0127 | 63.7226 | 99.5503 | 0 | 24741.7593 | 4243.9089 | See Note 57A | N/A | No project specific cost benefit performed. The Sub IR program for CB and transformers is reliability based with a Weibull curve analysis determining the appropriate number of annual replacements. The justification for the program is described in SCE general rate case submissions. | 1.5105e-11 | None | 100% | 0% | Column 52: Source= PMWIF (v1 Proj Summary)
N/A | PB-18.11 | Antelope Substation Transformer Bank Replacement | 34.688, -118.300 | Lancaster, Los Angeles County | Antelope 220/66 (S) - Replace No.1A Bank 220/66kV (three-phase unit) with (1) 280MVA three-phase unit | Transformer | Replacement | None | Infrastructure Replacement | Age/Condition | 2020-05-18 | 56 Years | The main analysis used to inform the health of the asset is the Health Index developed from the MDT (Maintenance Decision Tool). The health index is developed using specific data from the assets including fault interruption history, age, maintenance data etc… In addition to the health index, decisions are influenced by a Weibull analysis and subject matter input for conditions not included in the MDT, e.g. possible leaks. | Replacement due to criticality, age, spare part availability and/or known equipment issues; See Note 14A | Non-HFRA | See Note 16C | Substation can be impacted by temperature extremes and wind. | Demetric Brown, MPO - Programs | See Note 19B | 86.2 | See Note 21A | 220kV, 66kV, 280MVA | See Note 23B | 902157956 | CET-ET-IR-TB-521001 | 5210 | See Note 27A | Yes | 2017 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2020 = 2,132 2021 = 62 2022 = 9 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2020-06-15 | No | 2021-12-31 | 2020-09-05 | Other - See Notes | 6228 | 6228 | See Note 53A | 2203.2498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.5239 | 142.8898 | 1963.0057 | 62.2077 | 8.6227 | 2203.2498 | 450.678 | See Note 57A | N/A | No project specific cost benefit performed. The Sub IR program for CB and transformers is reliability based with a Weibull curve analysis determining the appropriate number of annual replacements. The justification for the program is described in SCE general rate case submissions. | 1.6344e-12 | None | 100% | 0% | Column 20: Based on measured area of boundary shown in SCE GeoView, measured substation fence line only. Column 51: Project advancement due to operational considerations. Project accelerated. See CM-1414 for more details. Column 57: 21% of all project cost was due to Construction Contract costs. Column 52: Source= Unverified estimate, documents not readily available
N/A | PB-18.12 | Vincent Substation Transformer Bank Replacement (2) | 34.486169;-118.118391 | Palmdale, Los Angeles County | Replace 1AA-C Single Phase Transformer | Transformers | Replacement | NA | Infrastructure Replacement | Age/Condition - Replace 230/115/70/60 kV Transformers | 2022-05-12 | 31 years | Field Maintenance Analysis | See Note 14A | HFTD Tier 3 | See Note 16C | High Wind Events, Extreme Temperature Conditions, High Seismic | Demetric Brown, MPO - Programs | See Note 19B | 46 | See Note 21A | 500kV, 220kV | See Note 23B | 902820061 | CET-ET-IR-TB-521001 | 5210 | See Note 27A | Yes | 2019 | 2019 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2023 = 4,356 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2023-01-02 | Yes | 2023-12-31 | 2023-05-26 | N/A | 35958 | 35958 | See Note 53A | 4355.5238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6748 | 401.2363 | 991.9945 | 2956.6182 | 4355.5238 | 467.2667 | See Note 57A | N/A | No project specific cost benefit performed. The Sub IR program for CB and transformers is reliability based with a Weibull curve analysis determining the appropriate number of annual replacements. The justification for the program is described in SCE general rate case submissions. | 4103.5949 | None | 100% | 0% | Column 52: Source = PMWIF (08/09/2019 Investment Summary)
N/A | PB-18.13 | Serrano Substation: Replace the 1AA/2AA Spare Transformer | 33.82822, -117.79125 | Orange County, Orange | Replace the 1AA/2AA Spare Transformer (single-phase) with one new (single-phase) unit | Transformer | Replacement | None | Infrastructure Replacement | Age/Condition | 2018-10-14 | 35 years | The main analysis used to inform the health of the asset is the Health Index developed from the MDT (Maintenance Decision Tool). The health index is developed using specific data from the assets including fault interruption history, age, maintenance data etc… In addition to the health index, decisions are influenced by a Weibull analysis and subject matter input for conditions not included in the MDT, e.g. possible leaks. | Replacement due to criticality, age, spare part availability and/or known equipment issues; See Note 14A | Tier 2 | See Note 16C | No significant environmental factors | Demetric Brown, MPO - Programs | See Note 19B | 19.2 | See Note 21A | 500kV, 220kV, 333MVA | See Note 23B | 901884594 | CET-ET-IR-TB-521001 | 5210 | See Note 27A | Yes | 2016 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2019 = 7,229 2020 = 69 2021 = 5 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2018-10-29 | No | 2019-12-31 | 2019-05-15 | Outage Restrictions | 3305 | 3305 | See Note 53A | 7302.7373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4928.854 | 2300.109 | 69.116 | 4.6583 | 0 | 7302.7373 | 941.8357 | See Note 57A | N/A | See Note 59A | 1.5522e-11 | None | 100% | 0% | Column 23: While SCE does not have a utility-wide prioritization ranking system, please see tab "Supplement-Part 1" for additional details on how work is identified and prioritized for this area. Column 52: Source= C55
0: N/A; Project Description 1: PB-18.14; Project Description 2: Chino Sub: Replace 220/66kV No. 1A, No. 2A, and No. 3A Transformer Banks; Project Description 4: Chino, San Bernardino County; Project Description 5: Chino Sub: Replace 220/66kV No. 1A, No. 2A, and No. 3A Transformer Banks; Project Description 6: A & AA Transformer Bank Replacement; Project Description 7: New and Replacement; Project Description (Cont.) 24: 903907113; Project Description (Cont.) 25: CET-ET-IR-TB-521001; Project Description (Cont.) 26: 5210; Project Status 45: Engineering more than 50% completed; Project Status 50: 2026-06-01; Costs 52: 10879; Costs 52.1: 10879; Costs 54: 10879.1805 | [16 empty] | Column 52: Source = Verified PMWIF (11/08/2022 Investment Summary)
N/A | PB-19 | Transformer Bank: On-line Dissolved Gas Analysis (DGA) - 220 kV & above | Not applicable at program level | Not applicable at program level | This activity installs online dissolved gas analysis equipment to monitor the health of transformers. | Not applicable at program level | New | Not applicable at program level | Infrastructure Enhancement | Substation Reliability | Not applicable at program level | Not applicable at program level | Installed New Equipment to allows SCE to get the most out of its fleet of transformers. With the realization of these objectives, a substantial reduction in overall transformer operating risk can be achieved. Order was based on station criticality and transformer replacement. | Not applicable at program level | Not applicable at program level | See Note 16C | Not applicable at program level | Demetric Brown, MPO - Programs | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 23B | Not applicable at program level | CET-ET-IR-ME-619700 | 6197 | See Note 27A | Not applicable at program level | Not applicable at program level | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | Not applicable at program level | Not applicable at program level | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Not applicable at program level | See Note 46A | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 53A | Not applicable at program level | 804.367 | 330 | 1685.1431 | 320.6313 | 0 | Not Available | 3140.1413 | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not applicable at program level | Not applicable at program level | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | See Note 60A | None | 100% | 0%
N/A | PB-19.01 | Vincent Substation Transformer Bank On-Line DGA | 34.486, -118.118 | Palmdale, Los Angeles County | Vincent Sub: On-Line DGA Equipment and Bushing monitoring on A Banks; 1AA, 2AA, 3AA, 4AA (12 Monitors total) | Online Dissolved Gas Analysis | New | PB-16.18, PB-11.03, PB-11.01, PB-16.04, PB-18.01 | Infrastructure Enhancement | Substation Reliability | N/A - New equipment install | N/A - New equipment install | Installed New Equipment to allows SCE to get the most out of its fleet of transformers. With the realization of these objectives, a substantial reduction in overall transformer operating risk can be achieved. Order was based on station criticality and transformer replacement. | See Note 14A | Tier 3 | See Note 16C | The asset’s service life can be affected by the following environmental factors; high corrosive soils, weather climates, airborne contamination, and pollution. | Demetric Brown, MPO - Programs | See Note 19B | 49.4 | See Note 21A | 500/220kV | See Note 23B | 800062760 | CET-ET-IR-ME-619700 | 6197 | See Note 27A | Yes | 2010 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2019 = 4,816 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2011-01-26 | No | 2012-12-31 | 2019-01-08 | Coordination with DGA Installation & Pilot, incomplete pilot testing, | 185 | 185 | See Note 53A | 4815.5427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4809.5711 | 5.9716 | 0 | 0 | 0 | 4815.5427 | 2341.1364 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | -1.2226e-12 | None | 100% | 0% | Column 52: Source= v0 Project Summary; SCE notes that the v1 Proj Summary updated the cost to $2.192M
N/A | PB-19.02 | Lugo Substation Transformer Bank On-Line DGA | 34.367, -117.370 | Hesperia, San Bernardino County | Lugo Sub: On-Line DGA Equipment and Bushing monitoring on AA Banks; 1AA & 2AA Banks (6 Monitors total) | Online Dissolved Gas Analysis | New | PB-11.05, PB-18.08 | Infrastructure Enhancement | Substation Reliability | N/A - New equipment install | N/A - New equipment install | Installed New Equipment to allows SCE to get the most out of its fleet of transformers. With the realization of these objectives, a substantial reduction in overall transformer operating risk can be achieved. Order was based on station criticality and transformer replacement. | See Note 14A | Tier 2 | See Note 16C | Extreme Rain / Flooding, Extreme Temperature Conditions | Demetric Brown, MPO - Programs | See Note 19B | 46 | See Note 21A | 500kV, 220kV | See Note 23B | 800062824 | CET-ET-IR-ME-619700 | 6197 | See Note 27A | Yes | 2010 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2020 = 2,446 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2020-03-25 | No | 2020-06-30 | 2020-06-09 | Required Redesign, Voltage Issues, DGA Pilot Testing, PSC Requirements, & Outage Coordination with Other Projects | 185 | 185 | See Note 53A | 2445.6211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2086.3914 | 211.328 | 147.9016 | 0 | 0 | 2445.6211 | 1166.3829 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | -1.0121e-12 | None | 100% | 0% | Column 52: Source= v0 Project Summary; SCE notes that the v1 Proj Summary updated the cost to $2.192M
N/A | PB-19.03 | Devers Substation Transformer Bank On Line DGA | 33.933, -116.578 | North Palm Springs, Riverside County | Devers Sub: On-Line DGA Equipment and Bushing monitoring on AA Banks; 1AA, 2AA, & 5AA (9 Monitors total) | Online Dissolved Gas Analysis | New | PB-05.01 | Infrastructure Enhancement | Substation Reliability | N/A - New equipment install | N/A - New equipment install | Installed New Equipment to allows SCE to get the most out of its fleet of transformers. With the realization of these objectives, a substantial reduction in overall transformer operating risk can be achieved. Order was based on station criticality and transformer replacement. | See Note 14A | Non-HFRA | See Note 16C | No significant environmental factors | Demetric Brown, MPO - Programs | See Note 19B | 98 | See Note 21A | 500kV, 220kV, 115kV | See Note 23B | 800062865 | CET-ET-IR-ME-619700 | 6197 | See Note 27A | Yes | 2010 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2020 = 2,897 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2014-07-31 | No | 2013-12-31 | 2020-04-22 | Resource and Space Constraints, Coordination with DGA, DGA Pilot Testing | 364 | 305.5789 | See Note 53A | 2896.5306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2577.2269 | 255.9304 | 63.0273 | 0.34594 | 0 | 2896.5306 | 1346.6861 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | -7.5837e-12 | None | 100% | 0% | Column 52: Source= PMWIF(v0 Project Summary); SCE provided in its Dec SRP an estimate of $5.2M which represents an estimate for multiple DGA projects; however, consistent with the methodology of the July SRP, SCE provides the original cost from PMWIF for the referenced WO
N/A | PB-19.04 | Serrano Substation Transformer Bank On-Line DGA | 33.828, -117.791 | Orange, Orange County | Serrano Sub: On-Line DGA Equipment and Bushing monitoring on AA Banks; 1AA, 2AA, & 3AA Banks (9 Monitors total) | Online Dissolved Gas Analysis | New | PB-18.10, PB-18.05 | Infrastructure Enhancement | Substation Reliability | N/A - New equipment install | N/A - New equipment install | Installed New Equipment to allows SCE to get the most out of its fleet of transformers. With the realization of these objectives, a substantial reduction in overall transformer operating risk can be achieved. Order was based on station criticality and transformer replacement. | See Note 14A | Tier 2 | See Note 16C | No significant environmental factors | Demetric Brown, MPO - Programs | See Note 19B | 19.2 | See Note 21A | 500kV, 220kV | See Note 23B | 800062963 | CET-ET-IR-ME-619700 | 6197 | See Note 27A | Yes | 2010 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2020 = 3,447 2021 = -3 2022 = 5 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2014-12-01 | No | 2014-12-31 | 2020-07-20 | Coordination with DGA Installation & Pilot, and Other Projects | 185 | 185 | See Note 53A | 3448.9973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2631.5977 | 569.5353 | 245.5812 | -3.1736 | 5.4568 | 3448.9973 | 1712.0317 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | 1.1179e-12 | None | 100% | 0% | Column 52: Source= v0 Project Summary
N/A | PB-19.05 | Mira Loma Substation Transformer Bank On-Line DGA | 34.006, -117.560 | Ontario, San Bernardino County | Mira Loma Substation: On-Line DGA Equipment and Bushing monitoring on AA Banks 1AA, 2AA, 3AA & 4AA Banks (12 Monitors Total) | Online Dissolved Gas Analysis | New | PB-16.07, PB-18.09 | Infrastructure Enhancement | Substation Reliability | N/A - New equipment install | N/A - New equipment install | Installed New Equipment to allows SCE to get the most out of its fleet of transformers. With the realization of these objectives, a substantial reduction in overall transformer operating risk can be achieved. Order was based on station criticality and transformer replacement. | See Note 14A | Non-HFRA | See Note 16C | No significant environmental factors | Demetric Brown, MPO - Programs | See Note 19B | 102.1 | See Note 21A | 500kV, 220kV, 66kV | See Note 23B | 800406543 | CET-ET-IR-ME-619700 | 6197 | See Note 27A | Yes | 2010 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2019 = 4,969 2020 = 5 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2015-03-02 | No | 2015-12-31 | 2019-11-13 | Coordination with DGA Pilot, and Equipment Failure | 450 | 383.058 | See Note 53A | 4973.9494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4572.0903 | 397.1028 | 4.7563 | 0 | 0 | 4973.9494 | 1722.9992 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | 1.6168e-12 | None | 100% | 0% | Column 52: Source= PMWIF; SCE provided in its Dec 2020 SRP an estimate of $265k which represents a later Project Summary (v0 09/27/2012) estimate; however, consistent with the July SRP methodology, SCE lists the cost from initial PMWIF
0: N/A; Project Description 1: PB-19.06; Project Description 2: Windhub Substation Transformer Bank On-Line DGA; Project Description 4: Mojave, Kern County; Project Description 5: Windhub Substation: On-Line DGA Equipment and Bushing monitoring on AA Bank 1AA, 2AA, 1AA&2AA Spare (7 Monitors total); Project Description 6: Online Dissolved Gas Analysis; Project Description 7: New; Project Description (Cont.) 24: 902157761; Project Description (Cont.) 25: CET-ET-IR-ME-619700; Project Description (Cont.) 26: 6197; Project Status 45: Canceled; Project Status 50: Canceled; Costs 52: 2211; Costs 52.1: 2211; Costs 54: 446.25 | [16 empty] | Column 52: Source= PMWIF (v1 Proj Summary)
N/A | PB-19.07 | Antelope Sub: On-Line DGA Equipment | 34.687, -118.300 | Lancaster, Los Angeles County | Antelope Substation: Antelope Substation: Install 2 combination DGA/Bushing units for 1AA and 2AA and 4 DGA single units for 1AA and 2AA | Online Dissolved Gas Analysis | New | None | Infrastructure Enhancement | Substation Reliability | 02/16/2022 | N/A - New equipment install | Installed New Equipment to allows SCE to get the most out of its fleet of transformers. With the realization of these objectives, a substantial reduction in overall transformer operating risk can be achieved. Order was based on station criticality and transformer replacement. | See Note 14A | Non HFRA | See Note 16C | High Wind Events, Extreme Temperature Conditions, High Seismic | Demetric Brown, MPO - Programs | See Note 19B | 86.2 | See Note 21A | 500/220kV | See Note 23B | 901583606 | CET-ET-IR-ME-619700 | 6197 | See Note 27A | Yes | 2015 | Pre-2017 | Annual Capital Operating Plan Process | N/A | N/A | N/A | N/A | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Construction more than 50% completed | See Note 46A | 2022-02-22 | Yes | 2017-12-31 | 2023-12-29 | Coordination with other projects, material delays, scope increase, and resource constraints | 1286 | 1286 | See Note 53A | 1366.7097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 419.2711 | 38.9747 | 95.2503 | 813.2136 | 1366.7097 | 282.3435 | See Note 57A | N/A | See Note 59A | 1297.7452 | None | 100% | 0% | Column 52: Source = PMWIF (Project Summary V.0); Project was re-PMWIF'd (06/2019), so SCE provided updated cost for revised PMWIF
N/A | PB-19.08 | Whirlwind Substation: On-Line DGA Equipment | 34.857, -118.436 | Rosamond, Kern County | Whirlwind Substation: On-Line DGA Equipment and Bushing monitoring on AA Banks 1AA, 3AA, 4AA (9 total units). | Online Dissolved Gas Analysis | New | None | Infrastructure Enhancement | Substation Reliability | 08/02/2022 | N/A - New equipment install | Installed New Equipment to allows SCE to get the most out of its fleet of transformers. With the realization of these objectives, a substantial reduction in overall transformer operating risk can be achieved. Order was based on station criticality and transformer replacement. | See Note 14A | Non HFRA | See Note 16C | High Wind Events, Extreme Temperature Conditions, High Seismic | Demetric Brown, MPO - Programs | See Note 19B | 92 | 500/220kV | 500/220kV | See Note 23B | 901583599 | CET-ET-IR-ME-619700 | 6197 | See Note 27A | Yes | 2021 | 2022 | Annual Capital Operating Plan Process | N/A | N/A | N/A | N/A | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Construction more than 50% completed | See Note 46A | 2022-08-15 | Yes | 2022-12-31 | 2023-12-29 | Resource and outage constraints, and engineering rework | 970 | 970 | See Note 53A | 1510.3238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 982.1679 | 528.1558 | 1510.3238 | 187.1375 | See Note 57A | N/A | See Note 59A | 1510.3238 | None | 100% | 0% | Column 52: Source= PMWIF (Investment Summary from 02/26/2021); Project was re-PMWIF'd (02/2021), so SCE provided updated cost for revised PMWIF
0: N/A; Project Description 1: PB-19.09; Project Description 2: Red Bluff Substation: On-Line DGA Equipment; Project Description 4: Desert Center, Riverside County; Project Description 5: Red Bluff Substation: On-Line DGA Equipment and Bushing monitoring on 2AA (3 Monitors total); Project Description 6: DGA; Project Description 7: New; Project Description (Cont.) 24: 903143044; Project Description (Cont.) 25: CET-ET-IR-ME-619700; Project Description (Cont.) 26: 6197; Project Status 45: Construction more than 50% completed; Project Status 50: 2023-12-29; Costs 52: 762.196; Costs 52.1: 762.196; Costs 54: 808.0996 | [16 empty] | Column 52: Source= PMWIF (7/6/2020 Investment Summary)
N/A | PB-19.11 | Eldorado Sub-Install DGA on the 4AA bank | 35.798, -115.007 | Laughlin, Clark County | Install on-line dissolved Gas Analysis units and required communication equipment on the 4AA bank (3 banks total). | Online Dissolved Gas Analysis | New | None | Infrastructure Enhancement | Substation Reliability | 2016-03-08 | N/A - New equipment install | Installed New Equipment to allows SCE to get the most out of its fleet of transformers. With the realization of these objectives, a substantial reduction in overall transformer operating risk can be achieved. Order was based on station criticality and transformer replacement. | See Note 14A | Non HFRA | See Note 16C | Extreme Temperature Conditions | Demetric Brown, MPO - Programs | See Note 19B | 86.7 | See Note 21A | 500kV - 220kV, 498 MVA | See Note 23B | 901024893 | CET-ET-IR-ME-619700 | 6197 | See Note 27A | Yes | 2010 | Pre-2017 | Annual Capital Operating Plan Process | N/A | N/A | N/A | N/A | See Col. 37 | 2020 = 1,256 2021 = 27 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2016-03-28 | No | 2020-12-31 | 2020-09-24 | N/A | 832 | 832 | See Note 53A | 1283.5166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1100.0311 | 80.6788 | 75.7552 | 27.0516 | 0 | 1283.5166 | 424.9371 | See Note 57A | N/A | See Note 59A | -9.2009e-13 | None | 100% | 0% | Column 52: Source = PMWIFed on 11/17/2010 but document could not be located
N/A | PB-19.12 | Rancho Vista Substation: On-Line DGA Equipment & Bushing monitoring on AA BK 3AA, 4AA, Spare (7 Moni | 34.518, -117.216 | Rancho Cucamonga, San Bernardino County | Rancho Vista Substation: On-Line DGA Equipment and Bushing monitoring on AA Bank 3AA, 4AA (6 Monitors total | Online Dissolved Gas Analysis | New | None | Infrastructure Enhancement | Substation Reliability | 2020-08-04 | N/A - New equipment install | Installed New Equipment to allows SCE to get the most out of its fleet of transformers. With the realization of these objectives, a substantial reduction in overall transformer operating risk can be achieved. Order was based on station criticality and transformer replacement. | See Note 14A | Non HFRA | See Note 16C | High Wind Events, High Seismic | Demetric Brown, MPO - Programs | See Note 19B | 44.5 | See Note 21A | 500kV, 220kV | See Note 23B | 901583577 | CET-ET-IR-ME-619700 | 6197 | See Note 27A | Yes | 2015 | Pre-2017 | Annual Capital Operating Plan Process | N/A | N/A | N/A | N/A | See Col. 37 | 2022 = 1,401 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2020-09-08 | Yes | 2021-12-31 | 2022-02-08 | N/A | 1809 | 1809 | See Note 53A | 1400.7667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 501.3726 | 725.4231 | 139.4338 | 34.5372 | 1400.7667 | 348.3007 | See Note 57A | N/A | See Note 59A | 1.2302e-12 | None | 100% | 0% | Column 52: Source = PMWIF (Project Summary V.1)
N/A | PB-19.13 | Windhub Substation Transformer Bank On-Line DGA | 35.035, -118.281 | Mojave, Kern County | Windhub Substation: On-Line DGA Equipment and Bushing monitors (14) for: 1. 1AA_A Phase 2. 1AA_B Phase 3. 1AA_C Phase 4. 2AA_A Phase 5. 2AA_B Phase 6. 2AA_C Phase 7. 3AA_A Phase 8. 3AA_B Phase 9. 3AA_C Phase 10. 4AA_A Phase 11. 4AA_B Phase 12. 4AA_C Phase 13. 2A 14. 3A | Online Dissolved Gas Analysis | New | None | Infrastructure Enhancement | Substation Reliability | N/A - New | N/A - New equipment install | Installed New Equipment to allows SCE to get the most out of its fleet of transformers. With the realization of these objectives, a substantial reduction in overall transformer operating risk can be achieved. Order was based on station criticality and transformer replacement. | See Note 14A | Non-HFRA | See Note 16C | Aside from typical weathering of components, seismic activity can impact retrofits, requiring re-inspection | Demetric Brown, MPO - Programs | See Note 19B | 59.2 | See Note 21A | 500/220kV | See Note 23B | 901886660 | CET-ET-IR-ME-619701 | 6197 | See Note 27A | Yes | 2021 | 2023 | Annual capital operating plan process | N/A | N/A | N/A | N/A | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Construction less than 50% completed | See Note 46A | 2023-08-07 | No | 2023-12-31 | 2024-06-28 | Design Change, Outage Constraints, Material Delays, and Coordination with other work | 1906 | 1906 | See Note 53A | 2535.2469 | 799.863 | 330 | 0 | 0 | 0 | 0 | 1129.863 | 0 | 0 | 0 | 0 | 1405.3839 | 1405.3839 | 84.8894 | See Note 57A | 0 | See Note 59A | 1405.3839 | None | 100% | 0% | SCE cancelled the work order in 2021 (unique ID 902157761) after consolidating the scope with another existing DGA project at Windhub (Work Order/Unique ID 901886660). Column 52: Source = PMWIF (Project Summary V.3)
N/A | PB-20 | Phasor Measurement System Install | Not applicable at program level | Not applicable at program level | Install Phasor Measurement unit (PMU) and Replace excising DFR to meet NERC PRC 002 requirements | PMU and DFR | New and Replacement | Not applicable at program level | Other - See Notes | Age/Condition - Replace Relays | Not applicable at program level | Not applicable at program level | NERC PRC 002 Requirements capability | Not applicable at program level | Not applicable at program level | See Note 16C | Not applicable at program level | Demetric Brown, MPO - Programs | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 23B | Not applicable at program level | CET-ET-GA-EM-644600 | 6446 | See Note 27A | Not applicable at program level | Not applicable at program level | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | Not applicable at program level | Not applicable at program level | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Not applicable at program level | See Note 46A | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 53A | Not applicable at program level | 904.7184 | 939.1319 | 54.6 | 88.7181 | 0 | Not Available | 1987.1684 | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not applicable at program level | Not applicable at program level | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | See Note 60A | None | 100% | 0% | Column 9: NERC Compliance (PRC 002)
N/A | PB-20.01 | Devers Substation PMU Install | 33.935, -116.578 | North Palm Springs, Riverside County | Devers Sub: Install Phasor Measurement unit (PMU) and Replace existing DFRs in order to meet NERC PRC 002 compliance requirements | PMU and DFR | New and Replacement | None | Infrastructure Replacement | Provide disturbance monitoring and events recording | Every 12th year | 25 | NERC PRC 002 Requirements capability | Project required to meet NERC PRC 002 Requirements. Alternative solution to replace current equipment is not a viable option due to lack of replacement parts. | Non-HFRA | See Note 16C | No significant environmental factors | Demetric Brown, MPO - Programs | See Note 19B | 98 | 500kV | 500kV, 220kV, 115kV | See Note 23B | 900379934 | CET-ET-GA-EM-644603 | 6446 | See Note 27A | Yes | 2011 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2019 = 2,610 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2016-08-01 | No | 2015-12-31 | 2019-06-28 | Resource Constraints, Outage Constraints, Coordination with PSCE & Corporate Security | 1050 | 881.4777 | See Note 53A | 2610.0106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2506.5859 | 103.2552 | 0 | 0.16956 | 0 | 2610.0106 | 807.6654 | See Note 57A | N/A | N/A - Compliance Requirement | 7.9792e-14 | None | 100% | 0% | Column 52: Source= PMWIF (v0 Project Summary)
N/A | PB-20.02 | Magunden Substation PMU Install | 35.361, -118.922 | Bakersfield, Kern County | Magunden Sub: Install Phasor Measurement unit (PMU) (Upgrade DFR to DFR/PMU Per ECS) | PMU and DFR | New and Replacement | None | Infrastructure Replacement | Provide disturbance monitoring and events recording | N/A - As Needed | 15.0795 | NERC PRC 002 Requirements capability, The existing Disturbance Monitoring Equipment was obsolete and lacked the capabilities required to record Series of Event s and Fauld Data on all thee phases and neutral for each transmission line, transmission buses and 550/220kV transformers as required by R2, R3, R4,R6,R7,R8,R9, and R11 of the requirement. Existing DFR did not meet the requirements | Project required to meet NERC PRC 002 Requirements. Alternative solution to replace current equipment is not a viable option due to lack of replacement parts. | Non-HFRA | See Note 16C | Seismic - Moderate | Demetric Brown, MPO - Programs | See Note 19B | 15.3 | 220 kV | 220 kV, 66 kV | See Note 23B | 900379936 | CET-ET-GA-EM-644605 | 6446 | See Note 27A | Yes | 2014 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2019 = 1,451 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2017-02-15 | No | 2012-12-31 | 2019-01-14 | Resource Constraints, Outage Constraints, Coordination with PSCE & Corporate Security | 1000 | 1000 | See Note 53A | 1451.2109 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 1333.4698 | 117.3909 | 0.35021 | 0 | 0 | 1451.2109 | 275.9563 | See Note 57A | N/A | N/A - Compliance Requirement | 2.0165e-12 | None | 100% | 0% | Column 52: Source= PMWIF (v0 Proj Summary)
N/A | PB-20.03 | Valley Substation PMU Install | 33.740, -117.157 | Romoland, Riverside County | Incorporate data from substations to the SCE Synchronized Phasor Measurement (SPM) System by installing necessary Phasor Measurement Units (PMUs). | PMU | New | None | Infrastructure Replacement | Replacement | Every 12th year | 7.1644 | NERC PRC 002 Requirements capability, The existing Disturbance Monitoring Equipment was obsolete and lacked the capabilities required to record Series of Event s and Fauld Data on all thee phases and neutral for each transmission line, transmission buses and 550/220kV transformers as required by R2, R3, R4,R6,R7,R8,R9, and R11 of the requirement. Existing DFR did not meet the requirements | Project required to meet NERC PRC 002 Requirements. Alternative solution to replace current equipment is not a viable option due to lack of replacement parts. | Non-HFRA | See Note 16C | High Seismic | Demetric Brown, MPO - Programs | See Note 19B | 57.4 | 500 kV, 115 kV | 500 kV, 115 kV | See Note 23B | 901597181 | CET-ET-GA-EM-644617 | 6446 | See Note 27A | Yes | 2015 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2019 = 2,267 2020 = 2 2021 = 36 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2017-06-12 | No | 2017-12-31 | 2019-04-09 | Resource Constraints, Outage Constraints, Coordination with PSCE & Corporate Security | 1000 | 1000 | See Note 53A | 2304.748 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 2137.6877 | 129.7522 | 1.5238 | 35.7844 | 0 | 2304.748 | 744.5899 | See Note 57A | N/A | N/A - Compliance Requirement | 4.34e-13 | None | 100% | 0% | Column 52: Source= PMWIF; Represents WO level cost estimate; total project cost including non-TD elements is $1.5M
N/A | PB-20.04 | Antelope Substation PMU Install | 34.688, -118.300 | Lancaster, Los Angeles County | Antelope Sub: Retrofit current 500kV and 220kV/66kV USI DFRs to APP hardware inside of existing USI DFR cabinets (may need to install additional cabinets if additional points are needed per EDSL 63-60-10). Install SEL PMU Per EDSL 63-60-20. | DFR, PMU | Upgrade, New | None | Infrastructure Replacement | Age/Condition | N/A - As Needed | 19 | NERC PRC 002 Requirements capability, The existing Disturbance Monitoring Equipment was obsolete and lacked the capabilities required to record Series of Event s and Fauld Data on all thee phases and neutral for each transmission line, transmission buses and 550/220kV transformers as required by R2, R3, R4,R6,R7,R8,R9, and R11 of the requirement. Existing DFR did not meet the requirements | Project required to meet NERC PRC 002 Requirements. Alternative solution to replace current equipment is not a viable option due to lack of replacement parts. | Non-HFRA | See Note 16C | Substation can be impacted by temperature extremes and wind. | Demetric Brown, MPO - Programs | See Note 19B | 86.2 | See Note 21A | 500/220kV | See Note 23B | 901896418 | CET-ET-GA-EM-644619 | 6446 | See Note 27A | Yes | 2013 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2022 = 2,342 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2020-09-08 | Yes | 2018-12-31 | 2022-09-06 | In-service deferred pending outcome of pilot project at Walnut Substation, completion of pilot project at Walnut Substation, to allow for bundled engineering, and to allow for resolution of newly identified NERC CIP compliance issue. | 1000 | 1000 | See Note 53A | 2341.576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.922 | 40.9154 | 1484.9152 | 793.3185 | 14.5049 | 2341.576 | 426.308 | See Note 57A | N/A | See Note 59A | -3.6945e-12 | None | 100% | 0% | Column 20: Based on measured area of boundary shown in SCE GeoView Column 51: Multiple delays with multiple causes including pilot program delays, vendor/material delays, and operational delays. Column 52: Source= PMWIF (v2 Project Summary); Represents WO level cost estimate; total project cost including non-TD elements is $1.5M
0: N/A; Project Description 1: PB-20.05; Project Description 2: Colorado River Substation PMU Install; Project Description 4: Blythe, Riverside County; Project Description 5: Colorado River Sub: Install new APP hardware in existing USI cabinet(s) for 500kV and 220kV systems per EDSL 63-60-10. Install new SEL PMU Per EDSL 63-60-20.; Project Description 6: PMU; Project Description 7: New; Project Description (Cont.) 24: 902165883; Project Description (Cont.) 25: CET-ET-GA-EM-644624; Project Description (Cont.) 26: 6446; Project Status 45: Construction more than 50% completed; Project Status 50: 2023-12-29; Costs 52: 1000; Costs 52.1: 1000; Costs 54: 817.3701 | [16 empty] | Column 52: Source= PMWIF (v1 Project Summary); Represents WO level cost estimate; total project cost including non-TD elements is $1.5M
N/A | PB-20.06 | Rector Substation PMU Install | 36.304219;-119.244023 | Visalia, Tulare County | Install Phasor measurement unit (PMU) Upgrade DFR to DFR/PMU per ECS) | PMU & DFR | Upgrade | NA | Infrastructure Replacement | Age/Condition - Replace Other Substation Equipment | 2020-10-14 | 22 | Replacement due to criticality, age, spare part availability and known equipment issues | See Note 14A | Not applicable - No HFRA | See Note 16C | Air particulate levels | Demetric Brown, MPO - Programs | See Note 19B | 31.7 | See Note 21A | 220kV/66kV/12kV | See Note 23B | 902471566 | CET-ET-GA-EM-644628 | 6446 | See Note 27A | Yes | 2019 | 2019 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2021 = 1,587 2022 = 43 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2020-11-02 | No | 2020-12-31 | 2021-06-11 | N/A | 1000 | 800 | See Note 53A | 1629.7211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.3645 | 862.367 | 622.2055 | 42.7841 | 1629.7211 | 302.0987 | See Note 57A | N/A | See Note 59A | -1.6646e-12 | None | 100% | 0% | Column 52: Source = PMWIF (V.2 Project Summary)
N/A | PB-20.07 | Rancho Vista Sub: Install phasor Measurement unit (PMU) | 34.518, -117.216 | Rancho Cucamonga, Ontario | Rancho Vista Sub: Retrofit current 500kV and 220kV USI DFRs to APP hardware inside of existing USI DFR cabinets (may need to install additional cabinets if additional points are needed per EDSL 63-60-10). Install SEL PMU Per EDSL 63-60-20 | PMU and DFR | New and Replacement | None | Infrastructure Replacement | Age/Condition | N/A - As Needed | 12 | NERC PRC 002 Requirements capability, The existing Disturbance Monitoring Equipment was obsolete and lacked the capabilities required to record Series of Event s and Fauld Data on all thee phases and neutral for each transmission line, transmission buses and 550/220kV transformers as required by R2, R3, R4,R6,R7,R8,R9, and R11 of the requirement. Existing DFR did not meet the requirements | Project required to meet NERC PRC 002 Requirements. Alternative solution to replace current equipment is not a viable option due to lack of replacement parts. | Non-HFRA | See Note 16C | High Wind Events | Demetric Brown, MPO - Programs | See Note 19B | 44.5 | See Note 21A | 500kV, 220kV | See Note 23B | 901896620 | CET-ET-GA-EM-644621 | 6446 | See Note 27A | Yes | 2016 | 2018 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2020 = 1,316 2021 = 66 2022 = 41 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2020-05-04 | No | 2018-12-31 | 2020-09-18 | Pending Outcome of Pilot Project, bundle with other projects, and vendor drawing issues | 1500 | 1500 | See Note 53A | 1422.9327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9109 | 520.4408 | 794.8187 | 66.1754 | 40.5869 | 1422.9327 | 302.7486 | See Note 57A | N/A | See Note 59A | 1.6216e-12 | None | 100% | 0% | Column 52: Source= PMWIF (v1 Project Summary)
N/A | PB-20.08 | Vestal: Install Phasor Measurement Units (PMU) | 35.8417, -119.0852 | Richgrove, Tulare County | Vestal Sub: Install new APP DFR(s) cabinet(s) for 220kV and 66kV systems per EDSL 63-60-10. | DFR | New | None | Infrastructure Replacement | Age/Condition | N/A - As Needed | 12 | NERC PRC 002 Requirements capability, The existing Disturbance Monitoring Equipment was obsolete and lacked the capabilities required to record Series of Event s and Fauld Data on all thee phases and neutral for each transmission line, transmission buses and 550/220kV transformers as required by R2, R3, R4,R6,R7,R8,R9, and R11 of the requirement. Existing DFR did not meet the requirements | Project required to meet NERC PRC 002 Requirements. Alternative solution to replace current equipment is not a viable option due to lack of replacement parts. | Non-HFRA | See Note 16C | Seismic - Moderate | Demetric Brown, MPO - Programs | See Note 19B | 10.3 | See Note 21A | 220kV, 66kV | See Note 23B | 900380021 | CET-ET-GA-EM-644610 | 6446 | See Note 27A | Yes | 2013 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2021 = 1,524 2022 = 7 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2020-08-03 | No | 2012-12-31 | 2021-04-06 | Coordination with other projects in the area, Outcome of the Walnut Sub Pilot, then Bundled with the ATS Project (Not sure what bundled with ATS project means) | 344 | 275.2 | See Note 53A | 1531.5689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153.839 | 205.565 | 701.612 | 463.2157 | 7.3372 | 1531.5689 | 288.2734 | See Note 57A | N/A | See Note 59A | 6.7966e-13 | None | 100% | 0% | Column 36 & 37: Not operational at time of data pull (late March) Column 52: Source= PMWIF (v0 Project Summary)
N/A | PB-20.09 | Mira Loma Sub: Upgrade 500kv USI DFR to APP DFR. | 34.009761;-117.564576 | Ontario, San Bernardino County | Upgrade 500kv USI DFR to APP DFR. Install new APP DFR(s) cabinet(s) for 220kV and 66kV systems per EDSL 63-60-10 | DFRs | Upgrade | NA | Infrastructure Replacement | Age/Condition - Replace Other Substation Equipment | 2021-09-21 | 20 | Replacement due to criticality, age, spare part availability and known equipment issues | See Note 14A | Not applicable - No HFRA | See Note 16C | No significant environmental factors | Demetric Brown, MPO - Programs | See Note 19B | 102.1 | See Note 21A | 500 kV/ 220 kV | See Note 23B | 900295591 | CET-ET-GA-EM-644600 | 6446 | See Note 27A | Yes | 2012 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Construction more than 50% completed | See Note 46A | 2021-10-11 | Yes | 2020-12-31 | 2023-12-29 | Coordination with Other Work, Material and Vendor Drawings Delays | 195 | 136.5 | See Note 53A | 2792.9967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 218.1263 | 45.1367 | 398.0813 | 1089.0043 | 1042.648 | 2792.9967 | 612.0335 | See Note 57A | N/A | See Note 59A | 2522.3218 | None | 100% | 0%
N/A | PB-20.10 | Eldorado Sub: Install phasor Measurement unit (PMU) | 35.798, -115.007 | Boulder City, Clark County, Nevada | Eldorado Sub: Upgrade 500kv USI DFR to APP DFR. Install new APP DFR(s) cabinet(s) for 220kV and 66kV systems per EDSL 63-60-10. Install SEL PMU Per EDSL 63-60-20 | PMU and DFR | New and Replacement | None | Infrastructure Replacement | Age/Condition - Replace Other Substation Equipment | 05/03/2022 | 500kV PMU- 16 500kV DFR- 12 220kV DFR/PMU-11 | Replacement due to criticality, age, spare part availability and known equipment issues | See Note 14A | Non HFRA | See Note 16C | High Wind Events, Extreme Temperature Conditions, Mudslide, Mountainous, Desert Region | Brent Gokbudak, MPO-Project Development & Execution | See Note 19B | 86.7 | See Note 21A | 500/220kV | See Note 23B | 901896619 | CET-ET-GA-EM-644620 | 6446 | See Note 27A | Yes | 2016 | 2017 | Annual Capital Operating Plan Process | N/A | N/A | N/A | N/A | See Col. 37 | 2023 = 3,245 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2022-05-10 | Yes | 2020-12-31 | 2023-08-03 | Resource availability, predecessor projects and outage sequencing | 1000 | 1000 | See Note 53A | 3244.9918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.9052 | 9.5621 | 18.1842 | 586.9279 | 2624.4125 | 3244.9918 | 480.7415 | See Note 57A | N/A | See Note 59A | 2030.8252 | None | 100% | 0% | Column 52: Source = PMWIF'd on 08/08/2016 but document could not be located. Original Cost and In-Service Date is from the Project Summary. Column 52: Source= PMWIF (v1 Proj Summary); WO level estimate
N/A | PB-20.11 | Windhub Sub: Install phasor Measurement unit (PMU) | 35.034918;-118.280829 | Mohave, Kern County | Install new APP hardware in existing USI cabinet(s) for 500kV, 220kV and 66kV systems per EDSL 63-60-10. Install new SEL PMU Per EDSL 63-60-20 | PMU | Upgrade | NA | Infrastructure Replacement | Age/Condition - Replace Other Substation Equipment | 2020-10-14 | 12 | Replacement due to criticality, age, spare part availability and known equipment issues | See Note 14A | Not applicable - No HFRA | See Note 16C | High Wind Events, Extreme Temperature Conditions, High Seismic | Demetric Brown, MPO - Programs | See Note 19B | 59.2 | See Note 21A | 500/220kV | See Note 23B | 902165882 | CET-ET-GA-EM-644623 | 6446 | See Note 27A | Yes | 2012 | 2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2023 = 2,477 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2020-11-09 | Yes | 2019-12-31 | 2023-05-05 | Scope Increase and Material Delays | 1000 | 1000 | See Note 53A | 2476.6159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.0771 | 861.8293 | 1169.1558 | 420.5537 | 2476.6159 | 661.858 | See Note 57A | N/A | See Note 59A | 2445.0457 | None | 100% | 0% | Column 52: Source = PMWIF (V.2 Project Summary)
N/A | PB-20.12 | Whirlwind Sub: Install phasor Measurement unit (PMU) | 34.8590690;-118.4365926 | Rosamond, Kern County | Install new APP hardware in existing USI cabinet(s) for 500kV, 220kV systems per EDSL 63-60-10. Install new SEL PMU Per EDSL 63- 60-20. | PMU | Upgrade | NA | Infrastructure Replacement | Age/Condition - Replace Other Substation Equipment | 2020-10-04 | 11 | Replacement due to criticality, age, spare part availability and known equipment issues | See Note 14A | Not applicable - No HFRA | See Note 16C | High Wind Events, Extreme Temperature Conditions, High Seismic | Demetric Brown, MPO - Programs | See Note 19B | 92 | See Note 21A | 500/220kV | See Note 23B | 902165885 | CET-ET-GA-EM-644625 | 6446 | See Note 27A | Yes | 2012 | 2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2022 = 1,678 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2020-11-09 | Yes | 2019-12-31 | 2022-09-06 | Scope Increase and Material Delays | 1000 | 1000 | See Note 53A | 1677.6722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.6262 | 787.8615 | 692.6518 | 170.5327 | 1677.6722 | 408.4001 | See Note 57A | N/A | See Note 59A | -5.3236e-13 | None | 100% | 0% | Column 52: Source = PMWIF (V.1 Project Summary)
N/A | PB-20.13 | Barre Sub: Install new APP DFR(s) | 33.809359;-117.982427 | Stanton, Orange County | Install new APP DFR(s) cabinet(s) for 220kV and 66kV systems per EDSL 63-60-10. | DFR | Upgrade | NA | Infrastructure Replacement | Age/Condition - Replace Other Substation Equipment | 2020-10-18 | 14 | Replacement due to criticality, age, spare part availability and known equipment issues | See Note 14A | Not applicable - No HFRA | See Note 16C | No significant environmental factors | Demetric Brown, MPO - Programs | See Note 19B | 13.8 | See Note 21A | 220kV/66kV/12kV | See Note 23B | 902471564 | CET-ET-GA-EM-644626 | 6446 | See Note 27A | Yes | 2012 | 2019 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2021 = 1,072 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2020-10-19 | No | 2020-12-31 | 2021-03-22 | N/A | 1350 | 675 | See Note 53A | 1072.3205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.1969 | 709.8057 | 349.3179 | 0 | 1072.3205 | 194.3018 | See Note 57A | N/A | See Note 59A | 3.1241e-13 | None | 100% | 0% | Column 52: Source = PMWIF (V.3 Project Summary)
0: N/A; Project Description 1: PB-20.14; Project Description 2: Control Sub: Install phasor Measurement unit (PMU); Project Description 4: Bishop, Inyo County; Project Description 5: Control Sub: Install Phasor Measurement unit (PMU) (Upgrade DFR to DFR/PMU Per ECS) Vendor selection: APP for DFR and SEL for PMU; Project Description 6: PMU and DFR; Project Description 7: New and Replacement; Project Description (Cont.) 24: 902471565; Project Description (Cont.) 25: CET-ET-GA-EM-644627; Project Description (Cont.) 26: 6446; Project Status 45: Pre-construction; Project Status 50: 2024-02-05; Costs 52: 1000; Costs 52.1: 1000; Costs 54: 683.5046 | [16 empty] | Column 52: Source= PMWIF (v2 Proj Summary); WO level estimate
N/A | PB-20.15 | Big Creek 3 Sub: Install phasor Measurement unit (PMU) | 37.148, -119.387 | Shaver Lake, Auberry | Big Creek 3 Sub: Install Phasor Measurement unit (PMU) (Upgrade DFR to DFR/PMU Per ECS) | PMU and DFR | New and Replacement | None | Infrastructure Replacement | Age/Condition - Replace Other Substation Equipment | 08/18/2022 | 15 | Replacement due to criticality, age, spare part availability and known equipment issues | See Note 14A | Tier 3 | See Note 16C | High Fire Area | Demetric Brown, MPO - Programs | See Note 19B | 2.29 | See Note 21A | 220kV/12kV | See Note 23B | 903111160 | CET-ET-GA-EM-644602 | 6446 | See Note 27A | Yes | 2020 | 2021 | Annual Capital Operating Plan Process | N/A | N/A | N/A | N/A | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Construction more than 50% completed | See Note 46A | 2022-09-06 | Yes | 2022-12-31 | 2023-10-31 | Resource availability and weather delays | 1109 | 1109 | See Note 53A | 1871.0716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.2792 | 342.5231 | 1509.2693 | 1871.0716 | 307.436 | See Note 57A | N/A | See Note 59A | 1783.4191 | None | 100% | 0% | Column 52: Source= PMWIF (v7 Proj Summary); WO level estimate
N/A | PB-20.16 | Red Bluff Sub: Install Phasor Measurement Unit (PMU) | 33.672, -115.559 | Desert Center, Riverside County | Install phasor measurement unit (PMU) Upgrade DFR to DFR/PMU per ECS) | PMU | Upgrade | None | Infrastructure Replacement | Age/Condition - Replace Other Substation Equipment | 2020-05-05 | 11 | Replacement due to criticality, age, spare part availability and known equipment issues | See Note 14A | Non HFRA | See Note 16C | High Wind Events, Extreme Temperature Conditions | Demetric Brown, MPO - Programs | See Note 19B | 75.7 | See Note 21A | 500kV - 220kV, 1120 MVA | See Note 23B | 902471567 | CET-ET-GA-EM-644606 | 6446 | See Note 27A | Yes | 2018 | 2020 | Annual Capital Operating Plan Process | N/A | N/A | N/A | N/A | See Col. 37 | 2022 = 1,006 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2020-05-26 | Yes | 2020-12-31 | 2022-11-29 | Additional time needed for verification of Project Requirements, delay in equipment certification | 1000 | 1000 | See Note 53A | 1005.9582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.8108 | 133.3255 | 574.0677 | 228.1865 | 59.5677 | 1005.9582 | 248.12 | See Note 57A | N/A | See Note 59A | -2.4738e-13 | None | 100% | 0% | Column 52: Source = PMWIF (Project Summary V.2)
0: N/A; Project Description 1: PB-20.17; Project Description 2: Gould 220/66 (S) - Install Phasor Measurement Unit (DFR); Project Description 4: La Canada, Los Angeles County; Project Description 5: Install phasor Measurement unit (DFR) (Upgrade DFR to DFR/PMU Per ECS); Project Description 6: PMU; Project Description 7: Upgrade; Project Description (Cont.) 24: 903476533; Project Description (Cont.) 25: CET-ET-GA-EM-644608; Project Description (Cont.) 26: 6446; Project Status 45: Operational; Project Status 50: 2023-05-10; Costs 52: 1000; Costs 52.1: 800; Costs 54: 1479.8183 | [16 empty] | Column 52: Source = PMWIF (V.2 Project Summary)
N/A | PB-20.18 | Center: Install Phasor Measurement Units (PMU) | 33.929, -118.105 | Norwalk, Los Angeles County | Center Substation: Install Phasor Measurement Unit (PMU) (Upgrade DFR to DFR/PMU per ECS) | EMS (DFR/PMU) | New and Upgrades | None | Infrastructure Enhancement | Age/Condition - Replace Other Substation Equipment | 04/14/2023 | DFR- 21 PMU- new | Replacement due to criticality, age, spare part availability and known equipment issues | See Note 14A | Non HFRA | See Note 16C | High Seismic | Demetric Brown, MPO - Programs | N/A | N/A | N/A | N/A | See Note 23B | 901219327 | CET-ET-GA-EM-644602 | 6446 | See Note 27A | Yes | 2014 | Pre-2017 | Annual Capital Operating Plan Process | N/A | N/A | N/A | N/A | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Construction more than 50% completed | See Note 46A | 2022-06-15 | Yes | 2015-12-31 | 2023-12-29 | Coordination with other projects and MEER Options | 1350 | 675 | See Note 53A | 1174.1235 | 72.056 | 59 | 0 | 0 | 0 | 0 | 131.056 | 451.3961 | 6.2632 | 13.7259 | 32.5603 | 539.1219 | 1043.0675 | 246.8247 | See Note 57A | N/A | See Note 59A | 961.3664 | None | 100% | 0% | Column 52: Source = PMWIF (Project Summary V.2)
0: N/A; Project Description 1: PB-20.19; Project Description 2: Big Creek 1 Sub: Install phasor Measurement unit (PMU) (Upgrade DFR to DFR/PMU Per ECS); Project Description 4: Big Creek, Fresno County; Project Description 5: Big Creek 1 Sub: Install phasor Measurement unit (PMU) (Upgrade DFR to DFR/PMU Per ECS); Project Description 6: EMS (DFR/PMU); Project Description 7: New and Upgrades; Project Description (Cont.) 24: 52452; Project Description (Cont.) 25: CET-ET-GA-EM-644606; Project Description (Cont.) 26: 6446; Project Status 45: Canceled; Project Status 50: Canceled; Costs 52: 1000; Costs 52.1: 1000; Costs 54: 0 | [16 empty] | Column 52: Source = Project has not yet been PMWIFed. Cost and In-Service Date is from Project Summary V.1
N/A | PB-20.20 | Mohave Sub: Install phasor Measurement unit (PMU) | 34.121, -117.640 | Clark County, Nevada | Mohave Sub: Install phasor Measurement unit (PMU) (Upgrade DFR to DFR/PMU Per ECS) | EMS (DFR/PMU) | New and Upgrades | None | Infrastructure Enhancement | Age/Condition - Replace Other Substation Equipment | 08/11/2022 | 14 | Replacement due to criticality, age, spare part availability and known equipment issues | See Note 14A | Non HFRA | See Note 16C | High Wind Events, Extreme Temperature Conditions | Brent Gokbudak, MPO-Project Development & Execution | See Note 19B | 11.5 | See Note 21A | 500kV | See Note 23B | 900379937 | CET-ET-GA-EM-644606 | 6446 | See Note 27A | Yes | 2011 | Pre-2017 | Annual capital operating plan process | N/A | N/A | N/A | N/A | See Col. 37 | 2022 = 1,086 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2022-08-15 | Yes | 2022-12-31 | 2022-11-08 | N/A | 361 | 361 | See Note 53A | 1086.1608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.2775 | 15.2722 | 13.4117 | 162.3672 | 877.8322 | 1086.1608 | 173.6146 | See Note 57A | N/A | See Note 59A | 556.0648 | None | 100% | 0% | Column 52: Source = Project has not yet been PMWIFed. Cost and In-Service Date is from Project Summary V.17
0: N/A; Project Description 1: PB-20.21; Project Description 2: Camino Sub: Install necessary phasor measurement units at Camino.; Project Description 4: Needles, San Bernardino County; Project Description 5: Camino Sub: Install necessary phasor measurement units at Camino.; Project Description 6: EMS (DFR/PMU); Project Description 7: New; Project Description (Cont.) 24: 52470; Project Description (Cont.) 25: CET-ET-GA-EM-644608; Project Description (Cont.) 26: 6446; Project Status 45: Canceled; Project Status 50: Canceled; Costs 52: 1250; Costs 52.1: 1000; Costs 54: 0 | [16 empty] | Column 52: Source = Project has not yet been PMWIFed. Cost and In-Service Date is from Project Summary V.0
N/A | PB-21 | Critical Infrastructure Protection (NERC CIP v5) | Not applicable at program level | Not applicable at program level | Implement physical access controls to meet NERC CIP-006 V5 compliance requirements | Physical Security measures | New | Not applicable at program level | Security | NERC CIP Compliance | Not applicable at program level | Not applicable at program level | N/A - Work related to meeting NERC CIP-006 V5 compliance requirements | Not applicable at program level | Not applicable at program level | See Note 16C | Not applicable at program level | Randy White, Corporate Security | Not applicable at program level | Not applicable at program level | Not applicable at program level | 500/220kV | See Note 23B | Not applicable at program level | COS-00-CS-CS-705100 | 7051 | See Note 27A | Not applicable at program level | Not applicable at program level | Pre-2017 | FRM/CRT | No | N/A | N/A | N/A | Not applicable at program level | Not applicable at program level | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Not applicable at program level | See Note 46A | 2015-02-11 | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 53A | Not applicable at program level | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 0 | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not applicable at program level | Not applicable at program level | See Note 57A | N/A | No specific cost benefit analysis performed – Activity is addressing NERC CIP-006 V5 compliance requirements | See Note 60A | None | 0% | 100% | Column 9: To comply with North American Electric Reliability Corporation (NERC) Critical Infrastructure Program (CIP) Version 5 Standard for Physical Security of Bulk Electric System (BES) Cyber Systems (CIP 006), R1.1-R1.10 (https://www.nerc.com/pa/Stand/Reliability%20Standards/CIP-006-6.pdf). • FERC Order 791 effective February 3, 2014 with required implementation date of April 1, 2016 for High and Medium Impact BES facilities
N/A | PB-21.01 | NERC CIP v5 Substation Physical Access Control Install (ES-2556) |  |  | Implement physical access controls to meet NERC CIP-006 V5 compliance requirements. • Provide engineered documentation regarding security system, confidential to Corporate Security Physical Security Systems team • Demo and replace existing station doors, locks, and peripherals with Corporate Security standard equipment • Deploy serialized lock cylinders with emergency override system • Seal, block, or augment with material and methods that do not adversely affect the operation of the station, openings in the physical security perimeters that are greater than 96 square inches • Furnish and install racking system(s) • Furnish and install wall mounted cabinet(s) • Furnish and install security system components • Furnish and install auxiliary sub-system components • Integrate system and sub-system security components • Establish physical security perimeter(s) • Provide other emergent work necessary for full system integration or construction, as required | Physical security measures | New | None | Security | NERC CIP Compliance | N/A - New. The last corporate security inspection was performed in 2019. | N/A - Largely includes installation of new equipment/technology | NERC CIP-002 defined three (3) Impact Ratings of Bulk Electric Systems based on “risk to the reliable operation of the BES”. Devices that provide electronic or physical security inherit the impact rating of the cyber system they protect. Impact Ratings: High, Medium and Low • High Impact (NERC CIP V5 Project) – Control centers used to perform load balancing, electric system reliability coordination, and transmission or generation operation (aka operation of the Energy Management System (EMS) and Generation Management System (GMS), respectively) • Examples: Switching Centers, Data Centers • Medium Impact (NERC CIP V5 Project) – Facilities that fall under the threshold for defined maximum reactive power rating or transmission facilities within the “bright-line” criteria • Medium with External Routable Connections (ERC) • Medium without External Routable Connectivity • Examples: 500kV, 220kV MEERs and Control Rooms • Low Impact (NERC CIP V6 Project) – Peaker plants, other non-medium substations • Examples: 66kV MEERs and Control Rooms, Low with External Routable Connectivity, Generation and Peaker plants | Option A - Utilize Guards 24/7 to Monitor Security Perimeters > Annual O&M for guards- $60.2M > One Time Capital $4M > Recurring Annual O&M $0.9M Option B - Mixed Model – New keys and padlocks at NERC sites > Annual O&M for guards - $10.5M > One Time Capital $11M Recurring Annual O&M $1.5M Option C- Utilize Centralized Monitoring Model & Security Technology at Perimeters (Recommended) > Annual O&M for guards - $1.5M > One-time Capital$76.BM > RecurringAnnualO&M$3.1M | Tier 2 | See Note 16C | Minimal besides catastrophic environmental events that would impact physical security measures | Randy White, Corporate Security | See Note 19B | 2.5 | See Note 21A | 500/220kV | See Note 23B | 801219508 | COS-00-CS-CS-705100 | 7051 | See Note 27A | Yes | 2014 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2015 = 2,406 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | Not Available | No | 2015-07-31 | 2015-05-28 | N/A | 2398 | 2060.8607 | See Note 53A | 2406.1069 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 2405.7433 | 0.38715 | -0.18138 | 0.15774 | 0 | 2406.1069 | 270.465 | See Note 57A | N/A | No specific cost benefit analysis performed – Activity is addressing NERC CIP-006 V5 compliance requirements | 1.4164e-12 | None | 0% | 100% | Column 9: To comply with North American Electric Reliability Corporation (NERC) Critical Infrastructure Program (CIP) Version 5 Standard for Physical Security of Bulk Electric System (BES) Cyber Systems (CIP 006), R1.1-R1.10 (https://www.nerc.com/pa/Stand/Reliability%20Standards/CIP-006-6.pdf). • FERC Order 791 effective February 3, 2014 with required implementation date of April 1, 2016 for High and Medium Impact BES facilities Column 52: Source= Unverified estimate; documents not readily available
N/A | PB-22 | TLRR Program - 220 kV & above | Not applicable at program level | Not applicable at program level | The Transmission Line Rating & Remediation (TLRR) program identifies and mitigates potential electrical clearance issues in accordance with CPUC's General Order (GO) 95 | Transmission Line | Replacement | Not applicable at program level | Other - See Notes | NERC CIP Compliance | Not applicable at program level | Not applicable at program level | IEEE-738 is the standard for calculating the current-temperature relationship of bare overhead conductors. This analysis along with SCE's standard rating methodology was used in conjunction with the PLS-CADD model that was created from the LiDAR study to identify any potential clearance issues on the circuits. | Not applicable at program level | Not applicable at program level | See Note 16B | Not applicable at program level | Demetric Brown, MPO - Programs | Not applicable at program level | Not applicable at program level | Various | 500/220kV | See Note 23B | Not applicable at program level | CET-PD-OT-PJ-TR; CET-PD-OT-PJ-729801 | 7298 | See Note 27A | FRM | Not applicable at program level | Pre-2017 | FRM/CRT | No | N/A | N/A | N/A | Not applicable at program level | Not applicable at program level | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Not applicable at program level | See Note 46A | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 53A | Not applicable at program level | 48486.697 | 60183.946 | 58912.251 | 27394.028 | 0 | 0 | 194976.922 | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not applicable at program level | Not applicable at program level | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | See Note 60A | None | 100% | 0% | Column 9: Mitigates potential electrical clearance issues in compliance with CPUC's GO 95; In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions. Column 31: Program received approvals via T&D BOT (September 2015), as well as by FRM (4/1/2021) Column 55: SCE emphasizes that costs reflected in the TLRR Program Blanket header (PB-22) are not in addition to the supporting project specific costs below. Costs shown here are the program total which includes the supporting items below, as well as other work order costs for the program.
N/A | PB-22.01 | Antelope-Magunden No.2 TLRR Remediation (1) | 34.688, -118.300 / 35.361, -118.922 | Kern County, Los Angeles County, Lancaster | Antelope-Magunden No.2 - 23 discrepancies (H) - raise 14 structures | Transmission Line (modification) | Modification/Upgrade | PB-22.07 | Other - See Notes | NERC Compliance - GO 95 | Inspections do not drive the need for TLRR projects. However, SCE performs annual patrols and triennial detailed inspections of its transmission circuits, which inspect the structures and lines on those circuits. The date of last inspection for this circuit was 10/31/2019 | 80-90 years | IEEE-738 is the standard for calculating the current-temperature relationship of bare overhead conductors. This analysis along with SCE's standard rating methodology was used in conjunction with the PLS-CADD model that was created from the LiDAR study to identify any potential clearance issues on the circuits. | Transmission line clearance discrepancies are remediated based on a series of criteria, including line sag when operating at or above 130 degrees Fahrenheit; potential risk to public safety; and system reliability risk based on the location of span, terrain, encroachment type, and extent of deviation from standards. Discrepancies may be remediated by a variety of construction activities, including, but not limited to Structure Replacements, Structure Raises, New Structure Insets, Line Reconductor, Line Re-tension, Hardware Replacements, Grading, Removing Encroachments, Undergrounding Line Segments, Rerouting Lines. | Tier 2 | See Note 16B | The asset’s service life can be affected by the following environmental factors; high corrosive soils, weather climates, airborne contamination, and pollution. | Demetric Brown, MPO - Programs | 24 | See Note 20B | 220kV | See Note 22A | See Note 23B | 901663242 | CET-PD-OT-PJ-TR | 7298 | See Note 27A | Yes | 2016 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2018 = 5,048 2019 = 12 2020 = 53 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2017-05-25 | No | 2018-12-31 | 2018-04-17 | Driven by budget Plan & OD Changes | 9212 | 9212 | See Note 53A | 5113.7606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5048.3036 | 12.0112 | 53.4458 | 0 | 0 | 5113.7606 | 463.439 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | -8.1989e-12 | None | 100% | 0% | Column 9: In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions. Column 52: Source= PMWIF (v1 Project Summary)
N/A | PB-22.02 | Pardee-Vincent TLRR Remediation | 34.440, -118.582 / 34.486, -118.118 | Los Angeles County, Santa Clarita | Pardee-Vincent No.2 - 21 discrepancies - 27 mile reconductor - reframe 2 structures - raise 1 structure | Transmission Line (reconductor and modification) | Reconductor | None | Other - See Notes | NERC Compliance - GO 95 | Inspections do not drive the need for TLRR projects. However, SCE performs annual patrols and triennial detailed inspections of its transmission circuits, which inspect the structures and lines on those circuits. The date of last inspection for this circuit was 4/30/2019 | 40-50 years | IEEE-738 is the standard for calculating the current-temperature relationship of bare overhead conductors. This analysis along with SCE's standard rating methodology was used in conjunction with the PLS-CADD model that was created from the LiDAR study to identify any potential clearance issues on the circuits. | Transmission line clearance discrepancies are remediated based on a series of criteria, including line sag when operating at or above 130 degrees Fahrenheit; potential risk to public safety; and system reliability risk based on the location of span, terrain, encroachment type, and extent of deviation from standards. Discrepancies may be remediated by a variety of construction activities, including, but not limited to Structure Replacements, Structure Raises, New Structure Insets, Line Reconductor, Line Re-tension, Hardware Replacements, Grading, Removing Encroachments, Undergrounding Line Segments, Rerouting Lines. | Tier 3 | See Note 16B | The asset’s service life can be affected by the following environmental factors; high corrosive soils, weather climates, airborne contamination, and pollution. | Demetric Brown, MPO - Programs | 27 | See Note 20B | 220kV | See Note 22A | See Note 23B | TD839139 | CET-PD-OT-PJ-TR | 7298 | See Note 27A | Yes | 2018 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2015 = 13,354 2016 = 794 2017 = 71 2018 = -58 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | Not Available | No | 2016-12-31 | 2015-11-03 | Driven by budget Plan & OD Changes | 12867 | 12867 | See Note 53A | 14162.3076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14162.3076 | 0 | 0 | 0 | 0 | 14162.3076 | 1295.2644 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | 9.3132e-12 | None | 100% | 0% | Column 9: In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions. Column 52: Source= PMWIF (v2 Proj Summary) as PMWIF'd under SAP WO# 902306764, which replaced SAP WO# TD923713
N/A | PB-22.03 | Magunden-Vestal No.1 TLRR Remediation | 35.361, -118.922 / 35.842, -119.085 | Tulare County & Bakersfield, Kern County | Magunden-Vestal No. 1 - 65 discrepancies - R/R 16 structures - 28 mile reconductor - replace OHGW | Transmission Line (reconductor and modification) | Reconductor | PB-22.04, SP-22 | Other - See Notes | NERC Compliance - GO 95 | Inspections do not drive the need for TLRR projects. However, SCE performs annual patrols and triennial detailed inspections of its transmission circuits, which inspect the structures and lines on those circuits. The date of last inspection for this circuit was 8/22/2019 | 90-100 years | IEEE-738 is the standard for calculating the current-temperature relationship of bare overhead conductors. This analysis along with SCE's standard rating methodology was used in conjunction with the PLS-CADD model that was created from the LiDAR study to identify any potential clearance issues on the circuits. | Transmission line clearance discrepancies are remediated based on a series of criteria, including line sag when operating at or above 130 degrees Fahrenheit; potential risk to public safety; and system reliability risk based on the location of span, terrain, encroachment type, and extent of deviation from standards. Discrepancies may be remediated by a variety of construction activities, including, but not limited to Structure Replacements, Structure Raises, New Structure Insets, Line Reconductor, Line Re-tension, Hardware Replacements, Grading, Removing Encroachments, Undergrounding Line Segments, Rerouting Lines. | Non-HFRA | See Note 16B | The asset’s service life can be affected by the following environmental factors; high corrosive soils, weather climates, airborne contamination, and pollution. | Demetric Brown, MPO - Programs | 28 | See Note 20B | 220kV | See Note 22A | See Note 23B | 901638336 | CET-PD-OT-PJ-TR | 7298 | See Note 27A | Yes | 2016 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2019 = 24,319 2020 = 395 2021 = -88 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2017-06-06 | No | 2018-12-31 | 2019-03-08 | N/A | 20060 | 20060 | See Note 53A | 24626.2648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16346.2437 | 7972.5554 | 395.0854 | -87.6198 | 0 | 24626.2648 | 2417.5333 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | -4.626e-11 | None | 100% | 0% | Column 9: In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions. Column 52: Source= PMWIF (v1 Project Summary)
N/A | PB-22.04 | Rector-Vestal No.1 TLRR Remediation | 36.304, -119.244 / 35.842, -119.085 | Tulare County | Rector-Vestal No. 1 - 62 discrepancies - R/R 2 structures - 33 mile reconductor - replace OHGW | Transmission Line (reconductor and modification) | Reconductor | PB-22.03, SP-22 | Other - See Notes | NERC Compliance - GO 95 | Inspections do not drive the need for TLRR projects. However, SCE performs annual patrols and triennial detailed inspections of its transmission circuits, which inspect the structures and lines on those circuits. The date of last inspection for this circuit was 6/16/2019 | 90-100 years | IEEE-738 is the standard for calculating the current-temperature relationship of bare overhead conductors. This analysis along with SCE's standard rating methodology was used in conjunction with the PLS-CADD model that was created from the LiDAR study to identify any potential clearance issues on the circuits. | Transmission line clearance discrepancies are remediated based on a series of criteria, including line sag when operating at or above 130 degrees Fahrenheit; potential risk to public safety; and system reliability risk based on the location of span, terrain, encroachment type, and extent of deviation from standards. Discrepancies may be remediated by a variety of construction activities, including, but not limited to Structure Replacements, Structure Raises, New Structure Insets, Line Reconductor, Line Re-tension, Hardware Replacements, Grading, Removing Encroachments, Undergrounding Line Segments, Rerouting Lines. | Non-HFRA | See Note 16B | The asset’s service life can be affected by the following environmental factors; high corrosive soils, weather climates, airborne contamination, and pollution. | Demetric Brown, MPO - Programs | 33 | See Note 20B | 220kV | See Note 22A | See Note 23B | 901653255 | CET-PD-OT-PJ-TR | 7298 | See Note 27A | Yes | 2017 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2018 = 20,435 2019 = 867 2020 = 265 2021 = 8 2022 = 4 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2017-05-01 | No | 2019-12-31 | 2018-12-19 | Driven by budget Plan & OD Changes | 16867 | 16867 | See Note 53A | 21577.9639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20435.3964 | 866.5146 | 264.6076 | 7.697 | 3.7483 | 21577.9639 | 1844.5485 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | 3.0632e-12 | None | 100% | 0% | Column 9: In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions. Column 52: Source= PMWIF (v1 Project Summary)
N/A | PB-22.05 | Rector-Vestal No.2 TLRR Remediation | 36.304, -119.244 / 35.842, -119.085 | Tulare County | Rector-Vestal No. 2 -73 discrepancies - R/R 1 structure - 33 mile reconductor - replace OHGW | Transmission Line (reconductor and modification) | Reconductor | PB-22.06, SP-22 | Other - See Notes | NERC Compliance - GO 95 | Inspections do not drive the need for TLRR projects. However, SCE performs annual patrols and triennial detailed inspections of its transmission circuits, which inspect the structures and lines on those circuits. The date of last inspection for this circuit was 6/16/2019 | 90-100 years | IEEE-738 is the standard for calculating the current-temperature relationship of bare overhead conductors. This analysis along with SCE's standard rating methodology was used in conjunction with the PLS-CADD model that was created from the LiDAR study to identify any potential clearance issues on the circuits. | Transmission line clearance discrepancies are remediated based on a series of criteria, including line sag when operating at or above 130 degrees Fahrenheit; potential risk to public safety; and system reliability risk based on the location of span, terrain, encroachment type, and extent of deviation from standards. Discrepancies may be remediated by a variety of construction activities, including, but not limited to Structure Replacements, Structure Raises, New Structure Insets, Line Reconductor, Line Re-tension, Hardware Replacements, Grading, Removing Encroachments, Undergrounding Line Segments, Rerouting Lines. | Non-HFRA | See Note 16B | The asset’s service life can be affected by the following environmental factors; high corrosive soils, weather climates, airborne contamination, and pollution. | Demetric Brown, MPO - Programs | 33 | See Note 20B | 220kV | See Note 22A | See Note 23B | 901653257 | CET-PD-OT-PJ-TR | 7298 | See Note 27A | Yes | 2017 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2018 = 21,964 2019 = 533 2020 = 318 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2017-04-03 | No | 2018-12-31 | 2018-08-20 | N/A | 16876 | 16876 | See Note 53A | 22815.341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21964.4849 | 532.9847 | 317.8715 | 0 | 0 | 22815.341 | 2054.0527 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | 1.283e-11 | None | 100% | 0% | Column 9: In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions. Column 52: Source= PMWIF (v1 Project Summary)
N/A | PB-22.06 | Magunden-Vestal No.2 TLRR Remediation | 35.361, -118.922 / 35.842, -119.085 | Tulare County & Bakersfield, Kern County | Magunden-Vestal No. 2 - 84 discrepancies - R/R 18 structures - 35 mile reconductor - replace OHGW | Transmission Line (reconductor and modification) | Reconductor | PB-22.05, SP-22 | Other - See Notes | NERC Compliance - GO 95 | Inspections do not drive the need for TLRR projects. However, SCE performs annual patrols and triennial detailed inspections of its transmission circuits, which inspect the structures and lines on those circuits. The date of last inspection for this circuit was 8/20/2019 | 90-100 years | IEEE-738 is the standard for calculating the current-temperature relationship of bare overhead conductors. This analysis along with SCE's standard rating methodology was used in conjunction with the PLS-CADD model that was created from the LiDAR study to identify any potential clearance issues on the circuits. | Transmission line clearance discrepancies are remediated based on a series of criteria, including line sag when operating at or above 130 degrees Fahrenheit; potential risk to public safety; and system reliability risk based on the location of span, terrain, encroachment type, and extent of deviation from standards. Discrepancies may be remediated by a variety of construction activities, including, but not limited to Structure Replacements, Structure Raises, New Structure Insets, Line Reconductor, Line Re-tension, Hardware Replacements, Grading, Removing Encroachments, Undergrounding Line Segments, Rerouting Lines. | Non-HFRA | See Note 16B | The asset’s service life can be affected by the following environmental factors; high corrosive soils, weather climates, airborne contamination, and pollution. | Demetric Brown, MPO - Programs | 35 | See Note 20B | 220kV | See Note 22A | See Note 23B | 901653359 | CET-PD-OT-PJ-TR | 7298 | See Note 27A | Yes | 2016 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2019 = 32,077 2020 = 396 2021 = -65 2022 = 5 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2017-06-06 | No | 2018-12-31 | 2019-05-16 | N/A | 31370 | 31370 | See Note 53A | 32413.2346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29092.9032 | 2984.5685 | 395.5659 | -65.0847 | 5.2818 | 32413.2346 | 3732.8837 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | 1.7877e-13 | None | 100% | 0% | Column 9: In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions. Column 52: Source= PMWIF (v1 Project Summary)
N/A | PB-22.07 | Antelope-Magunden No.2 TLRR Remediation (1) | 34.688, -118.300 / 35.361, -118.922 | Lancaster, Los Angeles County & Kern County | Antelope-Magunden No.2 - 53 discrepancies (SJ) - raise 41 structures - interset 1 structure | Transmission Line (modification) | Modification/Upgrade | PB-22.01 | Other - See Notes | NERC Compliance - GO 95 | Inspections do not drive the need for TLRR projects. However, SCE performs annual patrols and triennial detailed inspections of its transmission circuits, which inspect the structures and lines on those circuits. The date of last inspection for this circuit was 10/31/2019 | 80-90 years | IEEE-738 is the standard for calculating the current-temperature relationship of bare overhead conductors. This analysis along with SCE's standard rating methodology was used in conjunction with the PLS-CADD model that was created from the LiDAR study to identify any potential clearance issues on the circuits. | Transmission line clearance discrepancies are remediated based on a series of criteria, including line sag when operating at or above 130 degrees Fahrenheit; potential risk to public safety; and system reliability risk based on the location of span, terrain, encroachment type, and extent of deviation from standards. Discrepancies may be remediated by a variety of construction activities, including, but not limited to Structure Replacements, Structure Raises, New Structure Insets, Line Reconductor, Line Re-tension, Hardware Replacements, Grading, Removing Encroachments, Undergrounding Line Segments, Rerouting Lines. | Tier 2 | See Note 16B | The asset’s service life can be affected by the following environmental factors; high corrosive soils, weather climates, airborne contamination, and pollution. | Demetric Brown, MPO - Programs | 58 | See Note 20B | 220kV | See Note 22A | See Note 23B | 901663240 | CET-PD-OT-PJ-TR | 7298 | See Note 27A | Yes | 2016 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2018 = 12,485 2019 = 13 2020 = 69 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2017-10-10 | No | 2018-12-31 | 2018-08-13 | N/A | 20685 | 20685 | See Note 53A | 12566.5428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12484.5308 | 13.4906 | 68.5214 | 0 | 0 | 12566.5428 | 1080.7347 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | 4.9526e-12 | None | 100% | 0% | Column 9: In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions. Column 52: Source= PMWIF (v1 Project Summary)
N/A | PB-22.08 | Magunden-Springville No.1 TLRR Remediation | 35.361, -118.922 / 36.108, -118.938 | Tulare County & Bakersfield, Kern County | Magunden-Springville No. 1 - 74 discrepancies - R/R 5 structures - 50 mile reconductor | Transmission Line (reconductor and modification) | Reconductor | None | Other - See Notes | NERC Compliance - GO 95 | Inspections do not drive the need for TLRR projects. However, SCE performs annual patrols and triennial detailed inspections of its transmission circuits, which inspect the structures and lines on those circuits. The date of last inspection for this circuit was 8/23/2019 | 80-90 years | IEEE-738 is the standard for calculating the current-temperature relationship of bare overhead conductors. This analysis along with SCE's standard rating methodology was used in conjunction with the PLS-CADD model that was created from the LiDAR study to identify any potential clearance issues on the circuits. | Transmission line clearance discrepancies are remediated based on a series of criteria, including line sag when operating at or above 130 degrees Fahrenheit; potential risk to public safety; and system reliability risk based on the location of span, terrain, encroachment type, and extent of deviation from standards. Discrepancies may be remediated by a variety of construction activities, including, but not limited to Structure Replacements, Structure Raises, New Structure Insets, Line Reconductor, Line Re-tension, Hardware Replacements, Grading, Removing Encroachments, Undergrounding Line Segments, Rerouting Lines. | Tier 2 | See Note 16B | The asset’s service life can be affected by the following environmental factors; high corrosive soils, weather climates, airborne contamination, and pollution. | Demetric Brown, MPO - Programs | 50 | See Note 20B | 220kV | See Note 22A | See Note 23B | TD923713 | CET-PD-OT-PJ-TR | 7298 | See Note 27A | Yes | 2016 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2016 = 26,491 2017 = 517 2018 = 180 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | Not Available | No | 2016-12-31 | 2016-07-08 | N/A | 24111 | 24111 | See Note 53A | 27189.0394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27188.3984 | 0 | 0.21142 | 0.42956 | 0 | 27189.0394 | 2161.8541 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | 7.4506e-12 | None | 100% | 0% | Column 9: In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions. Column 52: Source= PMWIF (v1 Proj Summary) as PMWIF'd under SAP WO# 901881009 which was later replaced with SAP WO# TD923713
N/A | PB-22.09 | Kramer-Lugo No.1 TLRR Remediation | 34.989, -117.543 / 34.367, -117.369 | San Bernardino County, Adelanto, Victorville | Kramer-Lugo No. 1 - 2 discrepancies - raise 2 structures | Transmission Line (modification) | Modification/Upgrade | None | Other - See Notes | NERC Compliance - GO 95 | Inspections do not drive the need for TLRR projects. However, SCE performs annual patrols and triennial detailed inspections of its transmission circuits, which inspect the structures and lines on those circuits. The date of last inspection for this circuit was 4/17/2017 | 40-50 years | IEEE-738 is the standard for calculating the current-temperature relationship of bare overhead conductors. This analysis along with SCE's standard rating methodology was used in conjunction with the PLS-CADD model that was created from the LiDAR study to identify any potential clearance issues on the circuits. | Transmission line clearance discrepancies are remediated based on a series of criteria, including line sag when operating at or above 130 degrees Fahrenheit; potential risk to public safety; and system reliability risk based on the location of span, terrain, encroachment type, and extent of deviation from standards. Discrepancies may be remediated by a variety of construction activities, including, but not limited to Structure Replacements, Structure Raises, New Structure Insets, Line Reconductor, Line Re-tension, Hardware Replacements, Grading, Removing Encroachments, Undergrounding Line Segments, Rerouting Lines. | Tier 2 | See Note 16B | The asset’s service life can be affected by the following environmental factors; high corrosive soils, weather climates, airborne contamination, and pollution. | Demetric Brown, MPO - Programs | 33 | See Note 20B | 220kV | See Note 22A | See Note 23B | 901848367 | CET-PD-OT-PJ-729800 | 7298 | See Note 27A | Yes | 2016 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2017 = 1,633 2018 = 13 2019 = 3 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | Not Available | No | 2017-12-31 | 2017-05-22 | Driven by budget Plan & OD Changes | 4000 | 4000 | See Note 53A | 1649.1308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1646.1444 | 2.9864 | 0 | 0 | 0 | 1649.1308 | 133.9551 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | -3.9199e-13 | None | 100% | 0% | Column 9: In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions. Column 52: Source= PMWIF (v1 Project Summary)
N/A | PB-22.10 | Magunden-Springville No.2 TLRR Remediation | 35.361, -118.922 / 36.108, -118.938 | Tulare County & Bakersfield, Kern County | Magunden-Springville No. 2 - 2 discrepancies - R/R 1 structure | Transmission Line (modification) | Modification/Upgrade | None | Other - See Notes | NERC Compliance - GO 95 | Inspections do not drive the need for TLRR projects. However, SCE performs annual patrols and triennial detailed inspections of its transmission circuits, which inspect the structures and lines on those circuits. The date of last inspection for this circuit was 8/23/2019 | 50-60 years | IEEE-738 is the standard for calculating the current-temperature relationship of bare overhead conductors. This analysis along with SCE's standard rating methodology was used in conjunction with the PLS-CADD model that was created from the LiDAR study to identify any potential clearance issues on the circuits. | Transmission line clearance discrepancies are remediated based on a series of criteria, including line sag when operating at or above 130 degrees Fahrenheit; potential risk to public safety; and system reliability risk based on the location of span, terrain, encroachment type, and extent of deviation from standards. Discrepancies may be remediated by a variety of construction activities, including, but not limited to Structure Replacements, Structure Raises, New Structure Insets, Line Reconductor, Line Re-tension, Hardware Replacements, Grading, Removing Encroachments, Undergrounding Line Segments, Rerouting Lines. | Tier 2 | See Note 16B | The asset’s service life can be affected by the following environmental factors; high corrosive soils, weather climates, airborne contamination, and pollution. | Demetric Brown, MPO - Programs | 0.5 | See Note 20B | 220kV | See Note 22A | See Note 23B | 901881000 | CET-PD-OT-PJ-729800 | 7298 | See Note 27A | Yes | 2016 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2017 = 756 2018 = 429 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2016-09-08 | No | 2017-12-31 | 2017-09-28 | N/A | 475 | 475 | See Note 53A | 1184.8169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1184.8169 | 0 | 0 | 0 | 0 | 1184.8169 | 182.845 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | 3.9259e-13 | None | 100% | 0% | Column 9: In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions. Column 52: Source= PMWIF (v1 Project Summary)
N/A | PB-22.11 | Big Creek 1-Rector TLRR Remediation (1) | 37.204, -119.240 / 36.304, -119.244 | Orange Cove, Fresno County & Visalia, Tulare County | Big Creek 1-Rector 220kV - TLRR WO 901881001 This WO has 144 discrepancies to be remediated. Scope – ~63 mile reconductor and 20 AmpJack structure raises FLOC #s ET-01082 Discrepancy #s as shown: 4200583, 4200584, 4200585, 4200586, 4200587, 4200588, 4200589, 4200590, 4200591, 4200592, 4200593, 4200594, 4200596, 4200597, 4200598, 4200599, 4200600, 4200601, 4200602, 4200603, 4200604, 4200605, 4200606, 4200607, 4200608, 4200609, 4200610, 4200611, 4200612, 4200613, 4200614, 4200615, 4200616, 4200617, 4200618, 4200619, 4200620, 4200621, 4200622, 4200623, 4200624, 4200626, 4200627, 4200628, 4200629, 4200631, 4200632, 4200633, 4200634, 4200635, 4200637, 4200638, 4200639, 4200640, 4200641, 4200642, 4200646, 4200647, 4200648, 4200649, 4200652, 4200653, 4200654, 4200655, 4200656, 4200657, 4200659, 4200660, 4200661, 4200662, 4200663, 4200664, 4200665, 4200667, 4200670, 4200671, 4200672, 4200673, 4200675, 4200676, 4200677, 4200678, 4200680, 4200681, 4200682, 4200683, 4200684, 4200685, 4200686, 4200690, 4200691, 4200692, 4200693, 4200694, 4200695, 4200697, 4200698, 4200699, 4200700, 4200701, 4200702, 4200703, 4200704, 4200705, 4200706, 4200707, 4200708, 4200709, 4200710, 4200711, 4200713, 4200714, 4200716, 4200717, 4200718, 4200719, 4200720, 4200721, 4200722, 4200740, 4200741, 4200743, 4200750, 4200751, 4200752, 4200753, 4200754, 4200755, 4200756, 4200757, 4200758, 4200759, 4200760, 4200761, 4200762, 4200763, 4200764, 4200765, 4200766, 4200767, 4200768, 4200770, 4200771, 4200773. | Transmission Line (reconductor and modification) | Reconductor | PB-22.62, PB-22.64, PB-22.63, PB-22.40, PB-22.56, PB-22.29, PB-22.58 | Other - See Notes | NERC Compliance - GO 95 | Inspections do not drive the need for TLRR projects. However, SCE performs annual patrols and triennial detailed inspections of its transmission circuits, which inspect the structures and lines on those circuits. The date of last inspection for this circuit was 7/25/2019 | 70-80 years | IEEE-738 is the standard for calculating the current-temperature relationship of bare overhead conductors. This analysis along with SCE's standard rating methodology was used in conjunction with the PLS-CADD model that was created from the LiDAR study to identify any potential clearance issues on the circuits. | Transmission line clearance discrepancies are remediated based on a series of criteria, including line sag when operating at or above 130 degrees Fahrenheit; potential risk to public safety; and system reliability risk based on the location of span, terrain, encroachment type, and extent of deviation from standards. Discrepancies may be remediated by a variety of construction activities, including, but not limited to Structure Replacements, Structure Raises, New Structure Insets, Line Reconductor, Line Re-tension, Hardware Replacements, Grading, Removing Encroachments, Undergrounding Line Segments, Rerouting Lines. | Zone 1, Tier 2, Tier 3 | See Note 16B | The asset’s service life can be affected by the following environmental factors; high corrosive soils, weather climates, airborne contamination, and pollution. | Demetric Brown, MPO - Programs | 60 | See Note 20B | 220kV | See Note 22A | See Note 23B | 901881001 | CET-PD-OT-PJ-729800 | 7298 | See Note 27A | Yes | 2016 | Pre-2017 | FRM/CRT | No | N/A | N/A | N/A | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | On Hold | See Note 46A | 2019-08-27 | No | 2021-12-31 | 2024-06-01 | Driven by budget Plan & OD Changes | 58348 | 58348 | See Note 53A | 77458.4417 | 265 | 3569.817 | 0 | 0 | 0 | 0 | 3834.817 | 2390.6895 | 15971.3212 | 27847.9224 | 19296.4472 | 8117.2443 | 73623.6247 | 11645.0396 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | 66005.082 | None | 100% | 0% | Column 9: In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions. Process for Utility Approval: The TLRR Program received FRM Approval for all non-operational projects on 4/1/2021. General: This project is in a group of projects that are in the middle of the change management process to align schedules based on resource and outage availability. Costs forecasts have been updated for planning purposes, and schedule dates (including in-service dates) will be updated once the change management process is complete. Column 52: Source= PMWIF (v1 Proj Summary) Column 45: Project on holding pending the outcome of a pending material evaluation.
N/A | PB-22.12 | Midway-Vincent No.2 TLRR Remediation (1) | 35.404, -119.450 / 34.486, -118.118 | Buttonwillow, Kern County & Palmdale, Los Angeles County & Ventura County | Midway-Vincent No. 2 500kV - TLRR WO 901881004 This WO has 8 discrepancy to be remediated. Scope – 9 AmpJack structure raises. FLOC #s ET-00127-04626 Discrepancy #s as shown: 4600263, 4600264, 4600265, 4600273, 4600274, 4600275, 4600278, 4600280. | Transmission Line (modification) | Modification/Upgrade | PB-22.57 | Other - See Notes | NERC Compliance - GO 95 | Inspections do not drive the need for TLRR projects. However, SCE performs annual patrols and triennial detailed inspections of its transmission circuits, which inspect the structures and lines on those circuits. The date of last inspection for this circuit was 11/15/2019 | 40-50 years | IEEE-738 is the standard for calculating the current-temperature relationship of bare overhead conductors. This analysis along with SCE's standard rating methodology was used in conjunction with the PLS-CADD model that was created from the LiDAR study to identify any potential clearance issues on the circuits. | Transmission line clearance discrepancies are remediated based on a series of criteria, including line sag when operating at or above 130 degrees Fahrenheit; potential risk to public safety; and system reliability risk based on the location of span, terrain, encroachment type, and extent of deviation from standards. Discrepancies may be remediated by a variety of construction activities, including, but not limited to Structure Replacements, Structure Raises, New Structure Insets, Line Reconductor, Line Re-tension, Hardware Replacements, Grading, Removing Encroachments, Undergrounding Line Segments, Rerouting Lines. | Tier 2, Tier 3 | See Note 16B | The asset’s service life can be affected by the following environmental factors; high corrosive soils, weather climates, airborne contamination, and pollution. | Demetric Brown, MPO - Programs | 58 | See Note 20B | 500kV | See Note 22A | See Note 23B | 901881004 | CET-PD-OT-PJ-729800 | 7298 | See Note 27A | Yes | 2016 | Pre-2017 | FRM/CRT | No | N/A | N/A | N/A | See Col. 37 | 2021 = 7,646 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2018-11-03 | No | 2021-12-31 | 2021-06-24 | Driven by budget Plan & OD Changes | 3021 | 3021 | See Note 53A | 7646.4218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1573.3927 | 1151.9123 | 2996.4319 | 1924.4173 | 0.26771 | 7646.4218 | 1078.2457 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | -3.4342e-12 | None | 100% | 0% | Column 9: In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions. Process for Utility Approval: The TLRR Program received FRM Approval for all non-operational projects on 4/1/2021. Column 52: Source= PMWIF (v1 Proj Summary); SCE provided in its Feb 2021 SRP Supplement a cost of $1.468M which was pulled from the system using a code which has subsequently corrected. Consistent with the methodology for the July SRP, SCE provides the original project cost from the PMWIF (v1 Proj Summary)
N/A | PB-22.13 | Antelope-Magunden No.1 TLRR Remediation (1) | 34.688, -118.300 / 35.361, -118.922 | Lancaster, Los Angeles County & Kern County | Antelope-Magunden No.1 - 13 discrepancies (SJ) - R/R 6 structures - 6 mi reconductor | Transmission Line (reconductor and modification) | Reconductor | None | Other - See Notes | NERC Compliance - GO 95 | Inspections do not drive the need for TLRR projects. However, SCE performs annual patrols and triennial detailed inspections of its transmission circuits, which inspect the structures and lines on those circuits. The date of last inspection for this circuit was 10/31/2019 | 50-60 years | IEEE-738 is the standard for calculating the current-temperature relationship of bare overhead conductors. This analysis along with SCE's standard rating methodology was used in conjunction with the PLS-CADD model that was created from the LiDAR study to identify any potential clearance issues on the circuits. | Transmission line clearance discrepancies are remediated based on a series of criteria, including line sag when operating at or above 130 degrees Fahrenheit; potential risk to public safety; and system reliability risk based on the location of span, terrain, encroachment type, and extent of deviation from standards. Discrepancies may be remediated by a variety of construction activities, including, but not limited to Structure Replacements, Structure Raises, New Structure Insets, Line Reconductor, Line Re-tension, Hardware Replacements, Grading, Removing Encroachments, Undergrounding Line Segments, Rerouting Lines. | Tier 2 | See Note 16B | The asset’s service life can be affected by the following environmental factors; high corrosive soils, weather climates, airborne contamination, and pollution. | Demetric Brown, MPO - Programs | 6 | See Note 20B | 220kV | See Note 22A | See Note 23B | 901881005 | CET-PD-OT-PJ-729800 | 7298 | See Note 27A | Yes | 2016 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2017 = 4,232 2018 = 271 2019 = 12 2020 = 3 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2017-09-05 | No | 2017-12-31 | 2017-10-03 | N/A | 6040 | 6040 | See Note 53A | 4517.4591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4503.2876 | 11.5365 | 2.635 | 0 | 0 | 4517.4591 | 445.5376 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | 2.633e-12 | None | 100% | 0% | Column 9: In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions. Column 52: Source= PMWIF (v1 Project Summary)
N/A | PB-22.14 | Antelope-Magunden No.1 TLRR Remediation (1) | 34.688, -118.300 / 35.361, -118.922 | Lancaster, Los Angeles County & Kern County | Antelope-Magunden No.1 - 3 discrepancies (H) - R/R 3 structures | Transmission Line (modification) | Modification/Upgrade | None | Other - See Notes | NERC Compliance - GO 95 | Inspections do not drive the need for TLRR projects. However, SCE performs annual patrols and triennial detailed inspections of its transmission circuits, which inspect the structures and lines on those circuits. The date of last inspection for this circuit was 10/31/2019 | 50-60 years | IEEE-738 is the standard for calculating the current-temperature relationship of bare overhead conductors. This analysis along with SCE's standard rating methodology was used in conjunction with the PLS-CADD model that was created from the LiDAR study to identify any potential clearance issues on the circuits. | Transmission line clearance discrepancies are remediated based on a series of criteria, including line sag when operating at or above 130 degrees Fahrenheit; potential risk to public safety; and system reliability risk based on the location of span, terrain, encroachment type, and extent of deviation from standards. Discrepancies may be remediated by a variety of construction activities, including, but not limited to Structure Replacements, Structure Raises, New Structure Insets, Line Reconductor, Line Re-tension, Hardware Replacements, Grading, Removing Encroachments, Undergrounding Line Segments, Rerouting Lines. | Tier 2 | See Note 16B | The asset’s service life can be affected by the following environmental factors; high corrosive soils, weather climates, airborne contamination, and pollution. | Demetric Brown, MPO - Programs | 5 | See Note 20B | 220kV | See Note 22A | See Note 23B | 901881006 | CET-PD-OT-PJ-729800 | 7298 | See Note 27A | Yes | 2016 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2017 = 1,662 2018 = 178 2019 = 14 2020 = 3 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2017-07-24 | No | 2017-12-31 | 2017-10-05 | N/A | 1394 | 1394 | See Note 53A | 1856.904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1840.0342 | 13.7686 | 3.1012 | 0 | 0 | 1856.904 | 252.1589 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | -4.0836e-13 | None | 100% | 0% | Column 9: In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions. Column 52: Source= PMWIF (v1 Project Summary)
N/A | PB-22.15 | Midway-Whirlwind TLRR Remediation | 35.404, -119.450 / 34.857, -118.436 | Kern County | Midway-Whirlwind - 3 discrepancies - raise 1 structures - R/R 1 structure | Transmission Line (modification) | Modification/Upgrade | None | Other - See Notes | NERC Compliance - GO 95 | Inspections do not drive the need for TLRR projects. However, SCE performs annual patrols and triennial detailed inspections of its transmission circuits, which inspect the structures and lines on those circuits. The date of last inspection for this circuit was 10/28/2019 | 40-50 years | IEEE-738 is the standard for calculating the current-temperature relationship of bare overhead conductors. This analysis along with SCE's standard rating methodology was used in conjunction with the PLS-CADD model that was created from the LiDAR study to identify any potential clearance issues on the circuits. | Transmission line clearance discrepancies are remediated based on a series of criteria, including line sag when operating at or above 130 degrees Fahrenheit; potential risk to public safety; and system reliability risk based on the location of span, terrain, encroachment type, and extent of deviation from standards. Discrepancies may be remediated by a variety of construction activities, including, but not limited to Structure Replacements, Structure Raises, New Structure Insets, Line Reconductor, Line Re-tension, Hardware Replacements, Grading, Removing Encroachments, Undergrounding Line Segments, Rerouting Lines. | Tier 2 | See Note 16B | The asset’s service life can be affected by the following environmental factors; high corrosive soils, weather climates, airborne contamination, and pollution. | Demetric Brown, MPO - Programs | 1.8 | See Note 20B | 500kV | See Note 22A | See Note 23B | 901881008 | CET-PD-OT-PJ-729800 | 7298 | See Note 27A | Yes | 2016 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2017 = 1,638 2018 = 161 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2016-07-25 | No | 2019-12-31 | 2017-04-27 | Driven by budget Plan & OD Changes | 374 | 374 | See Note 53A | 1799.357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1799.357 | 0 | 0 | 0 | 0 | 1799.357 | 118.5266 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | -1.1105e-12 | None | 100% | 0% | Column 9: In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions. Column 52: Source= PMWIF (v1 Project Summary)
N/A | PB-22.16 | Pardee-Santa Clara TLRR Remediation | 34.440, -118.582 / 34.302, -119.186 | Santa Paula/ Piru, Ventura County & Santa Clarita, Los Angeles County | Pardee-Santa Clara - 2 discrepancies - R/R 2 structures | Transmission Line (modification) | Modification/Upgrade | None | Other - See Notes | NERC Compliance - GO 95 | Inspections do not drive the need for TLRR projects. However, SCE performs annual patrols and triennial detailed inspections of its transmission circuits, which inspect the structures and lines on those circuits. The date of last inspection for this circuit was 5/31/2019 | 60-70 years | IEEE-738 is the standard for calculating the current-temperature relationship of bare overhead conductors. This analysis along with SCE's standard rating methodology was used in conjunction with the PLS-CADD model that was created from the LiDAR study to identify any potential clearance issues on the circuits. | Transmission line clearance discrepancies are remediated based on a series of criteria, including line sag when operating at or above 130 degrees Fahrenheit; potential risk to public safety; and system reliability risk based on the location of span, terrain, encroachment type, and extent of deviation from standards. Discrepancies may be remediated by a variety of construction activities, including, but not limited to Structure Replacements, Structure Raises, New Structure Insets, Line Reconductor, Line Re-tension, Hardware Replacements, Grading, Removing Encroachments, Undergrounding Line Segments, Rerouting Lines. | Tier 3 | See Note 16B | The asset’s service life can be affected by the following environmental factors; high corrosive soils, weather climates, airborne contamination, and pollution. | Demetric Brown, MPO - Programs | 4 | See Note 20B | 220kV | See Note 22A | See Note 23B | 901919850 | CET-PD-OT-PJ-729800 | 7298 | See Note 27A | Yes | 2016 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2016 = 535 2017 = 776 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2016-09-07 | No | 2016-12-31 | 2016-11-18 | N/A | 900 | 900 | See Note 53A | 1311.0065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1311.0065 | 0 | 0 | 0 | 0 | 1311.0065 | 233.1912 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | -1.7342e-13 | None | 100% | 0% | Column 9: In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions. Column 52: Source= Unverified estimate, documents not readily available
N/A | PB-22.17 | Devers-Valley No.1 TLRR Remediation (1) | 33.935, -116.578 / 33.740, -117.157 | Banning/ Beaumont/ Cabazon/ Menifee/ Palm Springs/ White Water Canyon/ Juniper Flats, Riverside County | Devers-Valley No 1 - 3 discrepancies - R/R 2 structures | Transmission Line (modification) | Modification/Upgrade | None | Other - See Notes | NERC Compliance - GO 95 | Inspections do not drive the need for TLRR projects. However, SCE performs annual patrols and triennial detailed inspections of its transmission circuits, which inspect the structures and lines on those circuits. The date of last inspection for this circuit was 9/22/2019 | 30-40 years | IEEE-738 is the standard for calculating the current-temperature relationship of bare overhead conductors. This analysis along with SCE's standard rating methodology was used in conjunction with the PLS-CADD model that was created from the LiDAR study to identify any potential clearance issues on the circuits. | Transmission line clearance discrepancies are remediated based on a series of criteria, including line sag when operating at or above 130 degrees Fahrenheit; potential risk to public safety; and system reliability risk based on the location of span, terrain, encroachment type, and extent of deviation from standards. Discrepancies may be remediated by a variety of construction activities, including, but not limited to Structure Replacements, Structure Raises, New Structure Insets, Line Reconductor, Line Re-tension, Hardware Replacements, Grading, Removing Encroachments, Undergrounding Line Segments, Rerouting Lines. | Non-CPUC HFRA, Tier 2, Tier 3 | See Note 16B | The asset’s service life can be affected by the following environmental factors; high corrosive soils, weather climates, airborne contamination, and pollution. | Demetric Brown, MPO - Programs | 3 | See Note 20B | 500kV | See Note 22A | See Note 23B | 901920163 | CET-PD-OT-PJ-729800 | 7298 | See Note 27A | Yes | 2016 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2017 = 1,893 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2016-09-07 | No | 2016-12-31 | 2017-01-30 | N/A | 1900 | 1900 | See Note 53A | 1892.6361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1892.6361 | 0 | 0 | 0 | 0 | 1892.6361 | 171.7765 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | 2.4886e-13 | None | 100% | 0% | Column 9: In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions. Column 52: Source= PMWIF (v1 Project Summary)
N/A | PB-22.18 | San Onofre-Santiago No.1 TLRR Remediation | 33.371, -117.557 / 33.665, -117.768 | San Diego,Orange County, Alisa Viejo, San Juan Capistrano, Irvine, San Clemente, Laguna Woods, Laguna Hills, Mission Viejo | San Onofre-Santiago No.1 - 2 discrepancies - interset 1 structure | Transmission Line (modification) | Modification/Upgrade | None | Other - See Notes | NERC Compliance - GO 95 | Inspections do not drive the need for TLRR projects. However, SCE performs annual patrols and triennial detailed inspections of its transmission circuits, which inspect the structures and lines on those circuits. The date of last inspection for this circuit was 10/20/2019 | 50-60 years | IEEE-738 is the standard for calculating the current-temperature relationship of bare overhead conductors. This analysis along with SCE's standard rating methodology was used in conjunction with the PLS-CADD model that was created from the LiDAR study to identify any potential clearance issues on the circuits. | Transmission line clearance discrepancies are remediated based on a series of criteria, including line sag when operating at or above 130 degrees Fahrenheit; potential risk to public safety; and system reliability risk based on the location of span, terrain, encroachment type, and extent of deviation from standards. Discrepancies may be remediated by a variety of construction activities, including, but not limited to Structure Replacements, Structure Raises, New Structure Insets, Line Reconductor, Line Re-tension, Hardware Replacements, Grading, Removing Encroachments, Undergrounding Line Segments, Rerouting Lines. | Tier 2, Tier 3 | See Note 16B | The asset’s service life can be affected by the following environmental factors; high corrosive soils, weather climates, airborne contamination, and pollution. | Demetric Brown, MPO - Programs | 1 | See Note 20B | 220kV | See Note 22A | See Note 23B | 901933431 | CET-PD-OT-PJ-729800 | 7298 | See Note 27A | Yes | 2016 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2017 = 668 2018 = 448 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2016-11-15 | No | 2016-12-31 | 2017-01-04 | N/A | 926 | 926 | See Note 53A | 1115.7214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1115.7214 | 0 | 0 | 0 | 0 | 1115.7214 | 117.1389 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | -2.8064e-13 | None | 100% | 0% | Column 9: In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions. Column 52: Source= PMWIF (v2 Project Summary)
N/A | PB-22.19 | Padua-Rancho Vista No.1 TLRR Remediation | 34.120, -117.639 / 34.518, -117.216 | San Antonio Heights/ Rancho Cucamonga/ Upland, San Bernardino County | Padua-Rancho Vista No.1 - 2 discrepancies - R/R 1 structure | Transmission Line (modification) | Modification/Upgrade | None | Other - See Notes | NERC Compliance - GO 95 | Inspections do not drive the need for TLRR projects. However, SCE performs annual patrols and triennial detailed inspections of its transmission circuits, which inspect the structures and lines on those circuits. The date of last inspection for this circuit was 3/17/2019 | 40-50 years | IEEE-738 is the standard for calculating the current-temperature relationship of bare overhead conductors. This analysis along with SCE's standard rating methodology was used in conjunction with the PLS-CADD model that was created from the LiDAR study to identify any potential clearance issues on the circuits. | Transmission line clearance discrepancies are remediated based on a series of criteria, including line sag when operating at or above 130 degrees Fahrenheit; potential risk to public safety; and system reliability risk based on the location of span, terrain, encroachment type, and extent of deviation from standards. Discrepancies may be remediated by a variety of construction activities, including, but not limited to Structure Replacements, Structure Raises, New Structure Insets, Line Reconductor, Line Re-tension, Hardware Replacements, Grading, Removing Encroachments, Undergrounding Line Segments, Rerouting Lines. | Tier 2, Tier 3 | See Note 16B | The asset’s service life can be affected by the following environmental factors; high corrosive soils, weather climates, airborne contamination, and pollution. | Demetric Brown, MPO - Programs | 0.5 | See Note 20B | 220kV | See Note 22A | See Note 23B | 901933433 | CET-PD-OT-PJ-729800 | 7298 | See Note 27A | Yes | 2016 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2017 = 1,276 2018 = 24 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | Not Available | No | 2016-12-31 | 2017-01-05 | N/A | 812 | 812 | See Note 53A | 1300.6736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1300.6736 | 0 | 0 | 0 | 0 | 1300.6736 | 96.6919 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | 5.2444e-13 | None | 100% | 0% | Column 9: In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions. Column 52: Source= PMWIF (v2 Project Summary)
N/A | PB-22.20 | Eagle Rock-Pardee TLRR Remediation (1) | 34.149, -118.184 / 34.440, -118.582 | Los Angeles(Based on Substation locations) | Eagle Rock-Pardee - 2 discrepancies - interset 1 structure | Transmission Line (modification) | Modification/Upgrade | None | Other - See Notes | NERC Compliance - GO 95 | Inspections do not drive the need for TLRR projects. However, SCE performs annual patrols and triennial detailed inspections of its transmission circuits, which inspect the structures and lines on those circuits. The date of last inspection for this circuit was 3/31/2015 | 40-50 years | IEEE-738 is the standard for calculating the current-temperature relationship of bare overhead conductors. This analysis along with SCE's standard rating methodology was used in conjunction with the PLS-CADD model that was created from the LiDAR study to identify any potential clearance issues on the circuits. | Transmission line clearance discrepancies are remediated based on a series of criteria, including line sag when operating at or above 130 degrees Fahrenheit; potential risk to public safety; and system reliability risk based on the location of span, terrain, encroachment type, and extent of deviation from standards. Discrepancies may be remediated by a variety of construction activities, including, but not limited to Structure Replacements, Structure Raises, New Structure Insets, Line Reconductor, Line Re-tension, Hardware Replacements, Grading, Removing Encroachments, Undergrounding Line Segments, Rerouting Lines. | Tier 3 | See Note 16B | The asset’s service life can be affected by the following environmental factors; high corrosive soils, weather climates, airborne contamination, and pollution. | Demetric Brown, MPO - Programs | 0.3 | See Note 20B | 220kV | See Note 22A | See Note 23B | 901933437 | CET-PD-OT-PJ-729800 | 7298 | See Note 27A | Yes | 2016 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2016 = 206 2017= 860 2018 = 115 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2016-10-19 | No | 2016-12-31 | 2016-12-05 | N/A | 578 | 578 | See Note 53A | 1181.8607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1181.8607 | 0 | 0 | 0 | 0 | 1181.8607 | 229.4673 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | -6.7075e-13 | None | 100% | 0% | Column 9: In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions. Column 52: Source= PMWIF (v1 Project Summary)
N/A | PB-22.21 | Devers-Red Bluff No.1 TLRR Remediation | 33.935, -116.578 / 33.672, -115.559 | Coachella/ Desert Hot Springs/ Cathedral City/ Indio, Riverside County | Devers-Red Bluff No. 1 500kV - TLRR WO 901942793 This WO has 65 discrepancies to be remediated. Scope – ~80 mile reconductor, 7 AmpJack structure raises FLOC #s ET-00942 Discrepancy #s as shown: 4500046, 4500047, 4500048, 4500049, 4500050, 4500051, 4500052, 4500053, 4500054, 4500055, 4500056, 4500057, 4500058, 4500059, 4500060, 4500061, 4500062, 4500063, 4500064, 4500065, 4500066, 4500067, 4500068, 4500069, 4500070, 4500071, 4500072, 4500073, 4500074, 4500075, 4500076, 4500077, 4500078, 4500079, 4500080, 4500081, 4500082, 4500083, 4500084, 4500085, 4507775, 4507776, 4507777, 4507778, 4507779, 4507780, 4507781, 4507782, 4507783, 4507784, 4507785, 4507786, 4507787, 4507788, 4507789, 4507790, 4507791, 4507792, 4507793, 4507794, 4507795, 4507796, 4507797, 4507798, 4507799, 4507900, 4507901, 4507902, 4507903, 4507904, 4507905, 4507906, 4507907, 4507908, 4507909, 4507910, 4507911, 4507912, 4507913, 4507914, 4507915, 4507916, 4507917, 4507918, 4507919, 4507920, 4507921, 4507922, 4507923, 4507924, 4507925, 4507926, 4507927, 4507928, 4507929, 4507930, 4507931, 4507932, 4507933, 4507934, 4507935. | Transmission Line (reconductor and modification) | Reconductor | PB-22.54 | Other - See Notes | NERC Compliance - GO 95 | Inspections do not drive the need for TLRR projects. However, SCE performs annual patrols and triennial detailed inspections of its transmission circuits, which inspect the structures and lines on those circuits. The date of last inspection for this circuit was 3/17/2019 | ~45 years | IEEE-738 is the standard for calculating the current-temperature relationship of bare overhead conductors. This analysis along with SCE's standard rating methodology was used in conjunction with the PLS-CADD model that was created from the LiDAR study to identify any potential clearance issues on the circuits. | Transmission line clearance discrepancies are remediated based on a series of criteria, including line sag when operating at or above 130 degrees Fahrenheit; potential risk to public safety; and system reliability risk based on the location of span, terrain, encroachment type, and extent of deviation from standards. Discrepancies may be remediated by a variety of construction activities, including, but not limited to Structure Replacements, Structure Raises, New Structure Insets, Line Reconductor, Line Re-tension, Hardware Replacements, Grading, Removing Encroachments, Undergrounding Line Segments, Rerouting Lines. | Non-HFRA | See Note 16B | The asset’s service life can be affected by the following environmental factors; high corrosive soils, weather climates, airborne contamination, and pollution. | Demetric Brown, MPO - Programs | 80 | See Note 20B | 500 kV | See Note 22A | See Note 23B | 901942793 | CET-PD-OT-PJ-729800 | 7298 | See Note 27A | Yes | 2016 | Pre-2017 | FRM/CRT | No | N/A | N/A | N/A | See Col. 37 | 2021 = 73,953 2022 = 86 | CEQA Final Certified Sept 2018 | MND/CatEx | CDFW/BLM | N/A | N/A | Exempt: Not subject to GO 131-D licensing | 2018 | Operational | See Note 46A | 2017-12-15 | No | 2018-12-31 | 2021-01-04 | Driven by Budget Plan & OD Changes | 36868 | 36868 | See Note 53A | 74039.2536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37626.4038 | 20950.8005 | 14503.6553 | 872.1011 | 86.2928 | 74039.2536 | 12054.4824 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | 1.0634e-10 | None | 100% | 0% | Column 9: In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions. Column 12: Based on updated Transmission Engineering input Process for Utility Approval: The TLRR Program received FRM Approval for all non-operational projects on 4/1/2021. Column 52: Source= PMWIF (v4 Proj Summary)
N/A | PB-22.22 | Mesa-Vincent No.1 TLRR Remediation (1) | 34.036, -118.110 / 34.486, -118.118 | East Pasadena/ Altadena/ Monterey Park/ La Canada Flintridge/ South San Gabriel/ Rosemead/ San Gabriel/ Pasadena/ East San Gabriel, Los Angeles County | Mesa-Vincent No.1 - 3 discrepancies - interset 1 structure - 1 mile reconductor | Transmission Line (reconductor and modification) | Reconductor | None | Other - See Notes | NERC Compliance - GO 95 | Inspections do not drive the need for TLRR projects. However, SCE performs annual patrols and triennial detailed inspections of its transmission circuits, which inspect the structures and lines on those circuits. The date of last inspection for this circuit was 11/21/2019 | 50-60 years | IEEE-738 is the standard for calculating the current-temperature relationship of bare overhead conductors. This analysis along with SCE's standard rating methodology was used in conjunction with the PLS-CADD model that was created from the LiDAR study to identify any potential clearance issues on the circuits. | Transmission line clearance discrepancies are remediated based on a series of criteria, including line sag when operating at or above 130 degrees Fahrenheit; potential risk to public safety; and system reliability risk based on the location of span, terrain, encroachment type, and extent of deviation from standards. Discrepancies may be remediated by a variety of construction activities, including, but not limited to Structure Replacements, Structure Raises, New Structure Insets, Line Reconductor, Line Re-tension, Hardware Replacements, Grading, Removing Encroachments, Undergrounding Line Segments, Rerouting Lines. | Tier 2, Tier 3 | See Note 16B | The asset’s service life can be affected by the following environmental factors; high corrosive soils, weather climates, airborne contamination, and pollution. | Demetric Brown, MPO - Programs | 1 | See Note 20B | 220kV | See Note 22A | See Note 23B | 901960233 | CET-PD-OT-PJ-729800 | 7298 | See Note 27A | Yes | 2016 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2018 = 1,506 2019 = -21 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | Not Available | No | 2017-12-31 | 2018-10-03 | Driven by budget Plan & OD Changes | 4000 | 4000 | See Note 53A | 1484.3179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1505.78 | -21.4621 | 0 | 0 | 0 | 1484.3179 | 181.9383 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | -1.8922e-12 | None | 100% | 0% | Column 9: In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions. Column 52: Source= PMWIF (v1 Project Summary)
N/A | PB-22.23 | Bailey-Pardee TLRR Remediation | 34.777, -118.774 / 34.440, -118.582 | Los Angeles County, Santa Clarita | Bailey-Pardee 220kV - TLRR WO 901965548 This WO has 74 discrepancies to be remediated. Scope – ~27 mile reconductor, 20 AmpJack structure raises FLOC #s ET-00665 Discrepancy #s as shown: 4600450, 4600451, 4600452, 4600453, 4600454, 4600455, 4600456, 4600457, 4600458, 4600459, 4600460, 4600461, 4600462, 4600463, 4600464, 4600465, 4600466, 4600467, 4600468, 4600469, 4600471, 4600473, 4600474, 4600475, 4600476, 4600477, 4600478, 4600479, 4600480, 4600481, 4600483, 4600484, 4600485, 4600486, 4600487, 4600488, 4600489, 4600490, 4600491, 4600492, 4600493, 4600495, 4600496, 4600497, 4600498, 4600499, 4600500, 4600502, 4600503, 4600504, 4600505, 4600507, 4600508, 4600509, 4600510, 4600511, 4600512, 4600513, 4600515, 4600516, 4600518, 4600519, 4600520, 4600521, 4600522, 4600523, 4600524, 4600525, 4600526, 4600527, 4600528, 4600529, 4600530, 4600531. | Transmission Line (reconductor and modification) | Reconductor | PB-22.32, PB-22.31, PB-22.47, PB-22.53 | Other - See Notes | NERC Compliance - GO 95 | Inspections do not drive the need for TLRR projects. However, SCE performs annual patrols and triennial detailed inspections of its transmission circuits, which inspect the structures and lines on those circuits. The date of last inspection for this circuit was 1/31/2020 | ~100 years | IEEE-738 is the standard for calculating the current-temperature relationship of bare overhead conductors. This analysis along with SCE's standard rating methodology was used in conjunction with the PLS-CADD model that was created from the LiDAR study to identify any potential clearance issues on the circuits. | Transmission line clearance discrepancies are remediated based on a series of criteria, including line sag when operating at or above 130 degrees Fahrenheit; potential risk to public safety; and system reliability risk based on the location of span, terrain, encroachment type, and extent of deviation from standards. Discrepancies may be remediated by a variety of construction activities, including, but not limited to Structure Replacements, Structure Raises, New Structure Insets, Line Reconductor, Line Re-tension, Hardware Replacements, Grading, Removing Encroachments, Undergrounding Line Segments, Rerouting Lines. | Tier 2, Tier 3 | See Note 16B | The asset’s service life can be affected by the following environmental factors; high corrosive soils, weather climates, airborne contamination, and pollution. | Demetric Brown, MPO - Programs | 27 | See Note 20B | 220kV | See Note 22A | See Note 23B | 901965548 | CET-PD-OT-PJ-729800 | 7298 | See Note 27A | Yes | 2016 | Pre-2017 | FRM/CRT | No | N/A | N/A | N/A | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Engineering more than 50% completed | See Note 46A | 2024-10-01 | No | 2019-12-31 | 2025-12-31 | Driven by budget Plan & OD Changes | 23000 | 23000 | See Note 53A | 36636.0764 | 412.544 | 10338.268 | 14049.449 | 8090.895 | 0 | 0 | 32891.156 | 1823.0993 | 450.6484 | 365.4735 | 621.118 | 484.5812 | 3744.9204 | 1167.9634 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | 3499.2005 | None | 100% | 0% | Column 9: In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions. Column 12: Column 12: Based on updated Transmission Engineering input Column 31: The TLRR Program received FRM Approval for all non-operational projects on 4/1/2021. Column 52: Source= PMWIF (v1 Proj Summary)
N/A | PB-22.24 | Lugo-Mira Loma No.3 TLRR Remediation (1) | 34.367, -117.369 / 34.010, -117.565 | Fontana/ Ontario/ Rialto/ Rancho Cucamonga, San Bernardino County & Eastvale/ Jurupa, Riverside County | Lugo-Mira Loma No.3 - 2 discrepancies - R/R 1 structure | Transmission Line (modification) | Modification/Upgrade | None | Other - See Notes | NERC Compliance - GO 95 | Inspections do not drive the need for TLRR projects. However, SCE performs annual patrols and triennial detailed inspections of its transmission circuits, which inspect the structures and lines on those circuits. The date of last inspection for this circuit was 7/31/2019 | 40-50 years | IEEE-738 is the standard for calculating the current-temperature relationship of bare overhead conductors. This analysis along with SCE's standard rating methodology was used in conjunction with the PLS-CADD model that was created from the LiDAR study to identify any potential clearance issues on the circuits. | Transmission line clearance discrepancies are remediated based on a series of criteria, including line sag when operating at or above 130 degrees Fahrenheit; potential risk to public safety; and system reliability risk based on the location of span, terrain, encroachment type, and extent of deviation from standards. Discrepancies may be remediated by a variety of construction activities, including, but not limited to Structure Replacements, Structure Raises, New Structure Insets, Line Reconductor, Line Re-tension, Hardware Replacements, Grading, Removing Encroachments, Undergrounding Line Segments, Rerouting Lines. | Tier 2, Tier 3 | See Note 16B | The asset’s service life can be affected by the following environmental factors; high corrosive soils, weather climates, airborne contamination, and pollution. | Demetric Brown, MPO - Programs | 0.5 | See Note 20B | 500kV | See Note 22A | See Note 23B | 901971822 | CET-PD-OT-PJ-729800 | 7298 | See Note 27A | Yes | 2016 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2017 = 991 2018 = 14 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | Not Available | No | 2016-12-31 | 2017-01-17 | N/A | 829 | 829 | See Note 53A | 1004.6511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1004.6511 | 0 | 0 | 0 | 0 | 1004.6511 | 67.6504 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | -2.583e-13 | None | 100% | 0% | Column 9: In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions. Column 52: Source= PMWIF (v3 Project Summary)
N/A | PB-22.25 | Mira Loma-Serrano No.1 TLRR Remediation | 34.010, -117.565 / 33.830, -117.790 | Orange/ Anaheim/ Yorba Linda, Orange County & Chino Hills/ Chino/ Ontario, San Bernardino County & Eastvale, Riverside County | Mira Loma-Serrano No.1 -2 discrepancies - R/R 1 structure - interset 1 structure | Transmission Line (modification) | Modification/Upgrade | None | Other - See Notes | NERC Compliance - GO 95 | Inspections do not drive the need for TLRR projects. However, SCE performs annual patrols and triennial detailed inspections of its transmission circuits, which inspect the structures and lines on those circuits. The date of last inspection for this circuit was 6/20/2019 | 30-40 years | IEEE-738 is the standard for calculating the current-temperature relationship of bare overhead conductors. This analysis along with SCE's standard rating methodology was used in conjunction with the PLS-CADD model that was created from the LiDAR study to identify any potential clearance issues on the circuits. | Transmission line clearance discrepancies are remediated based on a series of criteria, including line sag when operating at or above 130 degrees Fahrenheit; potential risk to public safety; and system reliability risk based on the location of span, terrain, encroachment type, and extent of deviation from standards. Discrepancies may be remediated by a variety of construction activities, including, but not limited to Structure Replacements, Structure Raises, New Structure Insets, Line Reconductor, Line Re-tension, Hardware Replacements, Grading, Removing Encroachments, Undergrounding Line Segments, Rerouting Lines. | Tier 2, Tier 3 | See Note 16B | The asset’s service life can be affected by the following environmental factors; high corrosive soils, weather climates, airborne contamination, and pollution. | Demetric Brown, MPO - Programs | 0.6 | See Note 20B | 500kV | See Note 22A | See Note 23B | 901971824 | CET-PD-OT-PJ-729800 | 7298 | See Note 27A | Yes | 2016 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2019 = 4,181 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2017-10-01 | No | 2017-12-31 | 2019-03-07 | Driven by budget Plan & OD Changes | 3068 | 3068 | See Note 53A | 4180.8748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2303.1373 | 1877.7375 | 0 | 0 | 0 | 4180.8748 | 669.8633 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | 9.9476e-13 | None | 100% | 0% | Column 9: In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions. Column 52: Source= PMWIF (v2 Project Summary)
N/A | PB-22.26 | Lugo-Vincent No.1 TLRR Remediation | 34.367, -117.369 / 34.486, -118.118 | Hesperia, San Bernardino | Lugo-Vincent No.1 - 4 discrepancies - R/R 4 structures | Transmission Line (modification) | Modification/Upgrade | None | Other - See Notes | NERC Compliance - GO 95 | Inspections do not drive the need for TLRR projects. However, SCE performs annual patrols and triennial detailed inspections of its transmission circuits, which inspect the structures and lines on those circuits. The date of last inspection for this circuit was 9/10/2019 | 50-60 years | IEEE-738 is the standard for calculating the current-temperature relationship of bare overhead conductors. This analysis along with SCE's standard rating methodology was used in conjunction with the PLS-CADD model that was created from the LiDAR study to identify any potential clearance issues on the circuits. | Transmission line clearance discrepancies are remediated based on a series of criteria, including line sag when operating at or above 130 degrees Fahrenheit; potential risk to public safety; and system reliability risk based on the location of span, terrain, encroachment type, and extent of deviation from standards. Discrepancies may be remediated by a variety of construction activities, including, but not limited to Structure Replacements, Structure Raises, New Structure Insets, Line Reconductor, Line Re-tension, Hardware Replacements, Grading, Removing Encroachments, Undergrounding Line Segments, Rerouting Lines. | Tier 2, Tier 3 | See Note 16B | The asset’s service life can be affected by the following environmental factors; high corrosive soils, weather climates, airborne contamination, and pollution. | Demetric Brown, MPO - Programs | 32 | See Note 20B | 500kV | See Note 22A | See Note 23B | 901971828 | CET-PD-OT-PJ-729800 | 7298 | See Note 27A | Yes | 2017 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2017 = 2,702 2018 = 56 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | Not Available | No | 2016-12-31 | 2016-12-19 | N/A | 3656 | 3656 | See Note 53A | 2757.9828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2757.9828 | 0 | 0 | 0 | 0 | 2757.9828 | 143.7453 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | 7.4579e-13 | None | 100% | 0% | Column 9: In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions. Column 52: Source= Unverified estimate, documents not readily available
N/A | PB-22.27 | Lugo-Rancho Vista TLRR Remediation | 34.367, -117.369 / 34.518, -117.216 | San Bernardino County, Fontana,Rancho Cucamonga | Lugo-Rancho Vista - 1 discrepancy - R/R 1 structure | Transmission Line (modification) | Modification/Upgrade | None | Other - See Notes | NERC Compliance - GO 95 | Inspections do not drive the need for TLRR projects. However, SCE performs annual patrols and triennial detailed inspections of its transmission circuits, which inspect the structures and lines on those circuits. The date of last inspection for this circuit was 9/2/2019 | 40-50 years | IEEE-738 is the standard for calculating the current-temperature relationship of bare overhead conductors. This analysis along with SCE's standard rating methodology was used in conjunction with the PLS-CADD model that was created from the LiDAR study to identify any potential clearance issues on the circuits. | Transmission line clearance discrepancies are remediated based on a series of criteria, including line sag when operating at or above 130 degrees Fahrenheit; potential risk to public safety; and system reliability risk based on the location of span, terrain, encroachment type, and extent of deviation from standards. Discrepancies may be remediated by a variety of construction activities, including, but not limited to Structure Replacements, Structure Raises, New Structure Insets, Line Reconductor, Line Re-tension, Hardware Replacements, Grading, Removing Encroachments, Undergrounding Line Segments, Rerouting Lines. | Tier 2, Tier 3 | See Note 16B | The asset’s service life can be affected by the following environmental factors; high corrosive soils, weather climates, airborne contamination, and pollution. | Demetric Brown, MPO - Programs | 0.5 | See Note 20B | 500kV | See Note 22A | See Note 23B | 901971829 | CET-PD-OT-PJ-729800 | 7298 | See Note 27A | Yes | 2016 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2017 = 1,496 2018 = 13 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2017-01-16 | No | 2017-12-31 | 2017-03-03 | Driven by budget Plan & OD Changes | 729 | 729 | See Note 53A | 1508.8838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1508.8838 | 0 | 0 | 0 | 0 | 1508.8838 | 109.3753 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | 2.6301e-13 | None | 100% | 0% | Column 9: In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions. Column 52: Source= PMWIF (v2 Project Summary)
N/A | PB-22.28 | Colorado River-Palo Verde TLRR Remediation | 33.589, -114.814 / 33.390, -112.862 | Ripley, Riverside County | Colorado River-Palo Verde - 9 discrepancies - interset 1 structure - 4 mile reconductor | Transmission Line (reconductor and modification) | Reconductor | None | Other - See Notes | NERC Compliance - GO 95 | Inspections do not drive the need for TLRR projects. However, SCE performs annual patrols and triennial detailed inspections of its transmission circuits, which inspect the structures and lines on those circuits. The date of last inspection for this circuit was 4/13/2019 | 30-40 years | IEEE-738 is the standard for calculating the current-temperature relationship of bare overhead conductors. This analysis along with SCE's standard rating methodology was used in conjunction with the PLS-CADD model that was created from the LiDAR study to identify any potential clearance issues on the circuits. | Transmission line clearance discrepancies are remediated based on a series of criteria, including line sag when operating at or above 130 degrees Fahrenheit; potential risk to public safety; and system reliability risk based on the location of span, terrain, encroachment type, and extent of deviation from standards. Discrepancies may be remediated by a variety of construction activities, including, but not limited to Structure Replacements, Structure Raises, New Structure Insets, Line Reconductor, Line Re-tension, Hardware Replacements, Grading, Removing Encroachments, Undergrounding Line Segments, Rerouting Lines. | Non-HFRA | See Note 16B | The asset’s service life can be affected by the following environmental factors; high corrosive soils, weather climates, airborne contamination, and pollution. | Demetric Brown, MPO - Programs | 4 | See Note 20B | 500kV | See Note 22A | See Note 23B | 901971831 | CET-PD-OT-PJ-729800 | 7298 | See Note 27A | Yes | 2016 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2016 = 1,552 2017 = 2,344 2018 = 81 | N/A | CatEx | BLM | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2016-10-24 | No | 2016-12-31 | 2016-11-26 | N/A | 1860 | 1860 | See Note 53A | 3977.4824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3977.4824 | 0 | 0 | 0 | 0 | 3977.4824 | 324.1602 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | -2.1173e-12 | None | 100% | 0% | Column 9: In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions. Column 52: Source= PMWIF (v2 Project Summary)
N/A | PB-22.29 | Big Creek 4-Springville TLRR Remediation | 37.139, -119.489 / 36.108, -118.938 | Squaw Valley/ Auberry, Fresno County & Madera County & Tulare County | Big Creek 4-Springville - 7 discrepancies - R/R 5 structures - interset 2 structures | Transmission Line (modification) | Modification/Upgrade | PB-22.11, PB-22.62, PB-22.64, PB-22.63, PB-22.40, PB-22.56, PB-22.58 | Other - See Notes | NERC Compliance - GO 95 | Inspections do not drive the need for TLRR projects. However, SCE performs annual patrols and triennial detailed inspections of its transmission circuits, which inspect the structures and lines on those circuits. The date of last inspection for this circuit was 3/21/2019 | 50-60 years | IEEE-738 is the standard for calculating the current-temperature relationship of bare overhead conductors. This analysis along with SCE's standard rating methodology was used in conjunction with the PLS-CADD model that was created from the LiDAR study to identify any potential clearance issues on the circuits. | Transmission line clearance discrepancies are remediated based on a series of criteria, including line sag when operating at or above 130 degrees Fahrenheit; potential risk to public safety; and system reliability risk based on the location of span, terrain, encroachment type, and extent of deviation from standards. Discrepancies may be remediated by a variety of construction activities, including, but not limited to Structure Replacements, Structure Raises, New Structure Insets, Line Reconductor, Line Re-tension, Hardware Replacements, Grading, Removing Encroachments, Undergrounding Line Segments, Rerouting Lines. | Tier 2, Tier 3 | See Note 16B | The asset’s service life can be affected by the following environmental factors; high corrosive soils, weather climates, airborne contamination, and pollution. | Demetric Brown, MPO - Programs | 67 | See Note 20B | 220kV | See Note 22A | See Note 23B | 901978106 | CET-PD-OT-PJ-729800 | 7298 | See Note 27A | Yes | 2016 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2018 = 4,220 2019 = 166 2020 = -107 2021 = 15 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2018-08-22 | No | 2018-12-31 | 2018-09-11 | N/A | 6907 | 6907 | See Note 53A | 4293.561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4220.35 | 165.7551 | -107.4549 | 14.9108 | 0 | 4293.561 | 556.0797 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | -4.4827e-12 | None | 100% | 0% | Column 9: In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions. Column 52: Source= PMWIF (v1 Project Summary)
N/A | PB-22.30 | Magunden-Pastoria No.3 TLRR Remediation | 35.361, -118.922 / 34.935, -118.843 | Weedpatch/ Lamont, Kern County | Magunden-Pastoria No.3 - 11 discrepancies - raise 10 structures | Transmission Line (modification) | Modification/Upgrade | None | Other - See Notes | NERC Compliance - GO 95 | Inspections do not drive the need for TLRR projects. However, SCE performs annual patrols and triennial detailed inspections of its transmission circuits, which inspect the structures and lines on those circuits. The date of last inspection for this circuit was 5/1/2019 | 50-60 years | IEEE-738 is the standard for calculating the current-temperature relationship of bare overhead conductors. This analysis along with SCE's standard rating methodology was used in conjunction with the PLS-CADD model that was created from the LiDAR study to identify any potential clearance issues on the circuits. | Transmission line clearance discrepancies are remediated based on a series of criteria, including line sag when operating at or above 130 degrees Fahrenheit; potential risk to public safety; and system reliability risk based on the location of span, terrain, encroachment type, and extent of deviation from standards. Discrepancies may be remediated by a variety of construction activities, including, but not limited to Structure Replacements, Structure Raises, New Structure Insets, Line Reconductor, Line Re-tension, Hardware Replacements, Grading, Removing Encroachments, Undergrounding Line Segments, Rerouting Lines. | Non-HFRA | See Note 16B | The asset’s service life can be affected by the following environmental factors; high corrosive soils, weather climates, airborne contamination, and pollution. | Demetric Brown, MPO - Programs | 26 | See Note 20B | 220kV | See Note 22A | See Note 23B | 901978206 | CET-PD-OT-PJ-729800 | 7298 | See Note 27A | Yes | 2016 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2018 = 3,009 2019 = 22 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2018-03-29 | No | 2018-12-31 | 2018-09-10 | N/A | 2955 | 2955 | See Note 53A | 3030.9219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3009.3931 | 21.5288 | 0 | 0 | 0 | 3030.9219 | 263.1909 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | 3.5612e-14 | None | 100% | 0% | Column 9: In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions. Column 52: Source= PMWIF (v1 Project Summary)
N/A | PB-22.31 | Pardee-Pastoria TLRR Remediation in North Coast Grid | 34.440, -118.582 / 34.935, -118.843 | Santa Clarita, Los Angeles County & Kern County | Pardee-Pastoria 220kV - TLRR WO 901982969 (NC) This WO has 63 discrepancies to be remediated. Scope – ~27 mile reconductor and 10 AmpJack structure raises FLOC #s ET-00667-04601 Discrepancy #s as shown: 4602055, 4602056, 4602057, 4602059, 4602060, 4602061, 4602062, 4602063, 4602065, 4602068, 4602069, 4602070, 4602071, 4602072, 4602073, 4602074, 4602075, 4602077, 4602078, 4602079, 4602080, 4602081, 4602082, 4602084, 4602085, 4602087, 4602088, 4602089, 4602090, 4602091, 4602093, 4602094, 4602095, 4602096, 4602097, 4602098, 4602100, 4602101, 4602103, 4602104, 4602105, 4602106, 4602107, 4602108, 4602109, 4602110, 4602111, 4602112, 4602113, 4602115, 4602116, 4602117, 4602118, 4602119, 4602120, 4602121, 4602122, 4602123, 4602124, 4602125, 4602126, 4602127, 4602130. | Transmission Line (reconductor and modification) | Reconductor | PB-22.47, PB-22.23, PB-22.32, PB-22.53 | Other - See Notes | NERC Compliance - GO 95 | Inspections do not drive the need for TLRR projects. However, SCE performs annual patrols and triennial detailed inspections of its transmission circuits, which inspect the structures and lines on those circuits. The date of last inspection for this circuit was 9/9/2019 | 100-110 years | IEEE-738 is the standard for calculating the current-temperature relationship of bare overhead conductors. This analysis along with SCE's standard rating methodology was used in conjunction with the PLS-CADD model that was created from the LiDAR study to identify any potential clearance issues on the circuits. | Transmission line clearance discrepancies are remediated based on a series of criteria, including line sag when operating at or above 130 degrees Fahrenheit; potential risk to public safety; and system reliability risk based on the location of span, terrain, encroachment type, and extent of deviation from standards. Discrepancies may be remediated by a variety of construction activities, including, but not limited to Structure Replacements, Structure Raises, New Structure Insets, Line Reconductor, Line Re-tension, Hardware Replacements, Grading, Removing Encroachments, Undergrounding Line Segments, Rerouting Lines. | Tier 2, Tier 3 | See Note 16B | The asset’s service life can be affected by the following environmental factors; high corrosive soils, weather climates, airborne contamination, and pollution. | Demetric Brown, MPO - Programs | 26 | See Note 20B | 220kV | See Note 22A | See Note 23B | 901982969 | CET-PD-OT-PJ-729800 | 7298 | See Note 27A | Yes | 2016 | Pre-2017 | FRM/CRT | No | N/A | N/A | N/A | See Col. 37 | 2022 = 43,789 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2019-06-04 | Yes | 2019-12-31 | 2022-05-04 | Driven by Budget Plan & OD Changes | 29064 | 29064 | See Note 53A | 43788.6076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1384.7921 | 6764.3893 | 3399.4168 | 12418.1658 | 19821.8437 | 43788.6076 | 4720.3781 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | 3.8356e-11 | None | 100% | 0% | Column 1: Formerly named Pardee-Pastoria TLRR Remediation (1) in July 1, 2021 SRP Column 9: In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions. Process for Utility Approval: The TLRR Program received FRM Approval for all non-operational projects on 4/1/2021. Column 52: Source= PMWIF (v1 Proj Summary)
N/A | PB-22.32 | Bailey-Pastoria TLRR Remediation | 34.777, -118.774 / 34.935, -118.843 | Los Angeles County & Kern County | Bailey-Pastoria - 32 discrepancies - raise 12 structures - 12 mile reconductor - reframe 4 structures - replace OHGW | Transmission Line (reconductor and modification) | Reconductor | PB-22.23, PB-22.31, PB-22.47, PB-22.53 | Other - See Notes | NERC Compliance - GO 95 | Inspections do not drive the need for TLRR projects. However, SCE performs annual patrols and triennial detailed inspections of its transmission circuits, which inspect the structures and lines on those circuits. The date of last inspection for this circuit was 8/26/2019 | 80-90 years | IEEE-738 is the standard for calculating the current-temperature relationship of bare overhead conductors. This analysis along with SCE's standard rating methodology was used in conjunction with the PLS-CADD model that was created from the LiDAR study to identify any potential clearance issues on the circuits. | Transmission line clearance discrepancies are remediated based on a series of criteria, including line sag when operating at or above 130 degrees Fahrenheit; potential risk to public safety; and system reliability risk based on the location of span, terrain, encroachment type, and extent of deviation from standards. Discrepancies may be remediated by a variety of construction activities, including, but not limited to Structure Replacements, Structure Raises, New Structure Insets, Line Reconductor, Line Re-tension, Hardware Replacements, Grading, Removing Encroachments, Undergrounding Line Segments, Rerouting Lines. | Tier 2 | See Note 16B | The asset’s service life can be affected by the following environmental factors; high corrosive soils, weather climates, airborne contamination, and pollution. | Demetric Brown, MPO - Programs | 12 | See Note 20B | 220kV | See Note 22A | See Note 23B | 901983101 | CET-PD-OT-PJ-729800 | 7298 | See Note 27A | Yes | 2016 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2019 = 16,947 2020 = 16 2021 = 4 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2018-10-24 | No | 2018-12-31 | 2019-09-11 | Driven by Budget Plan & OD Changes | 7550 | 7550 | See Note 53A | 16966.3459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8458.3171 | 8488.2939 | 15.7502 | 3.9848 | 0 | 16966.3459 | 1724.7419 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | -1.7444e-11 | None | 100% | 0% | Column 9: In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions. Column 52: Source= Unverified estimate, documents not readily available; Estimate based on cost pers
N/A | PB-22.33 | Midway-Vincent No.1 TLRR Remediation | 35.404, -119.450 / 34.486, -118.118 | Buttonwillow, Kern County & Palmdale, Los Angeles County & Ventura County | Midway-Vincent No. 1 500kV-TLRR WO 901986930 This WO has 10 discrepancies to be remediated. Scope - 10 AmpJack structure raises, 1 interset structure FLOC #s ET-00126-04726 and ET-00126-04626 Discrepancy #s as shown: 4600242, 4600243, 4600244, 4600253, 4600255, 4600256, 4600257, 4600258, 4600259, and 4600260. | Transmission Line (modification) | Modification/Upgrade | None | Other - See Notes | NERC Compliance - GO 95 | Inspections do not drive the need for TLRR projects. However, SCE performs annual patrols and triennial detailed inspections of its transmission circuits, which inspect the structures and lines on those circuits. The date of last inspection for this circuit was 11/15/2019 | 40-50 years | IEEE-738 is the standard for calculating the current-temperature relationship of bare overhead conductors. This analysis along with SCE's standard rating methodology was used in conjunction with the PLS-CADD model that was created from the LiDAR study to identify any potential clearance issues on the circuits. | Transmission line clearance discrepancies are remediated based on a series of criteria, including line sag when operating at or above 130 degrees Fahrenheit; potential risk to public safety; and system reliability risk based on the location of span, terrain, encroachment type, and extent of deviation from standards. Discrepancies may be remediated by a variety of construction activities, including, but not limited to Structure Replacements, Structure Raises, New Structure Insets, Line Reconductor, Line Re-tension, Hardware Replacements, Grading, Removing Encroachments, Undergrounding Line Segments, Rerouting Lines. | Tier 2, Tier 3 | See Note 16B | The asset’s service life can be affected by the following environmental factors; high corrosive soils, weather climates, airborne contamination, and pollution. | Demetric Brown, MPO - Programs | 36 | See Note 20B | 500kV | See Note 22A | See Note 23B | 901986930 | CET-PD-OT-PJ-729800 | 7298 | See Note 27A | Yes | 2016 | Pre-2017 | FRM/CRT | No | N/A | N/A | N/A | See Col. 37 | 2021 = 11,237 2022 = 1 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2018-10-22 | No | 2018-12-31 | 2021-05-10 | Driven by Budget Plan & OD Changes | 2901 | 2901 | See Note 53A | 11238.3247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1907.701 | 3982.3236 | 694.625 | 4652.7198 | 0.95534 | 11238.3247 | 1574.3529 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | -1.0374e-11 | None | 100% | 0% | Column 9: In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions. Process for Utility Approval: The TLRR Program received FRM Approval for all non-operational projects on 4/1/2021. Column 52: Source= PMWIF (v1 Proj Summary)
N/A | PB-22.34 | Lugo-Mira Loma No.3 TLRR Remediation (1) | 34.367, -117.369 / 34.010, -117.565 | Fontana/ Ontario/ Rialto/ Rancho Cucamonga, San Bernardino County & Eastvale/ Jurupa Valley, Riverside County | Lugo-Mira Loma No. 3 500kV - TLRR WO 901987196 This WO has 7 discrepancies to be remediated. Scope – 6 AmpJack structure raises, install marker balls, FAA lighting FLOC #s ET-00129 Discrepancy #s as shown: 4500154, 4500155, 4500166, 4500167, 4500174, 4500182 and 4500141 (L-ML2 DC w/ 4500174). | Transmission Line (modification) | Modification/Upgrade | None | Other - See Notes | NERC Compliance - GO 95 | Inspections do not drive the need for TLRR projects. However, SCE performs annual patrols and triennial detailed inspections of its transmission circuits, which inspect the structures and lines on those circuits. The date of last inspection for this circuit was 7/31/2019 | 40-50 years | IEEE-738 is the standard for calculating the current-temperature relationship of bare overhead conductors. This analysis along with SCE's standard rating methodology was used in conjunction with the PLS-CADD model that was created from the LiDAR study to identify any potential clearance issues on the circuits. | Transmission line clearance discrepancies are remediated based on a series of criteria, including line sag when operating at or above 130 degrees Fahrenheit; potential risk to public safety; and system reliability risk based on the location of span, terrain, encroachment type, and extent of deviation from standards. Discrepancies may be remediated by a variety of construction activities, including, but not limited to Structure Replacements, Structure Raises, New Structure Insets, Line Reconductor, Line Re-tension, Hardware Replacements, Grading, Removing Encroachments, Undergrounding Line Segments, Rerouting Lines. | Tier 2, Tier 3 | See Note 16B | The asset’s service life can be affected by the following environmental factors; high corrosive soils, weather climates, airborne contamination, and pollution. | Demetric Brown, MPO - Programs | 24 | See Note 20B | 500kV | See Note 22A | See Note 23B | 901987196 | CET-PD-OT-PJ-729800 | 7298 | See Note 27A | Yes | 2016 | Pre-2017 | FRM/CRT | No | N/A | N/A | N/A | See Col. 37 | 2022 = 4,451 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2018-09-18 | Yes | 2018-12-31 | 2022-01-27 | Driven by budget plan and resource leveling | 6372 | 6372 | See Note 53A | 4450.892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2367.2279 | 175.9013 | 223.9151 | 457.3009 | 1226.5468 | 4450.892 | 971.7499 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | 7.1891e-12 | None | 100% | 0% | Column 9: In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions. Process for Utility Approval: The TLRR Program received FRM Approval for all non-operational projects on 4/1/2021. General: This project is in a group of projects that are in the middle of the change management process to align schedules based on resource and outage availability. Costs forecasts have been updated for planning purposes, and schedule dates (including in-service dates) will be updated once the change management process is complete. Column 52: Source= PMWIF (v2 Proj Summary)
N/A | PB-22.35 | El Nido-La Cienega TLRR Remediation | 33.895, -118.372 / 34.001, -118.379 | Bel Aire/ Inglewood/ Ladera Heights/ Lennox/ Hawthorne/ Los Angeles, Los Angeles County | El Nido-La Cienega - 1 discrepancy - R/R 1 structure | Transmission Line (modification) | Replacement | None | Other - See Notes | NERC Compliance - GO 95 | Inspections do not drive the need for TLRR projects. However, SCE performs annual patrols and triennial detailed inspections of its transmission circuits, which inspect the structures and lines on those circuits. The date of last inspection for this circuit was 12/2/2019 | 40-50 years | IEEE-738 is the standard for calculating the current-temperature relationship of bare overhead conductors. This analysis along with SCE's standard rating methodology was used in conjunction with the PLS-CADD model that was created from the LiDAR study to identify any potential clearance issues on the circuits. | Transmission line clearance discrepancies are remediated based on a series of criteria, including line sag when operating at or above 130 degrees Fahrenheit; potential risk to public safety; and system reliability risk based on the location of span, terrain, encroachment type, and extent of deviation from standards. Discrepancies may be remediated by a variety of construction activities, including, but not limited to Structure Replacements, Structure Raises, New Structure Insets, Line Reconductor, Line Re-tension, Hardware Replacements, Grading, Removing Encroachments, Undergrounding Line Segments, Rerouting Lines. | Tier 2 | See Note 16B | The asset’s service life can be affected by the following environmental factors; high corrosive soils, weather climates, airborne contamination, and pollution. | Demetric Brown, MPO - Programs | 0.1 | See Note 20B | 220kV | See Note 22A | See Note 23B | 902067765 | CET-PD-OT-PJ-729800 | 7298 | See Note 27A | Yes | 2017 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2019 = 1,872 2020 = 19 2021 = -233 2022 = -211 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2019-11-05 | No | 2018-12-31 | 2019-11-15 | Driven by Budget Plan & OD Changes | 702 | 702 | See Note 53A | 1446.7887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1423.6838 | 448.4933 | 18.9941 | -233.2284 | -211.154 | 1446.7887 | 464.1562 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | -1.6098e-12 | None | 100% | 0% | Column 9: In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions. Column 52: Source= PMWIF (v1 Project Summary)
N/A | PB-22.36 | Moorpark-Pardee No.1 TLRR Remediation | 34.281, -118.903 / 34.440, -118.582 | Moorpark, Ventura & Santa Clarita, Los Angeles County | Moorpark-Pardee No.1 - 1 discrepancy - R/R 1 structure | Transmission Line (modification) | Replacement | None | Other - See Notes | NERC Compliance - GO 95 | Inspections do not drive the need for TLRR projects. However, SCE performs annual patrols and triennial detailed inspections of its transmission circuits, which inspect the structures and lines on those circuits. The date of last inspection for this circuit was 8/31/2019 | 40-50 years | IEEE-738 is the standard for calculating the current-temperature relationship of bare overhead conductors. This analysis along with SCE's standard rating methodology was used in conjunction with the PLS-CADD model that was created from the LiDAR study to identify any potential clearance issues on the circuits. | Transmission line clearance discrepancies are remediated based on a series of criteria, including line sag when operating at or above 130 degrees Fahrenheit; potential risk to public safety; and system reliability risk based on the location of span, terrain, encroachment type, and extent of deviation from standards. Discrepancies may be remediated by a variety of construction activities, including, but not limited to Structure Replacements, Structure Raises, New Structure Insets, Line Reconductor, Line Re-tension, Hardware Replacements, Grading, Removing Encroachments, Undergrounding Line Segments, Rerouting Lines. | Tier 3 | See Note 16B | The asset’s service life can be affected by the following environmental factors; high corrosive soils, weather climates, airborne contamination, and pollution. | Demetric Brown, MPO - Programs | 0.6 | See Note 20B | 220kV | See Note 22A | See Note 23B | 902067766 | CET-PD-OT-PJ-729800 | 7298 | See Note 27A | Yes | 2017 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2018 = 1,212 2019 = 37 2020 = 27 2021 = 330 2022 = -14 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2018-10-15 | No | 2018-12-31 | 2018-12-17 | N/A | 500 | 500 | See Note 53A | 1591.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1212.1306 | 37.4198 | 26.5152 | 330.2223 | -14.4351 | 1591.8528 | 225.0897 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | 6.0908e-13 | None | 100% | 0% | Column 9: In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions. Column 52: Source= PMWIF (v1 Project Summary)
0: N/A; Project Description 1: PB-22.37; Project Description 2: Moorpark-Santa Clara No.1 TLRR Remediation; Project Description 4: Moorpark, Ventura & Santa Clarita, Los Angeles County; Project Description 5: Moorpark-Santa Clara No.1 - 3 discrepancies - raise 3 structures; Project Description 6: Transmission Line (modification); Project Description 7: Modification/Upgrade; Project Description (Cont.) 24: 902067767; Project Description (Cont.) 25: CET-PD-OT-PJ-729800; Project Description (Cont.) 26: 7298; Project Status 45: Operational; Project Status 50: 2018-08-28; Costs 52: 900; Costs 52.1: 900; Costs 54: 790.5798 | [16 empty] | Column 9: In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions. Column 52: Source= PMWIF (v1 Project Summary)
N/A | PB-22.38 | Rector-Springville TLRR Remediation | 36.304, -119.244 / 36.108, -118.938 | Tulare County, Visalia | Rector-Springville 220 kV - TLRR WO 902067769 This WO has 10 discrepancies to be remediated. Scope – 10 AmpJack structure raises. FLOC #s ET-01073 Discrepancy #s as shown: 4200988, 4200990, 4200992, 4200996, 4200997, 4200998, 4200999, 4201000, 4201003, 4201004. | Transmission Line (modification) | Modification/Upgrade | None | Other - See Notes | NERC Compliance - GO 95 | Inspections do not drive the need for TLRR projects. However, SCE performs annual patrols and triennial detailed inspections of its transmission circuits, which inspect the structures and lines on those circuits. The date of last inspection for this circuit was 3/21/2019 | 80-90 years | IEEE-738 is the standard for calculating the current-temperature relationship of bare overhead conductors. This analysis along with SCE's standard rating methodology was used in conjunction with the PLS-CADD model that was created from the LiDAR study to identify any potential clearance issues on the circuits. | Transmission line clearance discrepancies are remediated based on a series of criteria, including line sag when operating at or above 130 degrees Fahrenheit; potential risk to public safety; and system reliability risk based on the location of span, terrain, encroachment type, and extent of deviation from standards. Discrepancies may be remediated by a variety of construction activities, including, but not limited to Structure Replacements, Structure Raises, New Structure Insets, Line Reconductor, Line Re-tension, Hardware Replacements, Grading, Removing Encroachments, Undergrounding Line Segments, Rerouting Lines. | Tier 2 | See Note 16B | The asset’s service life can be affected by the following environmental factors; high corrosive soils, weather climates, airborne contamination, and pollution. | Demetric Brown, MPO - Programs | 21 | See Note 20B | 220kV | See Note 22A | See Note 23B | 902067769 | CET-PD-OT-PJ-729800 | 7298 | See Note 27A | Yes | 2017 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2020 = 4,152 2021 = -237 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2018-03-15 | No | 2018-12-31 | 2020-07-02 | Driven by Budget Plan & OD Changes | 5356 | 5356 | See Note 53A | 3914.9851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1780.2115 | 1611.1725 | 760.736 | -237.1349 | 0 | 3914.9851 | 606.2082 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | -1.9952e-12 | None | 100% | 0% | Column 9: In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions. Column 52: Source= PMWIF (v0 Proj Summary); SCE provided in its Dec 2020 SRP a cost of $3.618M which was pulled from the system using a code which has subsequently corrected. Consistent with the methodology for the July SRP, SCE provides the original project cost from the PMWIF (v0 Proj Summary)
N/A | PB-22.39 | Serrano-Valley TLRR Remediation | 33.830, -117.790 / 33.740, -117.157 | Orange/ Lake Elsinore/ Menifee/ Perris/ Meadowbrook, Riverside County | Serrano-Valley 500 kV - TLRR WO 902067771 This WO has 7 discrepancies to be remediated. Scope – 1 structure replacement, ~4-mile retention. FLOC #s ET-00132-04988 (SJ) Discrepancy #s as shown: 4900328, 4900332, 4900333, 4900334, 4900343, 4900344, 4900345. | Transmission Line (modification) | Modification/Upgrade | None | Other - See Notes | NERC Compliance - GO 95 | Inspections do not drive the need for TLRR projects. However, SCE performs annual patrols and triennial detailed inspections of its transmission circuits, which inspect the structures and lines on those circuits. The date of last inspection for this circuit was 8/14/2019 | 30-40 years | IEEE-738 is the standard for calculating the current-temperature relationship of bare overhead conductors. This analysis along with SCE's standard rating methodology was used in conjunction with the PLS-CADD model that was created from the LiDAR study to identify any potential clearance issues on the circuits. | Transmission line clearance discrepancies are remediated based on a series of criteria, including line sag when operating at or above 130 degrees Fahrenheit; potential risk to public safety; and system reliability risk based on the location of span, terrain, encroachment type, and extent of deviation from standards. Discrepancies may be remediated by a variety of construction activities, including, but not limited to Structure Replacements, Structure Raises, New Structure Insets, Line Reconductor, Line Re-tension, Hardware Replacements, Grading, Removing Encroachments, Undergrounding Line Segments, Rerouting Lines. | Non-CPUC HFRA, Tier 2, Tier 3 | See Note 16B | The asset’s service life can be affected by the following environmental factors; high corrosive soils, weather climates, airborne contamination, and pollution. | Demetric Brown, MPO - Programs | 0.6 | See Note 20B | 500kV | See Note 22A | See Note 23B | 902067771 | CET-PD-OT-PJ-729800 | 7298 | See Note 27A | Yes | 2017 | Pre-2017 | FRM/CRT | No | N/A | N/A | N/A | See Col. 37 | 2023 = 4,243 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2018-03-26 | Yes | 2018-12-31 | 2023-03-27 | Driven by Budget Plan & OD Changes | 5469 | 5469 | See Note 53A | 4242.8483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1448.4561 | 116.6882 | -56.7431 | 1736.6059 | 997.8411 | 4242.8483 | 495.3253 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | 3726.6088 | None | 100% | 0% | Column 9: In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions. Process for Utility Approval: The TLRR Program received FRM Approval for all non-operational projects on 4/1/2021. Column 52: Source= PMWIF (v1 Proj Summary); SCE provided in its Dec 2020 SRP a cost of $2.007M which was pulled from the system using a code which has subsequently corrected. Consistent with the methodology for the July SRP, SCE provides the original project cost from the PMWIF (v1 Proj Summary)
N/A | PB-22.40 | Big Creek 3-Rector No.1 TLRR Remediation | 37.148, -119.389 / 36.304, -119.244 | Orange Cove, Fresno County & Visalia, Tulare County | Big Creek 3-Rector No. 1 220 kV - TLRR WO 902138163 This WO has 114 discrepancy to be remediated. Scope – ~53 mile reconductor, 45 AmpJack structure raises, hardware modifications. FLOC #s ET-00513 Discrepancy #s as shown: 4200831, 4200832, 4200833, 4200834, 4200835, 4200837, 4200838, 4200839, 4200840, 4200841, 4200842, 4200843, 4200845, 4200846, 4200847, 4200848, 4200849, 4200850, 4200851, 4200852, 4200853, 4200854, 4200855, 4200856, 4200857, 4200858, 4200860, 4200861, 4200862, 4200863, 4200864, 4200865, 4200866, 4200867, 4200868, 4200869, 4200870, 4200871, 4200872, 4200873, 4200874, 4200875, 4200876, 4200877, 4200878, 4200879, 4200880, 4200881, 4200882, 4200883, 4200884, 4200886, 4200887, 4200889, 4200890, 4200892, 4200894, 4200895, 4200896, 4200897, 4200898, 4200899, 4200900, 4200901, 4200903, 4200904, 4200905, 4200906, 4200907, 4200908, 4200910, 4200911, 4200912, 4200913, 4200914, 4200915, 4200918, 4200919, 4200920, 4200921, 4200922, 4200923, 4200924, 4200925, 4200926, 4200927, 4200929, 4200931, 4200933, 4200934, 4200935, 4200936, 4200937, 4200938, 4200939, 4200940, 4200941, 4200942, 4200943, 4200945, 4200946, 4200948, 4200949, 4200950, 4200951, 4200952, 4200953, 4200954, 4200955, 4200956, 4200957, 4200958, 4200959, 4200985. | Transmission Line (reconductor and modification) | Reconductor | PB-22.11, PB-22.62, PB-22.64, PB-22.63, PB-22.56, PB-22.29, PB-22.58 | Other - See Notes | NERC Compliance - GO 95 | Inspections do not drive the need for TLRR projects. However, SCE performs annual patrols and triennial detailed inspections of its transmission circuits, which inspect the structures and lines on those circuits. The date of last inspection for this circuit was 7/23/2019 | 80-90 years | IEEE-738 is the standard for calculating the current-temperature relationship of bare overhead conductors. This analysis along with SCE's standard rating methodology was used in conjunction with the PLS-CADD model that was created from the LiDAR study to identify any potential clearance issues on the circuits. | Transmission line clearance discrepancies are remediated based on a series of criteria, including line sag when operating at or above 130 degrees Fahrenheit; potential risk to public safety; and system reliability risk based on the location of span, terrain, encroachment type, and extent of deviation from standards. Discrepancies may be remediated by a variety of construction activities, including, but not limited to Structure Replacements, Structure Raises, New Structure Insets, Line Reconductor, Line Re-tension, Hardware Replacements, Grading, Removing Encroachments, Undergrounding Line Segments, Rerouting Lines. | Zone 1, Tier 2, Tier 3 | See Note 16B | The asset’s service life can be affected by the following environmental factors; high corrosive soils, weather climates, airborne contamination, and pollution. | Demetric Brown, MPO - Programs | 53 | See Note 20B | 220kV | See Note 22A | See Note 23B | 902138163 | CET-PD-OT-PJ-729800 | 7298 | See Note 27A | Yes | 2016 | 2017 | FRM/CRT | No | N/A | N/A | N/A | See Col. 37 | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Construction less than 50% completed | See Note 46A | 2022-07-11 | No | 2021-12-31 | 2027-12-31 | Driven by Budget Plan & OD Changes | 38132 | 38132 | See Note 53A | 84170.7249 | 9826.32 | 11438.072 | 18314.103 | 17798.604 | 4356.755 | 0 | 61733.854 | 1546.5662 | 752.5056 | 264.6093 | 518.6969 | 19354.493 | 22436.8709 | 2469.8579 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | 20238.8062 | None | 100% | 0% | Column 9: In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions. Process for Utility Approval: The TLRR Program received FRM Approval for all non-operational projects on 4/1/2021. General: This project is in a group of projects that are in the middle of the change management process to align schedules based on resource and outage availability. Costs forecasts have been updated for planning purposes, and schedule dates (including in-service dates) will be updated once the change management process is complete. Column 52: Source= PMWIF (v3 Proj Summary); SCE provided in its Dec 2020 SRP a cost of $31.574M which was pulled from the system using a code which has subsequently corrected. Consistent with the methodology for the July SRP, SCE provides the original project cost from the PMWIF (v3 Proj Summary)
N/A | PB-22.41 | Lugo-Victor No.2 TLRR Remediation | 34.367, -117.369 / 34.506, -117.387 | Hesperia/ Victorville, San Bernardino | Lugo-Victor No.2 - 7 discrepancies - raise 4 structures | Transmission Line (modification) | Modification/Upgrade | None | Other - See Notes | NERC Compliance - GO 95 | Inspections do not drive the need for TLRR projects. However, SCE performs annual patrols and triennial detailed inspections of its transmission circuits, which inspect the structures and lines on those circuits. The date of last inspection for this circuit was 8/28/2019 | 40-50 years | IEEE-738 is the standard for calculating the current-temperature relationship of bare overhead conductors. This analysis along with SCE's standard rating methodology was used in conjunction with the PLS-CADD model that was created from the LiDAR study to identify any potential clearance issues on the circuits. | Transmission line clearance discrepancies are remediated based on a series of criteria, including line sag when operating at or above 130 degrees Fahrenheit; potential risk to public safety; and system reliability risk based on the location of span, terrain, encroachment type, and extent of deviation from standards. Discrepancies may be remediated by a variety of construction activities, including, but not limited to Structure Replacements, Structure Raises, New Structure Insets, Line Reconductor, Line Re-tension, Hardware Replacements, Grading, Removing Encroachments, Undergrounding Line Segments, Rerouting Lines. | Tier 2 | See Note 16B | The asset’s service life can be affected by the following environmental factors; high corrosive soils, weather climates, airborne contamination, and pollution. | Demetric Brown, MPO - Programs | 6 | See Note 20B | 220kV | See Note 22A | See Note 23B | 902239303 | CET-PD-OT-PJ-729800 | 7298 | See Note 27A | Yes | 2017 | 2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2018 = 1,027 2019 = 26 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2018-06-08 | No | 2018-12-31 | 2018-06-19 | Driven by Budget Plan & OD Changes | 960 | 960 | See Note 53A | 1052.4428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1026.8988 | 25.544 | 0 | 0 | 0 | 1052.4428 | 76.337 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | -4.2679e-13 | None | 100% | 0% | Column 9: In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions. Column 52: Source= PMWIF (v1 Project Summary)
N/A | PB-22.42 | Lugo-Vincent No.2 TLRR Remediation | 34.367, -117.369 / 34.486, -118.118 | Hesperia, San Bernardino | Lugo-Vincent No. 2 - 2 discrepancies - raise 2 structures | Transmission Line (modification) | Modification/Upgrade | None | Other - See Notes | NERC Compliance - GO 95 | Inspections do not drive the need for TLRR projects. However, SCE performs annual patrols and triennial detailed inspections of its transmission circuits, which inspect the structures and lines on those circuits. The date of last inspection for this circuit was 8/28/2019 | 50-60 years | IEEE-738 is the standard for calculating the current-temperature relationship of bare overhead conductors. This analysis along with SCE's standard rating methodology was used in conjunction with the PLS-CADD model that was created from the LiDAR study to identify any potential clearance issues on the circuits. | Transmission line clearance discrepancies are remediated based on a series of criteria, including line sag when operating at or above 130 degrees Fahrenheit; potential risk to public safety; and system reliability risk based on the location of span, terrain, encroachment type, and extent of deviation from standards. Discrepancies may be remediated by a variety of construction activities, including, but not limited to Structure Replacements, Structure Raises, New Structure Insets, Line Reconductor, Line Re-tension, Hardware Replacements, Grading, Removing Encroachments, Undergrounding Line Segments, Rerouting Lines. | Tier 2, Tier 3 | See Note 16B | The asset’s service life can be affected by the following environmental factors; high corrosive soils, weather climates, airborne contamination, and pollution. | Demetric Brown, MPO - Programs | 3 | See Note 20B | 500kV | See Note 22A | See Note 23B | 902301449 | CET-PD-OT-PJ-729800 | 7298 | See Note 27A | Yes | 2017 | 2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2018 = 1,018 2020 = 2 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2018-06-18 | No | 2019-12-31 | 2018-07-18 | Driven by Budget Plan & OD Changes | 1000 | 1000 | See Note 53A | 1020.0531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1018.2701 | 0 | 1.7831 | 0 | 0 | 1020.0531 | 52.0357 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | 3.763e-14 | None | 100% | 0% | Column 9: In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions. Column 52: Source= PMWIF (v1 Project Summary)
N/A | PB-22.43 | Eagle Rock-Pardee TLRR Remediation (1) | 34.149, -118.184 / 34.440, -118.582 | Los Angeles (Based on Substation locations) | Eagle Rock-Pardee - 3 discrepancies - remove 4 structures, replace with 2 - 4 span reconductor | Transmission Line (reconductor and modification) | Reconductor | None | Other - See Notes | NERC Compliance - GO 95 | Inspections do not drive the need for TLRR projects. However, SCE performs annual patrols and triennial detailed inspections of its transmission circuits, which inspect the structures and lines on those circuits. The date of last inspection for this circuit was 3/31/2015 | 40-50 years | IEEE-738 is the standard for calculating the current-temperature relationship of bare overhead conductors. This analysis along with SCE's standard rating methodology was used in conjunction with the PLS-CADD model that was created from the LiDAR study to identify any potential clearance issues on the circuits. | Transmission line clearance discrepancies are remediated based on a series of criteria, including line sag when operating at or above 130 degrees Fahrenheit; potential risk to public safety; and system reliability risk based on the location of span, terrain, encroachment type, and extent of deviation from standards. Discrepancies may be remediated by a variety of construction activities, including, but not limited to Structure Replacements, Structure Raises, New Structure Insets, Line Reconductor, Line Re-tension, Hardware Replacements, Grading, Removing Encroachments, Undergrounding Line Segments, Rerouting Lines. | Tier 3 | See Note 16B | The asset’s service life can be affected by the following environmental factors; high corrosive soils, weather climates, airborne contamination, and pollution. | Demetric Brown, MPO - Programs | 1 | See Note 20B | 220kV | See Note 22A | See Note 23B | TD595732 | CET-PD-OT-PJ-729800 | 7298 | See Note 27A | Yes | 2013 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2014 = 3,544 2015 = 634 2016 = -208 2017 = 8 2019 = 105 2021 = -10 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | Not Available | No | Not readily available | 2014-12-10 | N/A | 1788 | 1788 | See Note 53A | 4072.8817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3978.4451 | 104.5422 | 0 | -10.1056 | 0 | 4072.8817 | 444.3721 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | 2.3283e-12 | None | 100% | 0% | Column 9: In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions. Column 52: Source= E3/ Design Manager Estimate; Project predates PMWIF process, so estimate represents initial cost from Design Manager program
N/A | PB-22.44 | Big Creek 1-Rector TLRR Remediation (1) | 37.204, -119.240 / 36.304, -119.244 | Orange Cove, Fresno County & Visalia, Tulare County | Big Creek 1-Rector - 1 discrepancy - interset 1 structure | Transmission Line (modification) | Modification/Upgrade | PB-22.11, PB-22.62, PB-22.64, PB-22.63, PB-22.56, PB-22.29, PB-22.58, PB-22.40 | Other - See Notes | NERC Compliance - GO 95 | Inspections do not drive the need for TLRR projects. However, SCE performs annual patrols and triennial detailed inspections of its transmission circuits, which inspect the structures and lines on those circuits. The date of last inspection for this circuit was 7/25/2019 | 70-80 years | IEEE-738 is the standard for calculating the current-temperature relationship of bare overhead conductors. This analysis along with SCE's standard rating methodology was used in conjunction with the PLS-CADD model that was created from the LiDAR study to identify any potential clearance issues on the circuits. | Transmission line clearance discrepancies are remediated based on a series of criteria, including line sag when operating at or above 130 degrees Fahrenheit; potential risk to public safety; and system reliability risk based on the location of span, terrain, encroachment type, and extent of deviation from standards. Discrepancies may be remediated by a variety of construction activities, including, but not limited to Structure Replacements, Structure Raises, New Structure Insets, Line Reconductor, Line Re-tension, Hardware Replacements, Grading, Removing Encroachments, Undergrounding Line Segments, Rerouting Lines. | Tier 2, Tier 3 | See Note 16B | The asset’s service life can be affected by the following environmental factors; high corrosive soils, weather climates, airborne contamination, and pollution. | Demetric Brown, MPO - Programs | 0.3 | See Note 20B | 220kV | See Note 22A | See Note 23B | TD612362 | CET-PD-OT-PJ-729800 | 7298 | See Note 27A | Yes | 2013 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2014 = 1,255 2020 = 30 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | Not Available | No | Not readily available | 2014-12-10 | N/A | Not readily available | Not readily available | See Note 53A | 1285.1861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1254.7641 | 0 | 30.422 | 0 | 0 | 1285.1861 | 344.743 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | 1.0477e-12 | None | 100% | 0% | Column 9: In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions.
N/A | PB-22.45 | Eagle Mountain-Blythe TLRR Remediation | 33.811, -115.454 / 33.611, -114.681 | Riverside County, Blythe | Eagle Mountain-Blythe line 161 kV - TLRR WO TD684647 This WO has 168 discrepancies to be remediated. Scope – ~53 mile reconductor, replace 53 existing structures with 44 new structures, replace 1 mile of existing underbuild subtrans (2 circuits) and distribution (2 circuits). FLOC #: ET-75165 Discrepancy #'s as shown: 4502353, 4502354, 4502355, 4502356, 4502357, 4502359, 4502362, 4502363, 4502364, 4502365, 4502366, 4502368, 4502370, 4502371, 4502372, 4502373, 4502375, 4502376, 4502377, 4502381, 4502382, 4502384, 4502385, 4502387, 4502388, 4502389, 4502390, 4502391, 4502392, 4502393, 4502394, 4502395, 4502396, 4502397, 4502398, 4502402, 4502403, 4502404, 4502405, 4502406, 4502407, 4502409, 4502410, 4502411, 4502412, 4502413, 4502414, 4502415, 4502416, 4502417, 4502418, 4502419, 4502420, 4502421, 4502422, 4502424, 4502425, 4502426, 4502427, 4502428, 4502429, 4502430, 4502431, 4502432, 4502433, 4502434, 4502436, 4502437, 4502439, 4502440, 4502441, 4502442, 4502444, 4502445, 4502446, 4502447, 4502448, 4502451, 4502453, 4502454, 4502456, 4502457, 4502458, 4502459, 4502461, 4502462, 4502463, 4502465, 4502466, 4502467, 4502468, 4502469, 4502470, 4502471, 4502472, 4502473, 4502474, 4502475, 4502476, 4502477, 4502478, 4502479, 4502480, 4502481, 4502482, 4502484, 4502485, 4502486, 4502487, 4502488, 4502489, 4502490, 4502491, 4502492, 4502493, 4502494, 4502495, 4502496, 4502497, 4502498, 4502500, 4502501, 4502502, 4502504, 4502505, 4502507, 4502509, 4502511, 4502512, 4502514, 4502516, 4502517, 4502519, 4502520, 4502521, 4502523, 4502524, 4502525, 4502526, 4502527, 4502528, 4502529, 4502530, 4502531, 4502532, 4502534, 4502535, 4502536, 4502537, 4502538, 4502539, 4502540, 4502541, 4502542, 4502543, 4502545, 4502546, 4502547, 4502548, 4502549, 4502550, 4502551, 4502552, 4502553, 4502554, 4502555, 4502557, and 4502558 | Transmission Line (reconductor and modification) | Reconductor | None | Other - See Notes | NERC Compliance - GO 95 | Inspections do not drive the need for TLRR projects. However, SCE performs annual patrols and triennial detailed inspections of its transmission circuits, which inspect the structures and lines on those circuits. The date of last inspection for this circuit was 3/14/2019 | 60-70 years | IEEE-738 is the standard for calculating the current-temperature relationship of bare overhead conductors. This analysis along with SCE's standard rating methodology was used in conjunction with the PLS-CADD model that was created from the LiDAR study to identify any potential clearance issues on the circuits. | Transmission line clearance discrepancies are remediated based on a series of criteria, including line sag when operating at or above 130 degrees Fahrenheit; potential risk to public safety; and system reliability risk based on the location of span, terrain, encroachment type, and extent of deviation from standards. Discrepancies may be remediated by a variety of construction activities, including, but not limited to Structure Replacements, Structure Raises, New Structure Insets, Line Reconductor, Line Re-tension, Hardware Replacements, Grading, Removing Encroachments, Undergrounding Line Segments, Rerouting Lines. | Non-HFRA | See Note 16B | The asset’s service life can be affected by the following environmental factors; high corrosive soils, weather climates, airborne contamination, and pollution. | Demetric Brown, MPO - Programs | 52 | See Note 20B | 161kV | See Note 22A | See Note 23B | TD684647 | CET-PD-OT-PJ-729800 | 7298 | See Note 27A | Yes | 2018 | Pre-2017 | FRM/CRT | No | N/A | N/A | N/A | Not Yet Operational | Not Yet Operational | TBD | TBD | CDFW | PTC | TBD | To Be Filed | 2022 | Pre-construction | See Note 46A | 2024-10-31 | No | 2021-12-31 | 2025-12-31 | Driven by Budget Plan & OD Changes | 25283 | 25283 | See Note 53A | 61236.4486 | 1000.004 | 13297.359 | 23388.601 | 8660.779 | 0 | 0 | 46346.743 | 2097.5402 | 331.434 | 849.6006 | 2668.1687 | 8942.9621 | 14889.7056 | 2425.5193 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | 12579.5352 | None | 0% | 100% | Column 9: In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions. Process for Utility Approval: The TLRR Program received FRM Approval for all non-operational projects on 4/1/2021. Column 52: Source= PMWIF (v1 Proj Summary)
N/A | PB-22.46 | Mira Loma-Rancho Vista TLRR Remediation | 34.010, -117.565 / 34.088, -117.533 | Rancho Cucamonga, Ontario | Mira Loma-Rancho Vista 500kV – 12 discrepancies – 2 interset structures and ~3 mile reconductor | Transmission Line (reconductor and modification) | Reconductor | None | Other - See Notes | NERC Compliance - GO 95 | Inspections do not drive the need for TLRR projects. However, SCE performs annual patrols and triennial detailed inspections of its transmission circuits, which inspect the structures and lines on those circuits. The date of last inspection for this circuit was 1/24/2020 | 30-40 years | IEEE-738 is the standard for calculating the current-temperature relationship of bare overhead conductors. This analysis along with SCE's standard rating methodology was used in conjunction with the PLS-CADD model that was created from the LiDAR study to identify any potential clearance issues on the circuits. | Transmission line clearance discrepancies are remediated based on a series of criteria, including line sag when operating at or above 130 degrees Fahrenheit; potential risk to public safety; and system reliability risk based on the location of span, terrain, encroachment type, and extent of deviation from standards. Discrepancies may be remediated by a variety of construction activities, including, but not limited to Structure Replacements, Structure Raises, New Structure Insets, Line Reconductor, Line Re-tension, Hardware Replacements, Grading, Removing Encroachments, Undergrounding Line Segments, Rerouting Lines. | Non-HFRA | See Note 16B | The asset’s service life can be affected by the following environmental factors; high corrosive soils, weather climates, airborne contamination, and pollution. | Demetric Brown, MPO - Programs | 3 | See Note 20B | 500 | See Note 22A | See Note 23B | 901942794 | CET-PD-OT-PJ-729800 | 7298 | See Note 27A | Yes | 2016-10-19 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2019 = 9,553 2020 = -190 2021 = -59 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2019-02-25 | No | 2017-12-31 | 2019-06-12 | Driven by Budget Plan & OD Changes | 5094 | 5094 | See Note 53A | 9303.1868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 601.5323 | 8951.2417 | -190.2619 | -59.232 | -0.09339 | 9303.1868 | 700.0831 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | -1.1817e-11 | None | 100% | 0% | Column 9: In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions. Column 52: Source= PMWIF (v0 Project Summary)
N/A | PB-22.47 | Pardee-Pastoria TLRR Remediation in San Joaquin Grid | 34.440, -118.582 / 34.935, -118.843 | Gorman, Los Angeles & Lebec, Kern County | Pardee-Pastoria 220kV - TLRR WO 901982966 (SJ) This WO has 30 discrepancies to be remediated. Scope – ~12 mile reconductor and 9 AmpJack structure raises FLOC #s ET-00667-04201 Discrepancy #s as shown: 4202016, 4202017, 4202018, 4202019, 4202020, 4202021, 4202022, 4202023, 4202025, 4202027, 4202030, 4202031, 4202033, 4202036, 4202037, 4202038, 4202039, 4202040, 4202041, 4202043, 4202044, 4202045, 4202046, 4202047, 4202048, 4202050, 4202051, 4202052, 4202053, 4202054. (WO# 901982966) | Transmission Line (reconductor and modification) | Reconductor | PB-22.31, PB-22.23, PB-22.32, PB-22.53 | Other - See Notes | NERC Compliance - GO 95 | Inspections do not drive the need for TLRR projects. However, SCE performs annual patrols and triennial detailed inspections of its transmission circuits, which inspect the structures and lines on those circuits. The date of last inspection for this circuit was 9/9/2019 | 100-110 years | IEEE-738 is the standard for calculating the current-temperature relationship of bare overhead conductors. This analysis along with SCE's standard rating methodology was used in conjunction with the PLS-CADD model that was created from the LiDAR study to identify any potential clearance issues on the circuits. | Transmission line clearance discrepancies are remediated based on a series of criteria, including line sag when operating at or above 130 degrees Fahrenheit; potential risk to public safety; and system reliability risk based on the location of span, terrain, encroachment type, and extent of deviation from standards. Discrepancies may be remediated by a variety of construction activities, including, but not limited to Structure Replacements, Structure Raises, New Structure Insets, Line Reconductor, Line Re-tension, Hardware Replacements, Grading, Removing Encroachments, Undergrounding Line Segments, Rerouting Lines. | Tier 2/Tier 3 | See Note 16B | The asset’s service life can be affected by the following environmental factors; high corrosive soils, weather climates, airborne contamination, and pollution. | Demetric Brown, MPO - Programs | See Note 19B | See Note 20B | 220 | See Note 22A | See Note 23B | 901982966 | CET-PD-OT-PJ-729800 | 7298 | See Note 27A | Yes | 2016-11-03 | Pre-2017 | FRM/CRT | No | N/A | N/A | N/A | See Col. 37 | 2022 = 21,936 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2019-06-04 | Yes | 2019-12-31 | 2022-05-04 | Driven by Budget Plan & OD Changes | 13841 | 13841 | See Note 53A | 21935.6118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 649.7113 | 6973.3363 | 10780.2369 | 1688.3201 | 1844.0073 | 21935.6118 | 4095.7718 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | 1.7785e-11 | None | 100% | 0% | Column 1: Formerly named Pardee-Pastoria TLRR Remediation (1) in July 1, 2021 SRP Column 9: In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions. Column 52: Source= PMWIF (v1 Project Summary) Process for Utility Approval: The TLRR Program received FRM Approval for all non-operational projects on 4/1/2021. Column 52: Source= Unverified system estimate
N/A | PB-22.48 | Mesa-Vincent No.1 TLRR Remediation (1) | 34.036, -118.110 / 34.486, -118.118 | Los Angeles County | Mesa-Vincent No. 1 220kV - TLRR WO 902698685 This WO has 7 discrepancies to be remediated. Scope – 7 AmpJack structure raises FLOC #s ET-01091 Discrepancy #s as shown: 4301930, 4301931, 4301933, 4301935, 4301946, 4301951, 4601939. | Transmission Line (modification) | Modification/Upgrade | None | Other - See Notes | NERC Compliance - GO 95 | Inspections do not drive the need for TLRR projects. However, SCE performs annual patrols and triennial detailed inspections of its transmission circuits, which inspect the structures and lines on those circuits. The date of last inspection for this circuit was 11/21/2019 | 50-60 years | IEEE-738 is the standard for calculating the current-temperature relationship of bare overhead conductors. This analysis along with SCE's standard rating methodology was used in conjunction with the PLS-CADD model that was created from the LiDAR study to identify any potential clearance issues on the circuits. | Transmission line clearance discrepancies are remediated based on a series of criteria, including line sag when operating at or above 130 degrees Fahrenheit; potential risk to public safety; and system reliability risk based on the location of span, terrain, encroachment type, and extent of deviation from standards. Discrepancies may be remediated by a variety of construction activities, including, but not limited to Structure Replacements, Structure Raises, New Structure Insets, Line Reconductor, Line Re-tension, Hardware Replacements, Grading, Removing Encroachments, Undergrounding Line Segments, Rerouting Lines. | Tier 2/Tier 3 | See Note 16B | The asset’s service life can be affected by the following environmental factors; high corrosive soils, weather climates, airborne contamination, and pollution. | Demetric Brown, MPO - Programs | 28 | See Note 20B | 220 | See Note 22A | See Note 23B | 902698685 | CET-PD-OT-PJ-729800 | 7298 | See Note 27A | Yes | 2016-10-04 | 2018 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2020 = 4,424 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2019-03-12 | No | 2019-12-31 | 2020-11-20 | Coordination with other projects in the area | 2377 | 2377 | See Note 53A | 4424.3138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2420.335 | 2003.9789 | 0 | 0 | 4424.3138 | 473.2545 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | -2.2101e-13 | None | 100% | 0% | Column 9: In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions. Column 52: Source= v5 Project Summary
N/A | PB-22.49 | Mira Loma-Vista No.1 TLRR Remediation | 34.010, -117.565 / 34.041, -117.320 | Jurupa Valley, Riverside County | Mira Loma-Vista No.1 - 15 discrepancies - raise 7 structures | Transmission Line (modification) | Modification/Upgrade | None | Other - See Notes | NERC Compliance - GO 95 | Inspections do not drive the need for TLRR projects. However, SCE performs annual patrols and triennial detailed inspections of its transmission circuits, which inspect the structures and lines on those circuits. The date of last inspection for this circuit was 9/1/2019 | 50-60 years | IEEE-738 is the standard for calculating the current-temperature relationship of bare overhead conductors. This analysis along with SCE's standard rating methodology was used in conjunction with the PLS-CADD model that was created from the LiDAR study to identify any potential clearance issues on the circuits. | Transmission line clearance discrepancies are remediated based on a series of criteria, including line sag when operating at or above 130 degrees Fahrenheit; potential risk to public safety; and system reliability risk based on the location of span, terrain, encroachment type, and extent of deviation from standards. Discrepancies may be remediated by a variety of construction activities, including, but not limited to Structure Replacements, Structure Raises, New Structure Insets, Line Reconductor, Line Re-tension, Hardware Replacements, Grading, Removing Encroachments, Undergrounding Line Segments, Rerouting Lines. | Tier 2 | See Note 16B | The asset’s service life can be affected by the following environmental factors; high corrosive soils, weather climates, airborne contamination, and pollution. | Demetric Brown, MPO - Programs | 9.5 | See Note 20B | 220 | See Note 22A | See Note 23B | 901960223 | CET-PD-OT-PJ-729800 | 7298 | See Note 27A | Yes | 2016-10-10 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2018 = 927 2019 = 1,438 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2017-10-16 | No | 2017-12-31 | 2018-03-29 | N/A | 1500 | 1500 | See Note 53A | 2364.8524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 927.1876 | 1437.6647 | 0 | 0 | 0 | 2364.8524 | 202.9362 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | -1.4224e-12 | None | 100% | 0% | Column 9: In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions. Column 52: Source= PMWIF (v1 Project Summary)
N/A | PB-22.50 | Rio Hondo-Vincent No.1 TLRR Remediation | 34.105, -117.981 / 34.486, -118.118 | Los Angeles County, Near Acton | Rio Hondo-Vincent No.1 - 3 discrepancies - raise 3 structures | Transmission Line (modification) | Modification/Upgrade | None | Other - See Notes | NERC Compliance - GO 95 | Inspections do not drive the need for TLRR projects. However, SCE performs annual patrols and triennial detailed inspections of its transmission circuits, which inspect the structures and lines on those circuits. The date of last inspection for this circuit was 11/22/2019 | 50-60 years | IEEE-738 is the standard for calculating the current-temperature relationship of bare overhead conductors. This analysis along with SCE's standard rating methodology was used in conjunction with the PLS-CADD model that was created from the LiDAR study to identify any potential clearance issues on the circuits. | Transmission line clearance discrepancies are remediated based on a series of criteria, including line sag when operating at or above 130 degrees Fahrenheit; potential risk to public safety; and system reliability risk based on the location of span, terrain, encroachment type, and extent of deviation from standards. Discrepancies may be remediated by a variety of construction activities, including, but not limited to Structure Replacements, Structure Raises, New Structure Insets, Line Reconductor, Line Re-tension, Hardware Replacements, Grading, Removing Encroachments, Undergrounding Line Segments, Rerouting Lines. | Tier 2/Tier 3 | See Note 16B | The asset’s service life can be affected by the following environmental factors; high corrosive soils, weather climates, airborne contamination, and pollution. | Demetric Brown, MPO - Programs | 11.5 | See Note 20B | 220 | See Note 22A | See Note 23B | 902137138 | CET-PD-OT-PJ-729800 | 7298 | See Note 27A | Yes | 2017-05-10 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2019 = 1,738 2020 = -3 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2018-12-11 | No | 2018-12-31 | 2019-05-22 | N/A | 718 | 718 | See Note 53A | 1735.2238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 594.6691 | 1143.6087 | -3.0541 | 0 | 0 | 1735.2238 | 150.0801 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | 7.7102e-13 | None | 100% | 0% | Column 9: In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions. Column 52: Source= PMWIF (v1 Project Summary)
N/A | PB-22.51 | Magunden-Pastoria No.1 TLRR Remediation | 35.361, -118.922 / 34.935, -118.843 | Kern County | Magunden-Pastoria No. 1 220kV - TLRR WO 901978202 This WO has 3 discrepancies to be remediated. Scope – 3 AmpJack structure raises. FLOC #s ET-00654 Discrepancy #s as shown: 4201642, 4201644, 4201647. | Transmission Line (modification) | Modification/Upgrade | None | Other - See Notes | NERC Compliance - GO 95 | Inspections do not drive the need for TLRR projects. However, SCE performs annual patrols and triennial detailed inspections of its transmission circuits, which inspect the structures and lines on those circuits. The date of last inspection for this circuit was 5/4/2020 | 80-90 years | IEEE-738 is the standard for calculating the current-temperature relationship of bare overhead conductors. This analysis along with SCE's standard rating methodology was used in conjunction with the PLS-CADD model that was created from the LiDAR study to identify any potential clearance issues on the circuits. | Transmission line clearance discrepancies are remediated based on a series of criteria, including line sag when operating at or above 130 degrees Fahrenheit; potential risk to public safety; and system reliability risk based on the location of span, terrain, encroachment type, and extent of deviation from standards. Discrepancies may be remediated by a variety of construction activities, including, but not limited to Structure Replacements, Structure Raises, New Structure Insets, Line Reconductor, Line Re-tension, Hardware Replacements, Grading, Removing Encroachments, Undergrounding Line Segments, Rerouting Lines. | Non-HFRA | See Note 16B | The asset’s service life can be affected by the following environmental factors; high corrosive soils, weather climates, airborne contamination, and pollution. | Demetric Brown, MPO - Programs | 5 | See Note 20B | 220 | See Note 22A | See Note 23B | 901978202 | CET-PD-OT-PJ-729800 | 7298 | See Note 27A | Yes | 2016-10-27 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2020 = 1,198 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2019-03-22 | No | 2018-12-31 | 2020-07-02 | Driven by Budget Plan & OD Changes | 1226 | 1226 | See Note 53A | 1198.4264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229.8796 | 1011.1706 | -42.6238 | 0 | 0 | 1198.4264 | 142.3011 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | -1.0842e-12 | None | 100% | 0% | Column 9: In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions. Column 52: Source= PMWIF (v1 Project Summary)
N/A | PB-22.52 | Magunden-Pastoria No.2 TLRR Remediation | 35.361, -118.922 / 34.935, -118.843 | Kern County | Magunden-Pastoria No. 2 220kV - TLRR WO 901978203 This WO has 4 discrepancies to be remediated. Scope – 4 AmpJack structure raises. FLOC #s ET-00657 Discrepancy #s as shown: 4201649, 4201654, 4201659, 4201664. | Transmission Line (modification) | Modification/Upgrade | None | Other - See Notes | NERC Compliance - GO 95 | Inspections do not drive the need for TLRR projects. However, SCE performs annual patrols and triennial detailed inspections of its transmission circuits, which inspect the structures and lines on those circuits. The date of last inspection for this circuit was 5/4/2020 | 80-90 years | IEEE-738 is the standard for calculating the current-temperature relationship of bare overhead conductors. This analysis along with SCE's standard rating methodology was used in conjunction with the PLS-CADD model that was created from the LiDAR study to identify any potential clearance issues on the circuits. | Transmission line clearance discrepancies are remediated based on a series of criteria, including line sag when operating at or above 130 degrees Fahrenheit; potential risk to public safety; and system reliability risk based on the location of span, terrain, encroachment type, and extent of deviation from standards. Discrepancies may be remediated by a variety of construction activities, including, but not limited to Structure Replacements, Structure Raises, New Structure Insets, Line Reconductor, Line Re-tension, Hardware Replacements, Grading, Removing Encroachments, Undergrounding Line Segments, Rerouting Lines. | Non-HFRA | See Note 16B | The asset’s service life can be affected by the following environmental factors; high corrosive soils, weather climates, airborne contamination, and pollution. | Demetric Brown, MPO - Programs | 27.5 | See Note 20B | 220 | See Note 22A | See Note 23B | 901978203 | CET-PD-OT-PJ-729800 | 7298 | See Note 27A | Yes | 2016-10-27 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2020 = 1,396 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2018-04-20 | No | 2018-12-31 | 2020-07-02 | Driven by Budget Plan & OD Changes | 2257 | 2257 | See Note 53A | 1395.8261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 544.0072 | 911.931 | -60.1121 | 0 | 0 | 1395.8261 | 131.4494 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | 4.2178e-14 | None | 100% | 0% | Column 9: In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions. Column 52: Source= PMWIF (v1 Project Summary)
N/A | PB-22.53 | Pardee-Pastoria-Warne TLRR Remediation | 34.440, -118.582 / 34.685, -118.787 | Los Angeles County, Castaic, Lebec | Pardee-Pastoria-Warne 220kV - TLRR This WO has 6 discrepancies to be remediated. Scope – 3 structure replacements and 2 interset structures FLOC #s ET-00624-04601 Discrepancy #s as shown: 4602131, 4602134, 4602139, 4602140, 4602141, 4602142. | Transmission Line (modification) | Modification/Upgrade | PB-22.31 PB-22.47, PB-22.23, PB-22.32 | Other - See Notes | NERC Compliance - GO 95 | Inspections do not drive the need for TLRR projects. However, SCE performs annual patrols and triennial detailed inspections of its transmission circuits, which inspect the structures and lines on those circuits. The date of last inspection for this circuit was 8/26/2019 | 60-70 years | IEEE-738 is the standard for calculating the current-temperature relationship of bare overhead conductors. This analysis along with SCE's standard rating methodology was used in conjunction with the PLS-CADD model that was created from the LiDAR study to identify any potential clearance issues on the circuits. | Transmission line clearance discrepancies are remediated based on a series of criteria, including line sag when operating at or above 130 degrees Fahrenheit; potential risk to public safety; and system reliability risk based on the location of span, terrain, encroachment type, and extent of deviation from standards. Discrepancies may be remediated by a variety of construction activities, including, but not limited to Structure Replacements, Structure Raises, New Structure Insets, Line Reconductor, Line Re-tension, Hardware Replacements, Grading, Removing Encroachments, Undergrounding Line Segments, Rerouting Lines. | Tier 2/Tier 3 | See Note 16B | The asset’s service life can be affected by the following environmental factors; high corrosive soils, weather climates, airborne contamination, and pollution. | Demetric Brown, MPO - Programs | 15.5 | See Note 20B | 220 | See Note 22A | See Note 23B | 901982968 | CET-PD-OT-PJ-729800 | 7298 | See Note 27A | Yes | 2016-11-03 | Pre-2017 | FRM/CRT | No | N/A | N/A | N/A | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Construction more than 50% completed | See Note 46A | 2020-08-03 | Yes | 2018-12-31 | 2023-11-20 | Driven by Budget Plan & OD Changes | 4339 | 4339 | See Note 53A | 2077.3681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 449.8579 | 761.2301 | 116.422 | 344.3746 | 405.4834 | 2077.3681 | 610.82 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | 1965.4846 | None | 100% | 0% | Column 9: In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions. Process for Utility Approval: The TLRR Program received FRM Approval for all non-operational projects on 4/1/2021. Column 52: Source= PMWIF (V0 Proj Summary); SCE provided in its Feb 2021 SRP Supplement a cost of $2.931M which was pulled from the system using a code which has subsequently corrected. Consistent with the methodology for the July SRP, SCE provides the original project cost from the PMWIF (v1 Proj Summary)
N/A | PB-22.54 | Colorado River-Red Bluff No.1 TLRR Remediation | 33.589, -114.814 / 33.672, -115.559 | Desert Center/ Blythe, Riverside County | Colorado River-Red Bluff No. 1 500kV - TLRR WO 901801050 This WO has 67 discrepancies to be remediated. Scope – ~30 mile reconductor from existing dead-end structure M1-T2 located just outside Colorado River Substation to dead-end structure M30-T3 located just outside of Red Bluff Substation. FLOC #s ET-00943 Discrepancy #s as shown: 4500011, 4500012, 4500013, 4500014, 4500015, 4500016, 4500017, 4500018, 4500019, 4500020, 4500021, 4500022, 4500023, 4500024, 4500025, 4500026, 4500027, 4500028, 4500029, 4500030, 4500031, 4500032, 4500033, 4500034, 4500035, 4500036, 4500037, 4500038, 4500039, 4500040, 4500041, 4500042, 4500043, 4500044, 4500045, 4507742, 4507743, 4507744, 4507745, 4507746, 4507747, 4507748, 4507749, 4507750, 4507751, 4507752, 4507753, 4507754, 4507755, 4507756, 4507757, 4507758, 4507759, 4507760, 4507761, 4507762, 4507763, 4507764, 4507765, 4507766, 4507767, 4507768, 4507769, 4507770, 4507771, 4507772, 4507773. | Transmission Line (reconductor) | Reconductor | PB-22.21 | Other - See Notes | NERC Compliance - GO 95 | Inspections do not drive the need for TLRR projects. However, SCE performs annual patrols and triennial detailed inspections of its transmission circuits, which inspect the structures and lines on those circuits. The date of last 3/11/2020 | ~45 years | IEEE-738 is the standard for calculating the current-temperature relationship of bare overhead conductors. This analysis along with SCE's standard rating methodology was used in conjunction with the PLS-CADD model that was created from the LiDAR study to identify any potential clearance issues on the circuits. | Transmission line clearance discrepancies are remediated based on a series of criteria, including line sag when operating at or above 130 degrees Fahrenheit; potential risk to public safety; and system reliability risk based on the location of span, terrain, encroachment type, and extent of deviation from standards. Discrepancies may be remediated by a variety of construction activities, including, but not limited to Structure Replacements, Structure Raises, New Structure Insets, Line Reconductor, Line Re-tension, Hardware Replacements, Grading, Removing Encroachments, Undergrounding Line Segments, Rerouting Lines. | Non-HFRA | See Note 16B | The asset’s service life can be affected by the following environmental factors; high corrosive soils, weather climates, airborne contamination, and pollution. | Demetric Brown, MPO - Programs | 30 | See Note 20B | 500 kV | See Note 22A | See Note 23B | 901801050 | CET-PD-OT-PJ-729800 | 7298 | See Note 27A | Yes | 2016-03-23 | Pre-2017 | FRM/CRT | No | N/A | N/A | N/A | See Col. 37 | 2021 = 23,966 2022 = 667 | CEQA Final Certified Sept 2018 | MND/CatEx | CDFW/BLM | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2021-10-01 | No | 2018-12-31 | 2021-12-17 | Driven by Budget Plan & OD Changes | 18895 | 18895 | See Note 53A | 24633.0807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8016.1456 | 522.8907 | 681.4495 | 14745.9272 | 666.6677 | 24633.0807 | 3784.8986 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | 3.4931e-12 | None | 100% | 0% | Column 9: In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions. Column 12: Column 12: Based on updated Transmission Engineering input Process for Utility Approval: The TLRR Program received FRM Approval for all non-operational projects on 4/1/2021. Column 52: Source= PMWIF (v1 Project Summary); SCE provided in its Feb 2021 SRP Supplement a cost of $14.234M which was pulled from the system using a code which has subsequently corrected. Consistent with the methodology for the July SRP, SCE provides the original project cost from the PMWIF (v1 Proj Summary)
N/A | PB-22.55 | Lugo-Mira Loma No.2 TLRR Remediation | 34.367, -117.369 / 34.010, -117.565 | San Bernardino, Lytle Creek | Lugo-Mira Loma No. 2 500 kV - TLRR WO 901987117 This WO has 2 discrepancies to be remediated. Scope – 2 AmpJack structure raises. FLOC #s ET-00083 Discrepancy #s as shown: 4500121, 4500150. | Transmission Line (modification) | Modification/Upgrade | None | Other - See Notes | NERC Compliance - GO 95 | Inspections do not drive the need for TLRR projects. However, SCE performs annual patrols and triennial detailed inspections of its transmission circuits, which inspect the structures and lines on those circuits. The date of last inspection for this circuit was 7/31/2019 | 50-60 years | IEEE-738 is the standard for calculating the current-temperature relationship of bare overhead conductors. This analysis along with SCE's standard rating methodology was used in conjunction with the PLS-CADD model that was created from the LiDAR study to identify any potential clearance issues on the circuits. | Transmission line clearance discrepancies are remediated based on a series of criteria, including line sag when operating at or above 130 degrees Fahrenheit; potential risk to public safety; and system reliability risk based on the location of span, terrain, encroachment type, and extent of deviation from standards. Discrepancies may be remediated by a variety of construction activities, including, but not limited to Structure Replacements, Structure Raises, New Structure Insets, Line Reconductor, Line Re-tension, Hardware Replacements, Grading, Removing Encroachments, Undergrounding Line Segments, Rerouting Lines. | Tier 2/Tier 3 | See Note 16B | The asset’s service life can be affected by the following environmental factors; high corrosive soils, weather climates, airborne contamination, and pollution. | Demetric Brown, MPO - Programs | 3.5 | See Note 20B | 500 | See Note 22A | See Note 23B | 901987117 | CET-PD-OT-PJ-729800 | 7298 | See Note 27A | Yes | 2016-11-09 | Pre-2017 | FRM/CRT | No | N/A | N/A | N/A | See Col. 37 | 2022 = 2,690 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2018-10-11 | Yes | 2018-12-31 | 2022-04-18 | Driven by Budget Plan & OD Changes | 19800 | 19800 | See Note 53A | 2690.1043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 683.0676 | 323.1074 | 117.0475 | 484.0394 | 1082.8424 | 2690.1043 | 475.7238 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | -4.3211e-12 | None | 100% | 0% | Column 9: In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions. Process for Utility Approval: The TLRR Program received FRM Approval for all non-operational projects on 4/1/2021. Column 52: Source= PMWIF (v1 Proj Summary); SCE provided in its Feb 2021 SRP Supplement a cost of $13.375M which was pulled from the system using a code which has subsequently corrected. Consistent with the methodology for the July SRP, SCE provides the original project cost from the PMWIF (v1 Proj Summary)
N/A | PB-22.56 | Big Creek 3-Rector No.2 TLRR Remediation | 37.148, -119.389 / 36.304, -119.244 | Tulare County, Fresno County | Big Creek 3-Rector No. 2 220kV - TLRR WO 901978105 This WO has 19 discrepancies to be remediated. Scope – 16 AmpJack structure raises, FAA marking and related scope as required FLOC #s ET-01058 Discrepancy #s as shown: 4201007, 4201009, 4201012, 4201013, 4201014, 4201016, 4201018, 4201019, 4201020, 4201021, 4201024, 4201025, 4201031, 4201032, 4201039, 4201040, 4201045, 4201048, 4201049. | Transmission Line (modification) | Modification/Upgrade | PB-22.11, PB-22.62, PB-22.64, PB-22.63, PB-22.40, PB-22.29, PB-22.58 | Other - See Notes | NERC Compliance - GO 95 | Inspections do not drive the need for TLRR projects. However, SCE performs annual patrols and triennial detailed inspections of its transmission circuits, which inspect the structures and lines on those circuits. The date of last inspection for this circuit was 6/27/2019 | 80-90 years | IEEE-738 is the standard for calculating the current-temperature relationship of bare overhead conductors. This analysis along with SCE's standard rating methodology was used in conjunction with the PLS-CADD model that was created from the LiDAR study to identify any potential clearance issues on the circuits. | Transmission line clearance discrepancies are remediated based on a series of criteria, including line sag when operating at or above 130 degrees Fahrenheit; potential risk to public safety; and system reliability risk based on the location of span, terrain, encroachment type, and extent of deviation from standards. Discrepancies may be remediated by a variety of construction activities, including, but not limited to Structure Replacements, Structure Raises, New Structure Insets, Line Reconductor, Line Re-tension, Hardware Replacements, Grading, Removing Encroachments, Undergrounding Line Segments, Rerouting Lines. | Tier 2/Tier 3 | See Note 16B | The asset’s service life can be affected by the following environmental factors; high corrosive soils, weather climates, airborne contamination, and pollution. | Demetric Brown, MPO - Programs | 49 | See Note 20B | 220 | See Note 22A | See Note 23B | 901978105 | CET-PD-OT-PJ-729800 | 7298 | See Note 27A | Yes | 2016-10-27 | Pre-2017 | FRM/CRT | No | N/A | N/A | N/A | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Construction more than 50% completed | See Note 46A | 2022-02-28 | No | 2019-12-31 | 2024-04-30 | Driven by Budget Plan & OD Changes | 23964 | 23964 | See Note 53A | 12858.0127 | 4310.426 | 1404.147 | 0 | 0 | 0 | 0 | 5714.573 | 754.7691 | 239.9645 | 115.8126 | 131.2204 | 5901.6731 | 7143.4397 | 1033.0461 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | 7143.4397 | None | 100% | 0% | Column 9: In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions. Process for Utility Approval: The TLRR Program received FRM Approval for all non-operational projects on 4/1/2021. General: This project is in a group of projects that are in the middle of the change management process to align schedules based on resource and outage availability. Costs forecasts have been updated for planning purposes, and schedule dates (including in-service dates) will be updated once the change management process is complete. Column 52: Source= PMWIF (v1 Proj Summary); SCE provided in its Dec 2020 SRP Supplement a cost of $16.188M which was pulled from the system using a code which has subsequently corrected. Consistent with the methodology for the July SRP, SCE provides the original project cost from the PMWIF (v1 Proj Summary)
N/A | PB-22.57 | Midway-Vincent No.2 TLRR Remediation (2) | 35.404, -119.450 / 34.486, -118.118 | Buttonwillow, Kern County & Palmdale, Los Angeles County & Ventura County | Midway-Vincent No. 2 500kV - TLRR WO 901881003 This WO has 1 discrepancy to be remediated. Scope – 2 AmpJack structure raises. FLOC #s ET-00127-04226 Discrepancy #s as shown: 4200268. | Transmission Line (modification) | Modification/Upgrade | PB-22.12 | Other - See Notes | NERC Compliance - GO 95 | Inspections do not drive the need for TLRR projects. However, SCE performs annual patrols and triennial detailed inspections of its transmission circuits, which inspect the structures and lines on those circuits. The date of last inspection for this circuit was 09/17/2019. | 40-50 years | IEEE-738 is the standard for calculating the current-temperature relationship of bare overhead conductors. This analysis along with SCE's standard rating methodology was used in conjunction with the PLS-CADD model that was created from the LiDAR study to identify any potential clearance issues on the circuits. | Transmission line clearance discrepancies are remediated based on a series of criteria, including line sag when operating at or above 130 degrees Fahrenheit; potential risk to public safety; and system reliability risk based on the location of span, terrain, encroachment type, and extent of deviation from standards. Discrepancies may be remediated by a variety of construction activities, including, but not limited to Structure Replacements, Structure Raises, New Structure Insets, Line Reconductor, Line Re-tension, Hardware Replacements, Grading, Removing Encroachments, Undergrounding Line Segments, Rerouting Lines. | Tier 2/Tier 3 | See Note 16B | The asset’s service life can be affected by the following environmental factors; high corrosive soils, weather climates, airborne contamination, and pollution. | Demetric Brown, MPO - Programs | 0.5 | See Note 20B | 500 kV | See Note 22A | See Note 23B | 901881003 | CET-PD-OT-PJ-729800 | 7298 | See Note 27A | Yes | 2016 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2021 = 1,100 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2018-11-03 | No | 2021-12-31 | 2021-05-24 | Driven by Budget Plan & OD Changes | 2173 | 2173 | See Note 53A | 1100.1269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 571.9971 | 102.3263 | 425.2256 | 0.57794 | 0 | 1100.1269 | 141.2556 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | -2.5773e-13 | None | 100% | 0% | Column 9: In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions. Column 52: Source= PMWIF (v1 Proj Summary); SCE provided in its Dec 2020 SRP Supplement a cost of $1.468M which was pulled from the system using a code which has subsequently corrected. Consistent with the methodology for the July SRP, SCE provides the original project cost from the PMWIF (v1 Proj Summary)
N/A | PB-22.58 | Big Creek1-Big Creek 2 TLRR Remediation | 37.204, -119.240 / 37.199, -119.307 | Orange Cove, Fresno County & Visalia, Tulare County | Big Creek 1-Big Creek 2 220 kV - TLRR WO 901978104 This WO has 7 discrepancies to be remediated. Scope – ~4.5 mile reconductor, 3 AmpJack structure raises, hardware modifications. FLOC #s ET-00449 Discrepancy #s as shown: 4200574, 4200575, 4200576, 4200577, 4200578, 4200581, 4200582. | Transmission Line (reconductor and modification) | Reconductor | PB-22.11, PB-22.62, PB-22.64, PB-22.63, PB-22.40, PB-22.56, PB-22.29 | Other - See Notes | NERC Compliance - GO 95 | Inspections do not drive the need for TLRR projects. However, SCE performs annual patrols and triennial detailed inspections of its transmission circuits, which inspect the structures and lines on those circuits. The date of last inspection for this circuit was 08/18/2020. | 100-110 years | IEEE-738 is the standard for calculating the current-temperature relationship of bare overhead conductors. This analysis along with SCE's standard rating methodology was used in conjunction with the PLS-CADD model that was created from the LiDAR study to identify any potential clearance issues on the circuits. | Transmission line clearance discrepancies are remediated based on a series of criteria, including line sag when operating at or above 130 degrees Fahrenheit; potential risk to public safety; and system reliability risk based on the location of span, terrain, encroachment type, and extent of deviation from standards. Discrepancies may be remediated by a variety of construction activities, including, but not limited to Structure Replacements, Structure Raises, New Structure Insets, Line Reconductor, Line Re-tension, Hardware Replacements, Grading, Removing Encroachments, Undergrounding Line Segments, Rerouting Lines. | Tier 3 | See Note 16B | The asset’s service life can be affected by the following environmental factors; high corrosive soils, weather climates, airborne contamination, and pollution. | Demetric Brown, MPO - Programs | 4.5 | See Note 20B | 220 kV | See Note 22A | See Note 23B | 901978104 | CET-PD-OT-PJ-729800 | 7298 | See Note 27A | Yes | 2016 | Pre-2017 | FRM/CRT | No | N/A | N/A | N/A | See Col. 37 | 2021 = 7,452 2022 = 21 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2020-04-22 | No | 2018-12-31 | 2021-04-20 | Driven by Budget Plan & OD Changes | 2842 | 2842 | See Note 53A | 7472.8663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 296.2246 | 189.8394 | 1112.5568 | 5853.2008 | 21.0447 | 7472.8663 | 679.0072 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | 9.195e-13 | None | 100% | 0% | General: This project is in a group of projects that are in the middle of the change management process to align schedules based on resource and outage availability. Costs forecasts have been updated for planning purposes, and schedule dates (including in-service dates) will be updated once the change management process is complete. Column 9: In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions. Column 31: The TLRR Program received FRM Approval for all non-operational projects on 4/1/2021. Column 36 & 37: Not operational at time of data pull (late March) Column 52: Source= PMWIF (v1 Proj Summary); SCE provided in its Dec 2020 SRP Supplement a cost of $1.92M which was pulled from the system using a code which has subsequently corrected. Consistent with the methodology for the July SRP, SCE provides the original project cost from the PMWIF (v1 Proj Summary)
N/A | PB-22.59 | Devers-Valley No.1 TLRR Remediation (2) | 33.935, -116.578 / 33.740, -117.157 | Banning/ Beaumont/ Cabazon/ Menifee/ Palm Springs/ White Water Canyon, Riverside County & Juniper Flats, San Bernardino County | Devers-Valley No. 1 500 kV - TLRR WO 902310543 This WO has 6 discrepancy to be remediated. Scope – 6 AmpJack structure raises. FLOC #s ET-00071-04987 Discrepancy #s as shown: 4500089, 4500095, 4500102, 4500105, 4500106, 4500107. | Transmission Line (modification) | Modification/Upgrade | None | Other - See Notes | NERC Compliance - GO 95 | Inspections do not drive the need for TLRR projects. However, SCE performs annual patrols and triennial detailed inspections of its transmission circuits, which inspect the structures and lines on those circuits. The date of last inspection for this circuit was 10/05/2020. | 30-40 years | IEEE-738 is the standard for calculating the current-temperature relationship of bare overhead conductors. This analysis along with SCE's standard rating methodology was used in conjunction with the PLS-CADD model that was created from the LiDAR study to identify any potential clearance issues on the circuits. | Transmission line clearance discrepancies are remediated based on a series of criteria, including line sag when operating at or above 130 degrees Fahrenheit; potential risk to public safety; and system reliability risk based on the location of span, terrain, encroachment type, and extent of deviation from standards. Discrepancies may be remediated by a variety of construction activities, including, but not limited to Structure Replacements, Structure Raises, New Structure Insets, Line Reconductor, Line Re-tension, Hardware Replacements, Grading, Removing Encroachments, Undergrounding Line Segments, Rerouting Lines. | Tier 2 | See Note 16B | The asset’s service life can be affected by the following environmental factors; high corrosive soils, weather climates, airborne contamination, and pollution. | Demetric Brown, MPO - Programs | 12 | See Note 20B | 500 kV | See Note 22A | See Note 23B | 902310543 | CET-PD-OT-PJ-729800 | 7298 | See Note 27A | Yes | 2018 | 2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2020 = 2,986 2021 = 3 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2020-04-27 | No | 2019-12-31 | 2020-08-11 | Driven by Budget Plan & OD Changes | 3000 | 3000 | See Note 53A | 2989.1659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.9446 | 25.1585 | 2955.3651 | 2.6978 | 0 | 2989.1659 | 243.5977 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | -1.7689e-12 | None | 100% | 0% | Column 9: In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions. Column 52: Source= PMWIF (v1 Proj Summary)
N/A | PB-22.60 | Control-Silver Peak 'A' High Fire Pole Replacement | 37.336, -118.481 | Bishop, Inyo County | The scope of work on the Control-Silver Peak ‘A’ 55kV line requires removing 59 poles and approximately 3.15 circuit miles of various amounts and sizes stranded aluminum and copper conductors, installing 57 Light Weight Steel Poles, Weathered and associated anchors and guy wires, installing approximately 3.15 circuit miles of 336.4 ACSR (30/7) conductor, installing approximately 3.15 linear miles of (one) 4/0 ACSR (6/1) Fault Return Conductor (FRC) at the shield wire position at the top of the LWS Poles from Control Substation to the Tubular Steel Pole (4696072E) on the Southside of Highway 395. | Transmission Line (rebuild) | Replacement | PB-22.61 | Other - See Notes | NERC Compliance - GO 95 | 2019-07-26 | 70-80 years | IEEE-738 is the standard for calculating the current-temperature relationship of bare overhead conductors. This analysis along with SCE's standard rating methodology was used in conjunction with the PLS-CADD model that was created from the LiDAR study to identify any potential clearance issues on the circuits. | Transmission line clearance discrepancies are remediated based on a series of criteria, including line sag when operating at or above 130 degrees Fahrenheit; potential risk to public safety; and system reliability risk based on the location of span, terrain, encroachment type, and extent of deviation from standards. Discrepancies may be remediated by a variety of construction activities, including, but not limited to Structure Replacements, Structure Raises, New Structure Insets, Line Reconductor, Line Re-tension, Hardware Replacements, Grading, Removing Encroachments, Undergrounding Line Segments, Rerouting Lines. | Tier 2 | See Note 16B | The asset’s service life can be affected by the following environmental factors; High Wind Events, High Fire Risk Area, Extreme Temperature Conditions, Mudslide | Demetric Brown, MPO - Programs | 3.5 | See Note 20B | 55 | See Note 22A | See Note 23B | TD1612502 | CET-PD-OT-PJ-TRHIGH | 7298 | See Note 27A | Yes | 2019 | 2018 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2020 = 4,757 2021 = 22 2022 = 16 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2020-05-26 | No | 2020-12-31 | 2020-08-20 | N/A | 3300 | 3300 | See Note 53A | 4794.4593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.2048 | 4746.4624 | 21.772 | 16.02 | 4794.4593 | 193.2954 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | 9.3132e-13 | None | 0% | 100% | Column 9: In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions. Column 52: Source= PMWIF (v0 Project Summary)
N/A | PB-22.61 | Control-Silver Peak 'C' High Fire Pole Replacement | 37.336, -118.481 | Bishop, Inyo County | The scope of work on the Control-Silver Peak ‘C’ line requires removing 59 poles and approximately 3.25 circuit miles of various amounts and sizes stranded aluminum and copper conductors, installing 60 Light Weight Steel Poles, Weathered and associated anchors and guy wires, installing approximately 3.25 circuit miles of 336.4 ACSR (30/7) conductor, installing approximately 3.25 linear miles of (one) 4/0 ACSR (6/1) Fault Return Conductor (FRC), at the shield wire position at the top of the LWS Poles from Control Substation to the Tubular Steel Pole (4832627E) on the Southside of Highway 395. | Transmission Line (rebuild) | Replacement | PB-22.60 | Other - See Notes | NERC Compliance - GO 95 | 2019-07-26 | 70-80 years | IEEE-738 is the standard for calculating the current-temperature relationship of bare overhead conductors. This analysis along with SCE's standard rating methodology was used in conjunction with the PLS-CADD model that was created from the LiDAR study to identify any potential clearance issues on the circuits. | Transmission line clearance discrepancies are remediated based on a series of criteria, including line sag when operating at or above 130 degrees Fahrenheit; potential risk to public safety; and system reliability risk based on the location of span, terrain, encroachment type, and extent of deviation from standards. Discrepancies may be remediated by a variety of construction activities, including, but not limited to Structure Replacements, Structure Raises, New Structure Insets, Line Reconductor, Line Re-tension, Hardware Replacements, Grading, Removing Encroachments, Undergrounding Line Segments, Rerouting Lines. | Tier 2 | See Note 16B | The asset’s service life can be affected by the following environmental factors; High Wind Events, High Fire Risk Area, Extreme Temperature Conditions, Mudslide | Demetric Brown, MPO - Programs | 3.5 | See Note 20B | 55 | See Note 22A | See Note 23B | TD1618682 | CET-PD-OT-PJ-TRHIGH | 7298 | See Note 27A | Yes | 2019 | 2018 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2020 = 6,001 2021 = 28 2022 = 4 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2020-05-26 | No | 2020-12-31 | 2020-08-20 | N/A | 3300 | 3300 | See Note 53A | 6033.9614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9829 | 5999.3895 | 28.4957 | 4.0933 | 6033.9614 | 335.0768 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | -9.3132e-13 | None | 0% | 100% | Column 9: In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions. Column 52: Source= PMWIF (v0 Project Summary)
N/A | PB-22.62 | Big Creek 2-Big Creek 3 TLRR Remediation | 37.199016;-119.306552 | Big Creek, Fresno County | Big Creek 2-Big Creek 3 220 kV - TLRR WO 901978113 This WO has 19 discrepancy to be remediated. Scope – ~7.5 mile reconductor, 3 AmpJack structure raises, hardware modifications. FLOC #s ET-00513 Discrepancy #s as shown: 4200774, 4200775, 4200776, 4200777, 4200778, 4200780, 4200781, 4200782, 4200783, 4200784, 4200785, 4200787, 4200788, 4200789, 4200790, 4200792, 4200793, 4200795, 4200796. | Transmission Line (reconductor and modification) | Reconductor | PB-22.11, PB-22.40, PB-22.44, PB-22.56, PB-22.58, PB-22.63, PB-22.64 | Other - See Notes | NERC Compliance - GO 95 | 2020-08-18 | 100-110 years | IEEE-738 is the standard for calculating the current-temperature relationship of bare overhead conductors. This analysis along with SCE's standard rating methodology was used in conjunction with the PLS-CADD model that was created from the LiDAR study to identify any potential clearance issues on the circuits. | Transmission line clearance discrepancies are remediated based on a series of criteria, including line sag when operating at or above 130 degrees Fahrenheit; potential risk to public safety; and system reliability risk based on the location of span, terrain, encroachment type, and extent of deviation from standards. Discrepancies may be remediated by a variety of construction activities, including, but not limited to Structure Replacements, Structure Raises, New Structure Insets, Line Reconductor, Line Re-tension, Hardware Replacements, Grading, Removing Encroachments, Undergrounding Line Segments, Rerouting Lines. | HFTD Tier 3 | See Note 16B | High Corrosive Soils, Weather Climates, Airborne Contamination, and Pollution | Demetric Brown, MPO - Programs | 7.5 | See Note 20B | 220kV | See Note 22A | See Note 23B | 901978113 | CET-PD-OT-PJ-729800 | 7298 | See Note 27A | Yes | 2016 | Pre-2017 | FRM/CRT | No | N/A | N/A | N/A | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | On Hold | See Note 46A | 2021-01-04 | No | 2019-12-31 | 2025-12-30 | Scope Increase, Resource and Outage Restrictions | 7721 | 7721 | See Note 53A | 18403.174 | 231.31 | 6613.82 | 6350.269 | 0 | 0 | 0 | 13195.399 | 455.9882 | 129.0434 | 78.9758 | 3279.2598 | 1264.5079 | 5207.775 | 777.4906 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | 4410.943 | None | 100% | 0% | Column 9: In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions. Process for Utility Approval: The TLRR Program received FRM Approval for all non-operational projects on 4/1/2021. Column 52: Source= PMWIF (v1 Project Summary); SCE provided in its Dec 2020 SRP Supplement a cost of $5.216M which was pulled from the system using a code which has subsequently corrected. Consistent with the methodology for the July SRP, SCE provides the original project cost from the PMWIF (v1 Proj Summary) General: This project is in a group of projects that are in the middle of the change management process to align schedules based on resource and outage availability. Costs forecasts have been updated for planning purposes, and schedule dates (including in-service dates) will be updated once the change management process is complete Column 45: Project on holding pending the outcome of a pending material evaluation.
N/A | PB-22.63 | Big Creek 3-Big Creek 8 TLRR Remediation | 37.148, -119.389 / 37.210, -119.329 | Orange Cove, Fresno County & Visalia, Tulare County | Big Creek 3-Big Creek 8 220 kV - TLRR WO 901978108 This WO has 14 discrepancies to be remediated. Scope – ~7 mile reconductor, 7 AmpJack structure raises, FAA marking as required. FLOC #s ET-00609 Discrepancy #s as shown: 4200812, 4200813, 4200815, 4200816, 4200819, 4200820, 4200821, 4200822, 4200823, 4200825, 4200826, 4200827, 4200828, 4200829. | Transmission Line (reconductor and modification) | Reconductor | PB-22.62, PB-22.64, PB-22.11, PB-22.40, PB-22.56, PB-22.29, PB-22.58 | Other - See Notes | NERC Compliance - GO 95 | 2022-08-09 | 70-80 years | IEEE-738 is the standard for calculating the current-temperature relationship of bare overhead conductors. This analysis along with SCE's standard rating methodology was used in conjunction with the PLS-CADD model that was created from the LiDAR study to identify any potential clearance issues on the circuits. | Transmission line clearance discrepancies are remediated based on a series of criteria, including line sag when operating at or above 130 degrees Fahrenheit; potential risk to public safety; and system reliability risk based on the location of span, terrain, encroachment type, and extent of deviation from standards. Discrepancies may be remediated by a variety of construction activities, including, but not limited to Structure Replacements, Structure Raises, New Structure Insets, Line Reconductor, Line Re-tension, Hardware Replacements, Grading, Removing Encroachments, Undergrounding Line Segments, Rerouting Lines. | Tier 2/Tier 3 | See Note 16C | High Fire Area Extreme Temperature Conditions | Demetric Brown, MPO - Programs | 7.3 | N/A | 220 | N/A | See Note 23B | 901978108 | CET-PD-OT-PJ-729800 | 7298 | See Note 27A | Yes | 2016 | Pre-2017 | FRM/CRT | N/A | N/A | N/A | N/A | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | On Hold | See Note 46A | 2022-11-29 | No | 2018-12-31 | 2025-03-18 | Resource and Outage Restrictions | 5689 | 5689 | See Note 53A | 15514.5789 | 2952.066 | 7958.836 | 0 | 0 | 0 | 0 | 10910.902 | 254.876 | 91.1598 | 39.4869 | 407.4931 | 3810.6611 | 4603.6769 | 558.7649 | See Note 57A | N/A | See Note 59A | 4176.7856 | None | 100% | 0% | Column 9: In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions. Process for Utility Approval: The TLRR Program received FRM Approval for all non-operational projects on 4/1/2021. Column 52: Source= PMWIF (v1 Project Summary); SCE provided in its Dec 2020 SRP Supplement a cost of $3.843M which was pulled from the system using a code which has subsequently corrected. Consistent with the methodology for the July SRP, SCE provides the original project cost from the PMWIF (v1 Proj Summary) General: This project is in a group of projects that are in the middle of the change management process to align schedules based on resource and outage availability. Costs forecasts have been updated for planning purposes, and schedule dates (including in-service dates) will be updated once the change management process is complete. Column 45: Project on holding pending the outcome of a pending material evaluation.
N/A | PB-22.64 | Big Creek 2-Big Creek 8 TLRR Remediation | 37.199016;-119.306552 | Big Creek, Fresno County | Big Creek 2-Big Creek 8 220 kV - TLRR WO 901978111 This WO has 6 discrepancies to be remediated. Scope – ~2 mile reconductor, 4 AmpJack structure raises, hardware modifications. FLOC #s ET-00545 Discrepancy #s as shown: 4200799, 4200801, 4200803, 4200804, 4200805, 4200807. | Transmission Line (reconductor and modification) | Reconductor | PB-22.11, PB-22.40, PB-22.44, PB-22.56, PB-22.58,PB-22.62, PB-22.63 | Other - See Notes | NERC Compliance - GO 95 | 2020-08-18 | 100-110 years | IEEE-738 is the standard for calculating the current-temperature relationship of bare overhead conductors. This analysis along with SCE's standard rating methodology was used in conjunction with the PLS-CADD model that was created from the LiDAR study to identify any potential clearance issues on the circuits. | Transmission line clearance discrepancies are remediated based on a series of criteria, including line sag when operating at or above 130 degrees Fahrenheit; potential risk to public safety; and system reliability risk based on the location of span, terrain, encroachment type, and extent of deviation from standards. Discrepancies may be remediated by a variety of construction activities, including, but not limited to Structure Replacements, Structure Raises, New Structure Insets, Line Reconductor, Line Re-tension, Hardware Replacements, Grading, Removing Encroachments, Undergrounding Line Segments, Rerouting Lines. | HFTD Tier 3 | See Note 16B | High Corrosive Soils, Weather Climates, Airborne Contamination, and Pollution | Demetric Brown, MPO - Programs | 1.7 | See Note 20B | 220kV | See Note 22A | See Note 23B | 901978111 | CET-PD-OT-PJ-729800 | 7298 | See Note 27A | Yes | 2016 | Pre-2017 | FRM/CRT | No | N/A | N/A | N/A | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | On Hold | See Note 46A | 2021-02-01 | No | 2018-12-31 | 2026-04-30 | Scope Increase, Resource and Outage Restrictions | 2437 | 2437 | See Note 53A | 11442.2694 | 204.881 | 0 | 6661.166 | 0 | 0 | 0 | 6866.047 | 194.4303 | 67.1106 | 40.9573 | 752.6197 | 3521.1044 | 4576.2224 | 521.8947 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | 4220.9107 | None | 100% | 0% | Column 9: In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions. Process for Utility Approval: The TLRR Program received FRM Approval for all non-operational projects on 4/1/2021. General: This project is in a group of projects that are in the middle of the change management process to align schedules based on resource and outage availability. Costs forecasts have been updated for planning purposes, and schedule dates (including in-service dates) will be updated once the change management process is complete. Column 52: Source= PMWIF (v1 Project Summary); SCE provided in its Dec 2020 SRP Supplement a cost of $1.646M which was pulled from the system using a code which has subsequently corrected. Consistent with the methodology for the July SRP, SCE provides the original project cost from the PMWIF (v1 Proj Summary) Column 45: Project on holding pending the outcome of a pending material evaluation.
0: N/A; Project Description 1: PB-22.65; Project Description 2: Eagle Rock-Gould TLRR Remediation; Project Description 4: Los Angeles County; Project Description 5: Eagle Rock-Gould 220kV - TLRR WO 903006911 This WO has 1 discrepancy to be remediated. Scope - 2 AmpJack structure raises FLOC #s ET-00035 Discrepancy #s as shown: 4401383.; Project Description 6: Transmission Line (modification); Project Description 7: Modification/Upgrade; Project Description (Cont.) 24: 903006911; Project Description (Cont.) 25: CET-PD-OT-PJ-729800; Project Description (Cont.) 26: 7298; Project Status 45: Operational; Project Status 50: 2023-05-02; Costs 52: 1250; Costs 52.1: 1250; Costs 54: 785.722 | [16 empty] | Column 9: In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions. Column 31: The TLRR Program received FRM Approval for all non-operational projects on 4/1/2021. Column 52: Source= PMWIF (v1 Project Summary)
0: N/A; Project Description 1: PB-22.66; Project Description 2: San Onofre-Santiago No. 1 & No. 2 TLRR Remediation; Project Description 4: Orange County; Project Description 5: San Onofre-Santiago No.1 & 2 220kV - TLRR WO 902266522 This WO has 3 discrepancies to be remediated. Scope - 2 structure raises (these are double circuit towers) FLOC #s ET-01188 Discrepancy #'s as Shown: 4802338, 4802341, and 4802343; Project Description 6: Transmission Line (modification); Project Description 7: Modification/Upgrade; Project Description (Cont.) 24: 902266522; Project Description (Cont.) 25: CET-PD-OT-PJ-729801; Project Description (Cont.) 26: 7298; Project Status 45: Operational; Project Status 50: 2021-10-29; Costs 52: 802.4; Costs 52.1: 802.4; Costs 54: 991.7546 | [16 empty] | Column 52: Source= PMWIF (V.1 Project Summary)
N/A | PB-22.67 | Padua-Rancho Vista No. 1 TLRR Remediation | 34.120, -117.639 / 34.518, -117.216 | Rancho Cucamonga, San Bernardino County | Padua-Rancho Vista No. 1 220kV - TLRR WO 902832617 This WO has 1 discrepancy to be remediated. Scope – 1 interset structure FLOC #s ET-01899 Discrepancy #s as shown: 4302006. | Transmission Line (modification) | Inset Structure | None | Other - See Notes | NERC Compliance - GO 95 | 2019-03-17 | 40-50 years | IEEE-738 is the standard for calculating the current-temperature relationship of bare overhead conductors. This analysis along with SCE's standard rating methodology was used in conjunction with the PLS-CADD model that was created from the LiDAR study to identify any potential clearance issues on the circuits. | Transmission line clearance discrepancies are remediated based on a series of criteria, including line sag when operating at or above 130 degrees Fahrenheit; potential risk to public safety; and system reliability risk based on the location of span, terrain, encroachment type, and extent of deviation from standards. Discrepancies may be remediated by a variety of construction activities, including, but not limited to Structure Replacements, Structure Raises, New Structure Insets, Line Reconductor, Line Re-tension, Hardware Replacements, Grading, Removing Encroachments, Undergrounding Line Segments, Rerouting Lines. | Non HFRA | See Note 16C | High Wind Events Extreme Temperature Conditions | Demetric Brown, MPO - Programs | 0.1 | N/A | 220 | N/A | See Note 23B | 902832617 | CET-PD-OT-PJ-729801 | 7298 | See Note 27A | Yes | 2016 | Pre-2017 | FRM/CRT | N/A | N/A | N/A | N/A | See Col. 37 | 2022 = 2,239 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2020-02-22 | Yes | 2019-12-31 | 2022-12-20 | Resource and Outage Restrictions | 400 | 400 | See Note 53A | 2238.8818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4477 | 2.6739 | 661.4598 | 1572.3004 | 2238.8818 | 281.5328 | See Note 57A | N/A | See Note 59A | -1.8626e-12 | None | 100% | 0% | Column 52: Source = PMWIF (08/30/2019 Investment Summary)
N/A | PB-23 | TLRR Program - 115 kV & below | Not applicable at program level | Not applicable at program level | Projects to mitigate potential electrical clearance issues in compliance with CPUC’s GO95 on circuits within the SCE territory that are 115kV or less. | Transmission Line (Seismic assessment and mitigation of transmission lines/towers) | New/Replacement/Modification | Not applicable at program level | Other - See Notes | NERC Compliance - GO 95 | Not applicable at program level | Not applicable at program level | N/A | Not applicable at program level | Not applicable at program level | See Note 16B | Not applicable at program level | Demetric Brown, MPO - Programs | Varies based on project | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 23B | Not applicable at program level | CET-PD-OT-PJ-729800 | 7298 | See Note 27A | Not applicable at program level | Not applicable at program level | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | Not applicable at program level | Not applicable at program level | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Not applicable at program level | See Note 46A | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 53A | Not applicable at program level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not applicable at program level | Not applicable at program level | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | See Note 60A | None | 0% | 100% | Column 9: In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions.
0: N/A; Project Description 1: PB-23.01; Project Description 2: Control-Haiwee-InyoKern No.1 TLRR Remediation; Project Description 4: Pearsville/ Lone Pine/ Big Pine/ Wilkerson/ Cartago/ Olancha, Inyo County; Project Description 5: Cancelled (see column 45); Project Description 6: Transmission line; Project Description 7: Cancelled (see column 45); Project Description (Cont.) 24: TD752247; Project Description (Cont.) 25: CET-PD-OT-PJ-729801; Project Description (Cont.) 26: 7298; Project Status 45: Canceled; Project Status 50: Canceled; Costs 52: Not readily available; Costs 52.1: Not readily available; Costs 54: 4.6896e-13 | [16 empty] | Column 9: In response to the NERC FAC-009-1 Standard Update issued in 2006 and the subsequent 2010 NERC Recommendation to Industry, Southern California Edison (SCE) conducted a Light Detection and Ranging (LiDAR) study to identify transmission lines potentially in violation of General Order (G.O.) 95. In conjunction with NERC and WECC, SCE agreed to remediate Bulk Electric System (BES) discrepancies by 2025, and all radial discrepancies by 2030. A discrepancy is generally defined where clearance between an energized conductor and its surroundings, such as the structure, another energized conductor of the same line or a different line, or the ground is not sufficient to meet G.O. 95 requirements during peak loading conditions.
N/A | PB-24 | Seismic Mitigation Program - Assessment & Prelim Engineering | Not applicable at program level | Not applicable at program level | Seismic Mitigation | Seismic Mitigation | New | Not applicable at program level | Other - See Notes | Age/Condition | Not applicable at program level | Typically 20+ years | Fragility and seismic analyses | Not applicable at program level | Not applicable at program level | See Note 16C | Not applicable at program level | Demetric Brown, MPO - Programs | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 23B | Not applicable at program level | COS-00-SP-BR-000000 | 7392 | See Note 27A | Yes | 2017 | 2017 | FRM/CRT | No | N/A | N/A | N/A | Not applicable at program level | Not applicable at program level | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Not applicable at program level | See Note 46A | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 53A | Not applicable at program level | 141.9321 | 101.3801 | 101.3801 | 101.3801 | 101.3801 | 506.9003 | 1054.3527 | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not applicable at program level | Not applicable at program level | See Note 57A | N/A | No Cost-Benefit analysis performed. Assessment identified possible risk of asset failure that could be caused by an earthquake/landslide. Also includes preliminary engineering activities to determine potential retrofit scope. | See Note 60A | None | 100% | 0% | Column 9: Seismic risk mitigation
N/A | PB-24.01 | SP T&D Asmt Trans Corridor Geotechnical | 34.777, -118.774 / 34.440, -118.582 | Bailey-Pardee M184-T3, Near Gorman, Los Angeles County Antelope-Vincent M7-T5, Palmdale, Los Angeles County Midway-Vincent M102-T2, Palmdale, Los Angeles County | Seismic slope stability mitigation by installation of soldier pile and lagging retaining wall or soil nail wall at selected 500kV or 220kV structures. | Transmission Line (Seismic slope stability mitigation by installation of soldier pile and lagging retaining wall or soil nail wall at selected 500kV or 220kV structures.) | New | None | Other - See Notes | Age/Condition | Bailey-Pardee M184-T3: 7/17/2018 Antelope-Vincent M7-T15: 1/24/2019 Midway-Vincent M102-T2: 8/8/18 Note Inspection date is of seismic inspection and not compliance driven inspection date | Midway-Vincent: 46y Only mitigation for support of tower being performed | Fragility and seismic analyses | Alternatives included not performing mitigation or relocating tower. Due to higher costs of relocating the tower including outages, no detailed cost estimate was performed but can be in the order of magnitude of 4 to 10 times the selected mitigation type depending on the location, voltage, circuit outage, and time of year. | Bailey-Pardee M184-T3: Tier 2 Antelope-Vincent M7-T5: Tier 3 Midway-Vincent M102-T2: Tier 3 | See Note 16C | Changing weather and climate conditions, erosion and landslide potential, seismic activity | Roderick Dela Cruz, Integrate System Strategy | See Note 19B | See Note 20B | 220kV and 500kV | See Note 22A | See Note 23B | 801678206 | COS-00-SP-TD-000002 | 7392 | See Note 27A | Yes | 2017 | Pre-2017 | FRM/CRT | No | N/A | N/A | N/A | See Col. 37 | 2018 = 2,980 2019 = 1,516 2020 = 5,228 2021 = 874 2022 = -1,991 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2018-10-28 | No | Bailey-Pardee M184-T3: 12/31/18 Antelope-Vincent M7-T5: 5/31/19 Midway-Vincent M102-T2: 12/19/18 | 2018-12-31 | N/A | ~3000/year for mitigating three tower site locations | ~3000/year for mitigating three tower site locations | See Note 53A | 8607.1202 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 2980.3055 | 1515.5932 | 5227.7299 | 874.0122 | -1990.5207 | 8607.1202 | 1018.901 | See Note 57A | N/A | No Cost-Benefit analysis performed. Assessment identified possible risk of tower failure that could be caused by an earthquake/landslide. | -6.8156e-12 | None | 100% | 0% | Column 9: Seismic mitigation Column 52: Source= Unverified estimate, documents not readily available
N/A | PB-25 | Seismic Mitigation Program - Substations | Not applicable at program level | Not applicable at program level | Seismic assessment and mitigation of transmission lines/towers | Transmission Line (Seismic assessment and mitigation of transmission lines/towers) | New / Replace /Upgrade | Not applicable at program level | Other - See Notes | Age/Condition | Antelope-Vincent M7-T15: 1/24/2019 | Not applicable at program level | Fragility and seismic analyses | Not applicable at program level | Not applicable at program level | See Note 16C | Not applicable at program level | Roderick Dela Cruz, Integrate System Strategy | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 23B | Not applicable at program level | COS-00-SP-TD-000000 | 7392 | See Note 27A | Yes | 2017 | Pre-2017 | FRM/CRT | No | N/A | N/A | N/A | Not applicable at program level | Not applicable at program level | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Not applicable at program level | See Note 46A | Not applicable at program level | Not applicable at program level | Antelope-Vincent M7-T15: 5/31/19 | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 53A | Not applicable at program level | 8108.6301 | 7173.019 | 7484.8894 | 7484.8894 | 1247.4816 | Not Available | 31498.9094 | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not applicable at program level | Not applicable at program level | See Note 57A | N/A | No Cost Benefit performed. Analysis identified possible loss of functionality and potential repair cost and times that could be caused by an earthquake that can be avoided through retrofit of substation components | See Note 60A | None | 100% | 0% | Column 9: Seismic mitigation
N/A | PB-25.01 | Devers Substation Seismic Mitigation Project | 33.935, -116.578 | Riverside County, North Palm Springs | Devers Sub - Seismic Mitigation Project Slacking / Re-Conductoring 500kV Pos. 1X: Reconductor A,B,C phases on North & South bus disc jumpers 500kV Pos. 1: Reconductor A,B,C phases on South bus disc jumpers 500kV Pos. 4: Reconductor A,B,C phases on South bus disc jumpers and from line disconnect to CB 217 500kV Pos. 7: Reconductor A,B,C phases on North bus disc jumpers and from line disconnect to CB 231 1AA bank: Reconductor from H1 bushing to jack bus 220kV Cap bank 3A and 3B:Reconductor disconnect bus jumper on both sides of cap switcher and cap side of 3B capacitor . Reconductor A, B phases north bus disconnect jumper. 220kV Pos. 1X: Reconductor all phases from CB 11 to line disconnect 220kV Pos. 3: Reconductor all phases from CB 19 to line disconnect 220kV Pos. 6: Reconductor all phases on south bus disconnect jumpers 220kV Pos. 7: Reconductor all phases from CB 35 to line disconnect 220kV Pos. 9: Reconductor all phases from CB 45 to line disconnect 220kV Pos. 10: Reconductor all phases from CB 49 to line disconnect Hanging Equipment (CCVT, WT, PT) 500kV Pos 1X: Replace three (3) tie down pedestal with latest standard 500kV Pos 1: Remove one (1) suspension mounted wave trap and upgrade six (6) tie down structure 500kV Pos 2: Replace six (6) tie down structure with latest standard 500kV Pos 4: Replace three (3) tie down structure with latest standard 500kV Pos 7: Replace three (3) tie down structure with latest standard 220kV Pos. 1X: Replace three (3) tie down structure with latest standard 220kV Pos. 1: Replace three (3) tie down structure with latest standard 220kV Pos. 2: Replace Six (6) tie down structure with latest standard. Relocate six (6)suspension mounted CCVT on new pedestals. 220kV Pos. 3: Replace three (3) tie down structure with latest standard. Relocate three (3) suspension mounted TRV onto new pedestals. 220kv Pos. 4: Remove three (3) tie down pedestals 220kV Pos. 6: Replace Six (6) tie down structure with latest standard. Relocate three (3) suspension mounted TRV on new pedestals. Replace three suspension mounted CCVT with 12,500pF rated CCVT and remove three (3) TRV and pedestals. 220kV Pos. 7: Relocate Three (3) suspension mounted TRV to pedestal and Replace three (3) tie down structures. Anchorage for AA Banks 500kV Pos. 1: Reactor Bank: Upgrade anchorage to minimum of 1G for each A,B,C bank 500/220 1AA Bank: Upgrade anchorage to minimum of 1G for each A,B,C bank Bushings (AA Bank) or CB replacement 220/115 4A Bank: Replace porcelain bushings with composite type 220/115 3A Bank: Replace porcelain bushings with composite type 220/115 1A Bank: Replace porcelain bushings with composite type Misc. Equipment MEER: Install bracing on all aluminum relay rack structures, anchor lockers, cabinets, and batteries Replace SEL 311L with SEL 421 and Remove RFL 9780 on 500kV Valley No. 1 line Install two (2) sets of BCT on CB 207 and CB 206 | Devers Sub - Seismic Mitigation Project Slacking / Re-Conductoring 500kV Pos. 1X: Reconductor A,B,C phases on North & South bus disc jumpers 500kV Pos. 1: Reconductor A,B,C phases on South bus disc jumpers 500kV Pos. 4: Reconductor A,B,C phases on South bus disc jumpers and from line disconnect to CB 217 500kV Pos. 7: Reconductor A,B,C phases on North bus disc jumpers and from line disconnect to CB 231 1AA bank: Reconductor from H1 bushing to jack bus 220kV Cap bank 3A and 3B:Reconductor disconnect bus jumper on both sides of cap switcher and cap side of 3B capacitor . Reconductor A, B phases north bus disconnect jumper. 220kV Pos. 1X: Reconductor all phases from CB 11 to line disconnect 220kV Pos. 3: Reconductor all phases from CB 19 to line disconnect 220kV Pos. 6: Reconductor all phases on south bus disconnect jumpers 220kV Pos. 7: Reconductor all phases from CB 35 to line disconnect 220kV Pos. 9: Reconductor all phases from CB 45 to line disconnect 220kV Pos. 10: Reconductor all phases from CB 49 to line disconnect Hanging Equipment (CCVT, WT, PT) 500kV Pos 1X: Replace three (3) tie down pedestal with latest standard 500kV Pos 1: Remove one (1) suspension mounted wave trap and upgrade six (6) tie down structure 500kV Pos 2: Replace six (6) tie down structure with latest standard 500kV Pos 4: Replace three (3) tie down structure with latest standard 500kV Pos 7: Replace three (3) tie down structure with latest standard 220kV Pos. 1X: Replace three (3) tie down structure with latest standard 220kV Pos. 1: Replace three (3) tie down structure with latest standard 220kV Pos. 2: Replace Six (6) tie down structure with latest standard. Relocate six (6)suspension mounted CCVT on new pedestals. 220kV Pos. 3: Replace three (3) tie down structure with latest standard. Relocate three (3) suspension mounted TRV onto new pedestals. 220kv Pos. 4: Remove three (3) tie down pedestals 220kV Pos. 6: Replace Six (6) tie down structure with latest standard. Relocate three (3) suspension mounted TRV on new pedestals. Replace three suspension mounted CCVT with 12,500pF rated CCVT and remove three (3) TRV and pedestals. 220kV Pos. 7: Relocate Three (3) suspension mounted TRV to pedestal and Replace three (3) tie down structures. Anchorage for AA Banks 500kV Pos. 1: Reactor Bank: Upgrade anchorage to minimum of 1G for each A,B,C bank 500/220 1AA Bank: Upgrade anchorage to minimum of 1G for each A,B,C bank Bushings (AA Bank) or CB replacement 220/115 4A Bank: Replace porcelain bushings with composite type 220/115 3A Bank: Replace porcelain bushings with composite type 220/115 1A Bank: Replace porcelain bushings with composite type Misc. Equipment MEER: Install bracing on all aluminum relay rack structures, anchor lockers, cabinets, and batteries Replace SEL 311L with SEL 421 and Remove RFL 9780 on 500kV Valley No. 1 line Install two (2) sets of BCT on CB 207 and CB 206 | New | None | Other - See Notes | Age/Condition | 2/13/2017 : Note Inspection date is of seismic inspection and not compliance driven inspection date | 20+ years | Fragility and seismic analyses | The alternative option considered is to keep the substation as is and potentially recover post seismic event. This has no upfront cost. Cost incurred would be in recovery time and effort that varies by size of seismic event. | Tier 3 | See Note 16C | Aside from typical weathering of components, seismic activity can impact retrofits, requiring re-inspection | Roderick Dela Cruz, Integrate System Strategy | See Note 19B | 98 | See Note 21A | 500/220 kv | See Note 23B | 902148977 | COS-00-SP-TD-000000 | 7392 | See Note 27A | Yes | 2017 | Pre-2017 | FRM/CRT | No | N/A | N/A | N/A | See Col. 37 | 2020 = 3,822 2022 = 104 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2018-10-08 | No | Midway-Vincent M102-T2: 12/19/18 | 2020-05-30 | Refinement of schedule for this project | 2501 | 2099.5958 | See Note 53A | 3926.5134 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 1759.0253 | 1823.8744 | 239.1593 | 0.23786 | 104.2165 | 3926.5134 | 684.3791 | See Note 57A | N/A | No Cost Benefit performed. Analysis identified possible loss of functionality and potential repair cost and times that could be caused by an earthquake that can be avoided through retrofit of substation components | -2.533e-12 | None | 100% | 0% | Column 9: Seismic mitigation Column 31: Column 52: Source= Unverified system estimate
N/A | PB-25.02 | Pardee Substation Seismic Mitigation Project | 34.440, -118.582 | Los Angeles County, Valencia | Pardee Sub - Seismic Mitigation Project Support/Modify Hanging Equipment: Position 5: Antelope Modify Hanging equipment Mount CCVT's on pedestals (East) Position 6: Bailey/Vincent No. 1 Modify Hanging equipment Mount CCVT's on pedestals (East and West) Position 7: Vincent No. 2/Pastoria Modify Hanging equipment Mount CCVT's on pedestals (East and West) Position 9: Pastoria-Warne/Santa Clara Modify Hanging equipment Mount CCVT's on pedestals (East and West) Position 10: Saugus No. 4 Modify Hanging equipment Mount CCVT's on pedestals (West) Position 12: Saugus No. 3 Modify Hanging equipment Mount CCVT's on pedestals (East) Position 13: Saugus No. 2 Modify Hanging equipment Mount CCVT's on pedestals (East) Position 15: Saugus No. 1/Moorpark No. 1 Modify Hanging equipment Mount CCVT's on pedestals (East and West) Position 17: Sylmar No. 2/Moorpark No. 2 Modify Hanging equipment Mount CCVT's on pedestals (East and West) Position 19: Sylmar No. 1/Moorpark No. 3 Modify Hanging equipment Mount CCVT's on pedestals (East and West) Misc. Battery Room control building Install styrofoam spacers Install seismic bracing for the freestanding aluminum relay racks in the MEER 220kV Positions 9E (Pastoria-Warne), 17E (Sylmar No. 2), and 19E (Sylmar No. 1): (CCVT with C phase wave trap) 1. Replace the three (3) existing tie-down CCVT’s mounting with a new pedestal pole type support structure, re-installing the CCVT’s with the required conduits and pull boxes as per latest SCE standards. 2. Leave the wave trap with its original vertical connection and a re-design tie down for the “C” phase only, re-installing the CCVT on pedestal type structure support next to the tie down structure. 3. A new foundation will be required for the re-installed CCVTs. 4. Reconductor all phase jumpers on both sides of the line’s disconnect switches providing proper slack keeping the phase to phase and phase to ground clearances requirements. Drawings will show required slack. 5. Install grounding for all new and re-installed structures and equipment according to the latest SCE standards. | Seismic | Replacement/Upgrade | None | Other - See Notes | Age/Condition | 3/22/17: Note Inspection date is for seismic inspection | 20+ years | Fragility and seismic analyses | The alternative option considered is to keep the substation as is and potentially recover post seismic event. This has no upfront cost. Cost incurred would be in recovery time and effort that varies by size of seismic event. | Tier 3 | See Note 16C | Aside from typical weathering of components, seismic activity can impact retrofits, requiring re-inspection | Roderick Dela Cruz, Integrate System Strategy | See Note 19B | 29.4 | See Note 21A | 220 kv | See Note 23B | 902149131 | COS-00-SP-TD-000000 | 7392 | See Note 27A | Yes | 2017 | Pre-2017 | FRM/CRT | No | N/A | N/A | N/A | See Col. 37 | 2021 = 3,806 2022 = 19 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2018-10-01 | No | 2018-12-31 | 2021-06-22 | Refinement of schedule for this project | 1552 | 1351.6321 | See Note 53A | 3824.9679 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 1315.245 | 1579.6338 | 500.2452 | 411.1952 | 18.6487 | 3824.9679 | 883.5347 | See Note 57A | N/A | No Cost Benefit performed. Analysis identified possible loss of functionality and potential repair cost and times that could be caused by an earthquake that can be avoided through retrofit of substation components | 1.7794e-12 | None | 100% | 0% | Column 9: Seismic mitigation Column 52: Source= Unverified system estimate
N/A | PB-25.03 | Lugo Substation Seismic Mitigation Project | 34.367, -117.369 | San Bernardino County, Hesperia | Lugo Sub - Seismic Mitigation Project Reconductor/Slack 500kV Bank position No. 3: Reconductor from west operating bus to disconnect to provide more slacks including conductors to disconnect and line risers 500kV Line position No. 5: 5W, reconductor from west operating bus to disconnect to provide more slacks. Replace conductor taps to dead end risers from line disconnect Line position No. 6: 6W, Reconductor from west operating bus to disconnect to provide more slack 500kV Bank position No. 4: Replace 4E conductor taps to dead end risers 500kV Line position No. 2: 2W, reconductor from west operating bus to disconnect to provide more slacks. 500kV Line position No. 1: Reconductor from west and east operating bus to bus disconnects to provide more slack Replace 1W bus disconnect to CB conductors Replace 1E conductor taps to dead end risers from tie CB disconnect Hanging Equipment ---- Modify 5E line wave trap to pedestal mount. A & C phase Modify 6E line wave trap to pedestal mount A & C phase Modify 2W line wave trap to pedestal mount A & C phase Modify 1W line wave trap to pedestal mount. A & C phase 2W and 2E Line Dead end: Replace A and B phase suspension CCVTs with pedestal mount. Replace C phase CCVT and wave trap with pedestal mount" 6W Line Dead end: Replace A, B, and C phase suspension CCVT’s with pedestal mount 6E Line Dead end: Replace A and B phase suspension CCVTs with pedestal mount. Replace C phase CCVT and wave trap with pedestal mount" 3E Line Dead end: Replace A and B phase suspension CCVTs with pedestal mount. Replace C phase CCVT and wave trap with pedestal mount 5E Line Dead end: Replace A, B, and C phase CCVTs with pedestal mount" Modifying 500kV suspension mount wave traps from line risers with pedestal mount is not possible due to the electrical clearances requirement between equipment. Potential solution to mitigate seismic requirement is to remove wave traps and replace PLC line protection with fiber optic communication Bushing replacement --- 2AA bank rack: Replace A, B, C phase, and spare transformers 500kV and 220kV porcelain bushings with polymer type Misc Equipment --- Replace East and West 500kV operating bus suspension jumpers with V-insulator supports. Typical on four locations. Replace East and West 220kV operating bus suspension jumpers with V-insulator supports. Typical on two locations Brace All Aluminum Relay Racks in MEER | Lugo Sub - Seismic Mitigation Project Reconductor/Slack 500kV Bank position No. 3: Reconductor from west operating bus to disconnect to provide more slacks including conductors to disconnect and line risers 500kV Line position No. 5: 5W, reconductor from west operating bus to disconnect to provide more slacks. Replace conductor taps to dead end risers from line disconnect Line position No. 6: 6W, Reconductor from west operating bus to disconnect to provide more slack 500kV Bank position No. 4: Replace 4E conductor taps to dead end risers 500kV Line position No. 2: 2W, reconductor from west operating bus to disconnect to provide more slacks. 500kV Line position No. 1: Reconductor from west and east operating bus to bus disconnects to provide more slack Replace 1W bus disconnect to CB conductors Replace 1E conductor taps to dead end risers from tie CB disconnect Hanging Equipment ---- Modify 5E line wave trap to pedestal mount. A & C phase Modify 6E line wave trap to pedestal mount A & C phase Modify 2W line wave trap to pedestal mount A & C phase Modify 1W line wave trap to pedestal mount. A & C phase 2W and 2E Line Dead end: Replace A and B phase suspension CCVTs with pedestal mount. Replace C phase CCVT and wave trap with pedestal mount" 6W Line Dead end: Replace A, B, and C phase suspension CCVT’s with pedestal mount 6E Line Dead end: Replace A and B phase suspension CCVTs with pedestal mount. Replace C phase CCVT and wave trap with pedestal mount" 3E Line Dead end: Replace A and B phase suspension CCVTs with pedestal mount. Replace C phase CCVT and wave trap with pedestal mount 5E Line Dead end: Replace A, B, and C phase CCVTs with pedestal mount" Modifying 500kV suspension mount wave traps from line risers with pedestal mount is not possible due to the electrical clearances requirement between equipment. Potential solution to mitigate seismic requirement is to remove wave traps and replace PLC line protection with fiber optic communication Bushing replacement --- 2AA bank rack: Replace A, B, C phase, and spare transformers 500kV and 220kV porcelain bushings with polymer type Misc Equipment --- Replace East and West 500kV operating bus suspension jumpers with V-insulator supports. Typical on four locations. Replace East and West 220kV operating bus suspension jumpers with V-insulator supports. Typical on two locations Brace All Aluminum Relay Racks in MEER | New | None | Other - See Notes | Age/Condition | 2/28/2017: Note Inspection date is of seismic inspection and not compliance driven inspection date | 20+ years | Fragility and seismic analyses | The alternative option considered is to keep the substation as is and potentially recover post seismic event. This has no upfront cost. Cost incurred would be in recovery time and effort that varies by size of seismic event. | Tier 2 | See Note 16C | High Wind Events, Extreme Temperature Conditions, Air Particulate Levels, High Seismic Area, Desert Region | Roderick Dela Cruz, Integrate System Strategy | See Note 19B | 46 | See Note 21A | 500/220 kv | See Note 23B | 902149179 | COS-00-SP-TD-000000 | 7392 | See Note 27A | Yes | 2017 | Pre-2017 | FRM/CRT | No | N/A | N/A | N/A | See Col. 37 | 2018 = 4,256 2019 = 20 2020 = 9 2021 = -6 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2018-02-12 | No | 2018-12-31 | 2018-11-30 | N/A | 2198 | 2198 | See Note 53A | 4278.496 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 4256.1546 | 19.5813 | 9.2574 | -6.4972 | 0 | 4278.496 | 533.88 | See Note 57A | N/A | No Cost Benefit performed. Analysis identified possible loss of functionality and potential repair cost and times that could be caused by an earthquake that can be avoided through retrofit of substation components | -1.1619e-12 | None | 100% | 0% | Column 9: Seismic mitigation Column 31: Column 52: Source= Unverified system estimate
N/A | PB-25.04 | Serrano Substation Seismic Mitigation Project | 33.830, -117.790 | Orange County, Orange | Serrano Substation:San Onofre 220kV line, pos. 2W-Remove and replace all three (3) existing CCVT’s with three (3) new pedestal mounted CCVT’s.-Install the three (3) new pedestal mounted CCVT’s on new structures and foundations.-On all three phases, remove, replace and re-configure spring riser to the weighted riser configuration. Villa Park No.2 220kV line, pos. 3E-Remove and replace all three (3) existing CCVT’s with three (3) new pedestal mounted CCVT’s.-Install the three (3) new pedestal mounted CCVT’s on new structures and foundations.-On all three phases, remove, replace and re-configure spring riser to the weighted riser configuration. Villa Park No.1 220kV line, pos. 4W-Remove and replace all three (3) existing CCVT’s with three (3) new pedestal mounted CCVT’s.-Install the three (3) new pedestal mounted CCVT’s on new structures and foundations.-On all three phases, remove, replace and re-configure spring riser to the weighted riser configuration. No. 1AA, no. 2AA and no. 3AA 13.8 kV Overhead conductors to ground detector banks-Remove and replace all overhead conductors with conductors of the same rating.-Provide sufficient slack for seismic mitigation. Mira Loma – Serrano No.1 500kV Line Protection Requirements-Remove three (3) RFL9780.-Install one (1) new RFL9745 for DDT system B. Mira Loma – Serrano No.2 500kV Line Protection Requirements-Remove three (3) RFL9780.-Install one (1) new RFL9745 for DDT system B. | Serrano Substation:San Onofre 220kV line, pos. 2W-Remove and replace all three (3) existing CCVT’s with three (3) new pedestal mounted CCVT’s.-Install the three (3) new pedestal mounted CCVT’s on new structures and foundations.-On all three phases, remove, replace and re-configure spring riser to the weighted riser configuration. Villa Park No.2 220kV line, pos. 3E-Remove and replace all three (3) existing CCVT’s with three (3) new pedestal mounted CCVT’s.-Install the three (3) new pedestal mounted CCVT’s on new structures and foundations.-On all three phases, remove, replace and re-configure spring riser to the weighted riser configuration. Villa Park No.1 220kV line, pos. 4W-Remove and replace all three (3) existing CCVT’s with three (3) new pedestal mounted CCVT’s.-Install the three (3) new pedestal mounted CCVT’s on new structures and foundations.-On all three phases, remove, replace and re-configure spring riser to the weighted riser configuration. No. 1AA, no. 2AA and no. 3AA 13.8 kV Overhead conductors to ground detector banks-Remove and replace all overhead conductors with conductors of the same rating.-Provide sufficient slack for seismic mitigation. Mira Loma – Serrano No.1 500kV Line Protection Requirements-Remove three (3) RFL9780.-Install one (1) new RFL9745 for DDT system B. Mira Loma – Serrano No.2 500kV Line Protection Requirements-Remove three (3) RFL9780.-Install one (1) new RFL9745 for DDT system B. | New | None | Other - See Notes | Age/Condition | 10/24/2017: Note Inspection date is of seismic inspection and not compliance driven inspection date | 20+ years | Fragility and seismic analyses | The alternative option considered is to keep the substation as is and potentially recover post seismic event. This has no upfront cost. Cost incurred would be in recovery time and effort that varies by size of seismic event. | Tier 2 | See Note 16C | Aside from typical weathering of components, seismic activity can impact retrofits, requiring re-inspection | Roderick Dela Cruz, Integrate System Strategy | See Note 19B | 19.2 | See Note 21A | 500/220 kv | See Note 23B | 902214599 | COS-00-SP-TD-000000 | 7392 | See Note 27A | Yes | 2017 | Pre-2017 | FRM/CRT | No | N/A | N/A | N/A | See Col. 37 | 2020 = 3,305 2021 = 8 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2020-03-30 | No | 2019-12-31 | 2020-05-15 | N/A | 4124 | 4124 | See Note 53A | 3312.9565 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 1030.4041 | 1090.9169 | 1183.9686 | 7.5333 | 0.13367 | 3312.9565 | 544.1701 | See Note 57A | N/A | No Cost Benefit performed. Analysis identified possible loss of functionality and potential repair cost and times that could be caused by an earthquake that can be avoided through retrofit of substation components | 7.9581e-14 | None | 100% | 0% | Column 9: Seismic mitigation Column 31: Column 52: Source= Unverified system estimate
N/A | PB-25.05 | Mira Loma Substation Seismic Mitigation Project | 34.010, -117.565 | Ontario, San Bernardino County | Mira Loma Sub - Seismic Mitigation Project Reconductor/Slack: (3) No.1AA (6) No.3AA (2) Spare Bank Support/Modify Hanging equipment: (36) 220kV CCVT Anchorage Upgrade: 1AA (All 3phases) 2AA (All 3 phases) 4AA (B & C phases only) AA Spare Bank A Spare Bank Bushing Replacement: No.1AA(A&C phases-high side) No.2AA(All 3 phases-high & low Side) No.3AA(AA 3 phases-high side) AA Spare Bank (high side) Misc: (6) Brace Aluminum racks (MEER 4) (18) Brace Aluminum racks (MEER 2) (3) Replace operating bus weight suspension insulators with triangular insulators for the bus jumpers. (10) Remove WT and line turners, upgrade channel bank and replace protective relays | Mira Loma Sub - Seismic Mitigation Project Reconductor/Slack: (3) No.1AA (6) No.3AA (2) Spare Bank Support/Modify Hanging equipment: (36) 220kV CCVT Anchorage Upgrade: 1AA (All 3phases) 2AA (All 3 phases) 4AA (B & C phases only) AA Spare Bank A Spare Bank Bushing Replacement: No.1AA(A&C phases-high side) No.2AA(All 3 phases-high & low Side) No.3AA(AA 3 phases-high side) AA Spare Bank (high side) Misc: (6) Brace Aluminum racks (MEER 4) (18) Brace Aluminum racks (MEER 2) (3) Replace operating bus weight suspension insulators with triangular insulators for the bus jumpers. (10) Remove WT and line turners, upgrade channel bank and replace protective relays | New | None | Other - See Notes | Age/Condition | August 2015 : Note Inspection date is of seismic inspection and not compliance driven inspection date | 20+ years | Fragility and seismic analyses | The alternative option considered is to keep the substation as is and potentially recover post seismic event. This has no upfront cost. Cost incurred would be in recovery time and effort that varies by size of seismic event. | Non-HFRA | See Note 16C | Aside from typical weathering of components, seismic activity can impact retrofits, requiring re-inspection | Roderick Dela Cruz, Integrate System Strategy | See Note 19B | 102.1 | 500/220 kV | 500, 220 kV | See Note 23B | 902149135 | COS-00-SP-TD-000000 | 7392 | See Note 27A | Yes | 2017 | Pre-2017 | FRM/CRT | No | N/A | N/A | N/A | See Col. 37 | 2020 = 4,231 2021 = 9 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2019-06-17 | No | 2019-12-31 | 2020-03-12 | N/A | 4711 | 4010.1921 | See Note 53A | 4241.044 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 506.5016 | 3052.2056 | 672.6551 | 9.4738 | 0.20797 | 4241.044 | 577.5951 | See Note 57A | N/A | No Cost Benefit performed. Analysis identified possible loss of functionality and potential repair cost and times that could be caused by an earthquake that can be avoided through retrofit of substation components | 8.9529e-14 | None | 100% | 0% | Column 9: Seismic mitigation Column 52: Source= Unverified system estimate
N/A | PB-25.06 | Vincent Substation Seismic Mitigation Project | 34.486, -118.118 | Palmdale, Los Angeles County | Vincent Seismic Mitigation Project Slack Add 500kV Position 1X: Add Slack at South Bus Disc Sw 500kV Position 5: 5S: Add Slack at South Bus Disc Sw 5N: Add Slack at North Bus Disc Sw 500kV Position 6: Add Slack at South Bus Disc Sw 1AA BANK: Add Slack 2AA BANK: Add Slack 3AA BANK: Add Slack 4AA BANK: Add Slack 220kV Position 1X: 1XN - Add slack at North Bus Disc Sw Support/Mod Hanging Eq 500kV No. 1 Series Capacitor: (6) weight-type tie downs shall be modified to field weld tabs. 500kV No. 2 Series Capacitor: (6) weight-type tie downs shall be modified to field weld tabs. Relocate (3) CCVT to pedestals. 500kV No. 2 Shunt Capacitor: (3) weight-type tie downs shall be modified to field weld tabs. 500kV No. 3 Shunt Capacitor: (3) weight-type tie downs shall be modified to field weld tabs. 500kV Position 2X: (6) weight-type tie downs shall be modified to field weld tabs. 500kV Position 1X: Replace three (3) weight-type tie downs. 500kV Position 1: 1N: Relocate (2) Wave Traps to pedestals. 1N: (3) weight-type tie downs shall be modified to field weld tabs. 1S: Replace three (3) spring-type tie downs w/ weight-type. 500kV Position 2: 2N: Relocate Wave Traps to pedestals. 2N: (3) weight-type tie downs shall be modified to field weld tabs. 500kV Position 3: (3) weight-type tie downs shall be modified to field weld tabs. 500kV Position 4: (3) weight-type tie downs shall be modified to field weld tabs. 500kV Position 5: (6) weight-type tie downs shall be modified to field weld tabs. 5S: Relocate (2) Wave Traps to pedestals. 500kV Position 6: 6N: (3) weight-type tie downs shall be modified to field weld. 6S: Replace three (3) spring-type tie downs w/weight-type. 3AA BANK: 500KV-(3) weight-type tie downs shall be modified to field weld. 220KV-Replace three (3) spring-type tie downs w/ weight-type. 4AA BANK: 220KV-Replace three (3) spring-type tie downs w/ weight-type. 220kV Position 1X: Replace six (6) spring-type tie downs. 1XS: Relocate (2) Wave Traps to pedestals. 1XS: Relocate (3) CCVT's to pedestals. 220kV Position 1: (6) weight-type tie downs shall be modified to field weld tabs. 1S: Relocate (1) Wave Trap to pedestals. 1S: Relocate (3) CCVT's to pedestals. 220kV Position 2: (6) weight-type tie downs shall be modified to field weld tabs. Relocate (3) CCVT's to pedestals. 220kV Position 3: (6) weight-type tie downs shall be modified to field weld tabs. 3S: Relocate (3) CCVT's to pedestals. 220kV Position 5: (6) weight-type tie downs shall be modified to field weld tabs. 5S: Relocate (3) CCVT's to pedestals. 220kV Position 6: (6) weight-type tie downs shall be modified to field weld tabs. 6S: Relocate (3) CCVT's to pedestals. 220kV Position 7: Relocate (6) CCVT's to pedestals. 7N: (3) weight-type tie downs shall be modified to field weld tabs. 7S: Replace (3) spring-type tie downs. 7S: Relocate (1) Wave trap to pedestal. Bushing Bk /CB Repl. 1AA BANK: Replace 500 kV bushings w/ Composite 4AA BANK: Replace 500 kV bushings w/ Composite Misc. Install seismic bracing for the freestanding alum relay racks in MEER | Seismic | New/Upgrade | None | Other - See Notes | Age/Condition | July 2016 : Note Inspection date is of seismic inspection and not compliance driven inspection date | 20+ years | Fragility and seismic analyses | The alternative option considered is to keep the substation as is and potentially recover post seismic event. This has no upfront cost. Cost incurred would be in recovery time and effort that varies by size of seismic event. | Tier 3 | See Note 16C | Aside from typical weathering of components, seismic activity can impact retrofits, requiring re-inspection | Roderick Dela Cruz, Integrate System Strategy | See Note 19B | 55 | 500/220 kV | 500/220kV | See Note 23B | 902149130 | COS-00-SP-TD-000000 | 7392 | See Note 27A | Yes | 2017 | Pre-2017 | FRM/CRT | No | N/A | N/A | N/A | See Col. 37 | 2020 = 4,812 2021 = -28 2022 = -14 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2019-03-18 | No | 2018-12-31 | 2020-11-06 | Coordination with Other Work and Outages | 2178 | 2178 | See Note 53A | 4770.4175 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 695.7364 | 2561.3231 | 1554.539 | -27.6193 | -13.5615 | 4770.4175 | 834.3009 | See Note 57A | N/A | No Cost Benefit performed. Analysis identified possible loss of functionality and potential repair cost and times that could be caused by an earthquake that can be avoided through retrofit of substation components | -4.1563e-12 | None | 100% | 0% | Column 9: Seismic mitigation Column 52: Source= Unverified system estimate
N/A | PB-25.07 | Pastoria Substation Seismic Mitigation Project | 34.935, -118.843 | Grapevine, Kern County | Pastoria Sub - Seismic Mitigation Project Support/Modify Hanging Equipment 220kV Pos. No. 1N (Magunden No. 3) (1) existing suspension mounted C-PH CCVT shall be modify. Reconfigure the wave trap 220kV Pos. No. 1S (Pardee-Warne) (1) existing suspension mounted C-PH CCVT shall be modify. Reconfigure the wave trap 220kV Pos. No. 3N (Magunden No. 2)(1) existing suspension mounted C-PH CCVT shall be modify 220kV Pos. No. 3S (Pardee) (1) existing suspension mounted C-PH CCVT shall be modify 220kV Pos. No. 4N (Magunden No. 1) (1) existing suspension mounted C-PH CCVT shall be modify 220kV Pos. line 4S (Bailey)(1) existing suspension mounted C-PH CCVT shall be modify 220kV Pos. 5N (Lebec) (3) existing suspension mounted CCVT shall be modify 220kV Pos. 5S (Edmonston) (3) existing suspension mounted CCVT shall be modify Misc: Install seismic bracing for the freestanding aluminum relay racks in the MEER | Pastoria Sub - Seismic Mitigation Project Support/Modify Hanging Equipment 220kV Pos. No. 1N (Magunden No. 3) (1) existing suspension mounted C-PH CCVT shall be modify. Reconfigure the wave trap 220kV Pos. No. 1S (Pardee-Warne) (1) existing suspension mounted C-PH CCVT shall be modify. Reconfigure the wave trap 220kV Pos. No. 3N (Magunden No. 2)(1) existing suspension mounted C-PH CCVT shall be modify 220kV Pos. No. 3S (Pardee) (1) existing suspension mounted C-PH CCVT shall be modify 220kV Pos. No. 4N (Magunden No. 1) (1) existing suspension mounted C-PH CCVT shall be modify 220kV Pos. line 4S (Bailey)(1) existing suspension mounted C-PH CCVT shall be modify 220kV Pos. 5N (Lebec) (3) existing suspension mounted CCVT shall be modify 220kV Pos. 5S (Edmonston) (3) existing suspension mounted CCVT shall be modify Misc: Install seismic bracing for the freestanding aluminum relay racks in the MEER | New | None | Other - See Notes | Age/Condition | July 2016 : Note Inspection date is of seismic inspection and not compliance driven inspection date | 20+ years | Fragility and seismic analyses | The alternative option considered is to keep the substation as is and potentially recover post seismic event. This has no upfront cost. Cost incurred would be in recovery time and effort that varies by size of seismic event. | Non-HFRA | See Note 16C | Aside from typical weathering of components, seismic activity can impact retrofits, requiring re-inspection. High Seismic Area | Roderick Dela Cruz, Integrate System Strategy | See Note 19B | 4.6 | 220kV | 220 kV | See Note 23B | 902149132 | COS-00-SP-TD-000000 | 7392 | See Note 27A | Yes | 2017 | Pre-2017 | FRM/CRT | No | N/A | N/A | N/A | See Col. 37 | 2020 = 3,418 2021 = 81 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2019-03-04 | No | 2018-12-31 | 2021-05-04 | Coordination with Other Work and Outages | 273 | 273 | See Note 53A | 3498.5707 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 650.2805 | 1568.5057 | 1199.1974 | 80.5871 | 0 | 3498.5707 | 517.8413 | See Note 57A | N/A | No Cost Benefit performed. Analysis identified possible loss of functionality and potential repair cost and times that could be caused by an earthquake that can be avoided through retrofit of substation components | -2.7135e-12 | None | 100% | 0% | Column 9: Seismic mitigation Column 52: Source= PMWIF (v0 Project Summary)
N/A | PB-25.08 | Magunden Substation Seismic Mitigation Project | 35.361, -118.922 | Bakersfield, Kern County | Magunden Substation: 220kV Positions -Positions 1, 2, and 4, relocate the three (3) existing CCVT’s on new pedestal pole type support structures and new foundations. Install three (3) new weighted riser steel structures on the existing foundation. Install the CCVT’s with the required conduits and pull boxes as per latest SCE standards. Action item: See if one (1) wavetrap can be removed by upgrading protection. -Positions 3, 5, 7, and 9, relocate the three (3) existing CCVT’s on new pedestal pole type support structures and new foundations. Install three (3) new weighted riser steel structures on the existing foundation. Install the CCVT’s with the required conduits and pull boxes as per latest SCE standards. -Position 8, replace the three (3) existing CCVT’s with three (3) new CCVT’s on new pedestal pole type support structures and new foundations, re-installing the required conduits and pull boxes as per latest SCE standards. Remove three (3) existing risers and foundations and replace with three (3) new weighted risers and foundations. -Positions 10, and 11, replace the three (3) existing CCVT’s with three (3) new CCVT’s on new pedestal pole type support structures and new foundations, re-installing the required conduits and pull boxes as per latest SCE standards. Remove three (3) existing risers and foundations and replace with three (3) new weighted risers and foundations. Emergency Generators -Replace Onan Gen Set generator with seismically qualified unit 220kV Busses -220kV North Bus: Brace three (3) weighted risers at top of bus dead end to prevent side sway with triangular insulators -220kV South Bus:Brace three (3) weighted risers at top of bus dead end to prevent side sway with triangular insulators Control Room -Install six (6) new frames with span of 10 ft maximum to reinforce the aluminum relay racks. The new frame support will be located at the front side of the relay racks. | Magunden Substation: 220kV Positions -Positions 1, 2, and 4, relocate the three (3) existing CCVT’s on new pedestal pole type support structures and new foundations. Install three (3) new weighted riser steel structures on the existing foundation. Install the CCVT’s with the required conduits and pull boxes as per latest SCE standards. Action item: See if one (1) wavetrap can be removed by upgrading protection. -Positions 3, 5, 7, and 9, relocate the three (3) existing CCVT’s on new pedestal pole type support structures and new foundations. Install three (3) new weighted riser steel structures on the existing foundation. Install the CCVT’s with the required conduits and pull boxes as per latest SCE standards. -Position 8, replace the three (3) existing CCVT’s with three (3) new CCVT’s on new pedestal pole type support structures and new foundations, re-installing the required conduits and pull boxes as per latest SCE standards. Remove three (3) existing risers and foundations and replace with three (3) new weighted risers and foundations. -Positions 10, and 11, replace the three (3) existing CCVT’s with three (3) new CCVT’s on new pedestal pole type support structures and new foundations, re-installing the required conduits and pull boxes as per latest SCE standards. Remove three (3) existing risers and foundations and replace with three (3) new weighted risers and foundations. Emergency Generators -Replace Onan Gen Set generator with seismically qualified unit 220kV Busses -220kV North Bus: Brace three (3) weighted risers at top of bus dead end to prevent side sway with triangular insulators -220kV South Bus:Brace three (3) weighted risers at top of bus dead end to prevent side sway with triangular insulators Control Room -Install six (6) new frames with span of 10 ft maximum to reinforce the aluminum relay racks. The new frame support will be located at the front side of the relay racks. | New | None | Other - See Notes | Age/Condition | July 2016 : Note Inspection date is of seismic inspection and not compliance driven inspection date | 20+ years | Fragility and seismic analyses | The alternative option considered is to keep the substation as is and potentially recover post seismic event. This has no upfront cost. Cost incurred would be in recovery time and effort that varies by size of seismic event. | Non-HFRA | See Note 16C | Aside from typical weathering of components, seismic activity can impact retrofits, requiring re-inspection. Moderate Seismic Area, flooding | Roderick Dela Cruz, Integrate System Strategy | See Note 19B | 15.3 | 220kV | 220 kV | See Note 23B | 902214377 | COS-00-SP-TD-000000 | 7392 | See Note 27A | Yes | 2017 | Pre-2017 | FRM/CRT | No | N/A | N/A | N/A | See Col. 37 | 2020 = 2,283 2021 = 54 2022 = -56 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2019-10-09 | No | 2019-12-31 | 2020-04-02 | N/A | 2693 | 2564.3064 | See Note 53A | 2281.9049 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 235.8789 | 1139.5811 | 907.7568 | 54.4522 | -55.7641 | 2281.9049 | 289.526 | See Note 57A | N/A | No Cost Benefit performed. Analysis identified possible loss of functionality and potential repair cost and times that could be caused by an earthquake that can be avoided through retrofit of substation components | -1.034e-12 | None | 100% | 0% | Column 9: Seismic mitigation Column 52: Source= Unverified system estimate
N/A | PB-25.09 | Whirlwind Substation Seismic Mitigation Project | 34.857, -118.436 | Rosamond, Kern County | Whirlwind Substation: 500kV Positions -Position 1N, 1S, 2S, 7N, remove wavetrap and upgrade protection. 220kV Positions -Positions, 1, 2, 13, 14, 16 and 17, relocate the three (3) existing CCVT’s on new pedestal pole type support structures and new foundations. Install three (3) new weighted riser steel structures on the existing foundation. Install the CCVT’s with the required conduits and pull boxes as per latest SCE standards. Control Room -Install six (6) new frames with span of 10 ft maximum to reinforce the aluminum relay racks. The new frame support will be located at the front side of the relay racks. | Seismic | New/Upgrade | None | Other - See Notes | Age/Condition | July 2016 : Note Inspection date is of seismic inspection and not compliance driven inspection date | 20+ years | Fragility and seismic analyses | The alternative option considered is to keep the substation as is and potentially recover post seismic event. This has no upfront cost. Cost incurred would be in recovery time and effort that varies by size of seismic event. | Non-HFRA | See Note 16C | Aside from typical weathering of components, seismic activity can impact retrofits, requiring re-inspection | Roderick Dela Cruz, Integrate System Strategy | See Note 19B | 92 | 500/220kV | 500/220kV | See Note 23B | 902214603 | COS-00-SP-TD-000000 | 7392 | See Note 27A | Yes | 2017 | Pre-2017 | FRM/CRT | No | N/A | N/A | N/A | See Col. 37 | 2019 = 1,016 2020 = 328 2022 = -44 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2019-10-21 | No | 2019-12-31 | 2019-12-20 | N/A | 931 | 931 | See Note 53A | 1299.2324 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 138.2089 | 877.6384 | 327.8609 | 2e-05 | -44.4758 | 1299.2324 | 113.5534 | See Note 57A | N/A | No Cost Benefit performed. Analysis identified possible loss of functionality and potential repair cost and times that could be caused by an earthquake that can be avoided through retrofit of substation components | 2.708e-13 | None | 100% | 0% | Column 9: Seismic mitigation Column 52: Source= Unverified system estimate
N/A | PB-25.10 | Victor Substation Seismic Mitigation Project | 34.506, -117.387 | Victorville, San Bernardino County | Victor Sub (Phase 1): 220kV Positions 1. Position 1N – Lugo No.2 a. Replace three (3) existing CCVT on new pedestal pole type support structures and new foundations. b. Remove three (3) existing risers and foundations and replace with three (3) new weighted risers and foundations. c. Relocate pull box per latest SCE standards. d. Reconductor to add slack between CB 6012 and adjacent disconnect switch (south side) 3. Position 3S – Lugo No.1 a. Replace three (3) existing CCVT on new pedestal pole type support structures and new foundations. b. Remove three (3) existing risers and foundations and replace with three (3) new weighted risers and foundations. c. Relocate pull box per latest SCE standards. | Victor Sub (Phase 1): 220kV Positions 1. Position 1N – Lugo No.2 a. Replace three (3) existing CCVT on new pedestal pole type support structures and new foundations. b. Remove three (3) existing risers and foundations and replace with three (3) new weighted risers and foundations. c. Relocate pull box per latest SCE standards. d. Reconductor to add slack between CB 6012 and adjacent disconnect switch (south side) 3. Position 3S – Lugo No.1 a. Replace three (3) existing CCVT on new pedestal pole type support structures and new foundations. b. Remove three (3) existing risers and foundations and replace with three (3) new weighted risers and foundations. c. Relocate pull box per latest SCE standards. | New | None | Other - See Notes | Age/Condition | July 2016 : Note Inspection date is of seismic inspection and not compliance driven inspection date | 20+ years | Fragility and seismic analyses | The alternative option considered is to keep the substation as is and potentially recover post seismic event. This has no upfront cost. Cost incurred would be in recovery time and effort that varies by size of seismic event. | Non-HFRA | See Note 16C | Aside from typical weathering of components, seismic activity can impact retrofits, requiring re-inspection | Roderick Dela Cruz, Integrate System Strategy | See Note 19B | 33.3 | 220kV | 220kV | See Note 23B | 902391638 | COS-00-SP-TD-000000 | 7392 | See Note 27A | Yes | 2017 | 2017 | FRM/CRT | No | N/A | N/A | N/A | See Col. 37 | 2019 = 903 2020 = 116 2021 = 2 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2019-11-15 | No | 2019-12-31 | 2019-12-26 | N/A | 298 | 264.1363 | See Note 53A | 1021.819 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 157.7404 | 745.344 | 116.3541 | 2.3806 | 0 | 1021.819 | 279.5856 | See Note 57A | N/A | No Cost Benefit performed. Analysis identified possible loss of functionality and potential repair cost and times that could be caused by an earthquake that can be avoided through retrofit of substation components | -6.3998e-13 | None | 100% | 0% | Column 9: Seismic mitigation Column 52: Source= Unverified system estimate
N/A | PB-25.11 | Antelope Substation Seismic Mitigation Project | 34.688, -118.300 | Lancaster, Los Angeles County | Antelope Sub - Seismic Mitigation Project Remove 500KV Wave Traps, Line Tuners and associated conduits and home run cables from AØ & CØ tie downs. Re‐conductor Tie Downs at pos. 2W. Reconductor/Slack: 220kV Pos. No. 12E (from 220kV East Bus To Disconnect Switch) 550kV Pos. No. 1W & 1E (from 500kV East/West Buses To Disconnect Switch) 500kV Pos. No. 2E(from 500kV East Bus To Disconnect Switch) 500kV Pos. No. 6W & 6E (from 500kV East/West Bus to Disconnect Switch) No. 5 500kV Cap Bank (from bus support structure to Disconnect Switch) No. 6 500kV Cap Bank (from bus support structure to Disconnect Switch) No. 2AA 500-220kV Trans Bank (from bushings to first post) Support/Modify Hanging Eq: 220kV Pos. No. 1,2, & 4 500kV Pos. No. 1W 500kV Pos. No. 2W &2E 500kV Pos. No. 5W & 5E 500kV Pos. No. 6W No. 5 500 kV Cap Bank Misc: Brace All Aluminum Relay Racks in MEER Replace riser tie down rod and weights on all phases. Weld Tab to existing steel risers. | Seismic | Replacement/Upgrade | None | Other - See Notes | Age/Condition | July 2016 : Note Inspection date is of seismic inspection and not compliance driven inspection date | 20+ years | Fragility and seismic analyses | The alternative option considered is to keep the substation as is and potentially recover post seismic event. This has no upfront cost. Cost incurred would be in recovery time and effort that varies by size of seismic event. | Non-HFRA | See Note 16C | Aside from typical weathering of components, seismic activity can impact retrofits, requiring re-inspection | Roderick Dela Cruz, Integrate System Strategy | See Note 19B | 73 | 500/220kV | 500/220kV | See Note 23B | 902149138 | COS-00-SP-TD-000000 | 7392 | See Note 27A | Yes | 2017 | Pre-2017 | FRM/CRT | No | N/A | N/A | N/A | See Col. 37 | 2019 = 1,122 2020 = 134 2021 = 174 2022 = -4 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2019-01-14 | No | 2018-12-31 | 2019-05-17 | Coordination with Other Work and Outages | 1278 | 1278 | See Note 53A | 1426.2906 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 367.4159 | 754.2506 | 134.4968 | 173.6912 | -3.5639 | 1426.2906 | 283.8743 | See Note 57A | N/A | No Cost Benefit performed. Analysis identified possible loss of functionality and potential repair cost and times that could be caused by an earthquake that can be avoided through retrofit of substation components | 5.5559e-13 | None | 100% | 0% | Column 9: Seismic mitigation Column 52: Source= Unverified system estimate
N/A | PB-25.12 | Windhub Substation Seismic Mitigation Project | 35.035, -118.281 | Mojave, Kern County | Windhub Substation: Seismic Mitigation Project 500kV Positions Positions 1N and 6N 220kV Positions -Positions 3, 4, 10, 11, 12, 13N and 13S, relocate the three (3) existing CCVT’s on new pedestal pole type support structures and new foundations. Install three (3) new weighted riser steel structures on the existing foundation. Install the CCVT’s with the required conduits and pull boxes as per latest SCE standards. Control Room -Install six (6) new frames with span of 10 ft maximum to reinforce the aluminum relay racks. The new frame support will be located at the front side of the relay racks. | Seismic | New, Relocate | None | Other - See Notes | Age/Condition | July 2016 : Note Inspection date is of seismic inspection and not compliance driven inspection date | 20+ years | Fragility and seismic analyses | The alternative option considered is to keep the substation as is and potentially recover post seismic event. This has no upfront cost. Cost incurred would be in recovery time and effort that varies by size of seismic event. | Non-HFRA | See Note 16C | Aside from typical weathering of components, seismic activity can impact retrofits, requiring re-inspection | Roderick Dela Cruz, Integrate System Strategy | See Note 19B | 59.2 | 500/220kV | 500/220kV | See Note 23B | 902214604 | COS-00-SP-TD-000000 | 7392 | See Note 27A | Yes | 2017 | Pre-2017 | FRM/CRT | No | N/A | N/A | N/A | See Col. 37 | 2019 = 800 2020 = 256 2021 = -23 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2019-10-14 | No | 2019-12-31 | 2019-12-06 | N/A | 1042 | 926.3931 | See Note 53A | 1033.5538 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 102.7817 | 697.6502 | 256.4181 | -23.2963 | 0 | 1033.5538 | 98.9476 | See Note 57A | N/A | No Cost Benefit performed. Analysis identified possible loss of functionality and potential repair cost and times that could be caused by an earthquake that can be avoided through retrofit of substation components | -6.9574e-13 | None | 100% | 0% | Column 9: Seismic mitigation Column 52: Source= Unverified system estimate
N/A | PB-25.13 | Barre Substation Seismic Mitigation Project | 33.809, -117.982 | Stanton, Orange County | Barre Substation: 220kV Positions -Positions 4,8,10,11, 12 and 13, relocate the three (3) existing CCVT’s on new pedestal pole type support structures and new foundations. Remove three (3) existing spring risers and foundations and replace with three (3) new weighted risers and foundations. -Position 9, replace the three (3) existing CCVT’s with three (3) new CCVT’s on new pedestal pole type support structures and new foundations, re-installing the required conduits and pull boxes as per latest SCE standards. Remove three (3) existing risers and foundations and replace with three (3) new weighted risers and foundations. -Install grounding for all new and re-installed structures and equipment per the latest SCE standards. 220kV Transformer Banks 1A Bank -Replace high side bushings -Upgrade anchorage to 1g -Brace radiator -Reconductor to add slack between three (3) 1A bank surge arresters and overhead conductors 3A Bank -Reconductor to add slack between the 3A bank transformer high side bushings and overhead conductors 4A Bank Transformer -Replace high side bushings -Reconductor to add slack between three (3) 4A bank surge arresters and overhead conductors 220kV North and South Operating Buses -Modify bus dead end structures to provide a brace and install triangular jumper assembly to a total of eighteen (18) suspended weights to limit sideways movement. -Relocate the three (3) existing CCVT’s on the North bus with new pedestal pole type support structures and new foundations. Remove three (3) existing spring risers and foundations and replace with three (3) new weighted risers and foundations. -Relocate the three (3) existing CCVT’s on the North bus with new pedestal pole type support structures and new foundations. Remove three (3) existing spring risers and foundations and replace with three (3) new weighted risers and foundations. Control Room/building -Install six (6) new frames with span of 10 FT maximum to re-enforce the relay racks. This new frame support will be located at the front side of the relay racks. | Barre Substation: 220kV Positions -Positions 4,8,10,11, 12 and 13, relocate the three (3) existing CCVT’s on new pedestal pole type support structures and new foundations. Remove three (3) existing spring risers and foundations and replace with three (3) new weighted risers and foundations. -Position 9, replace the three (3) existing CCVT’s with three (3) new CCVT’s on new pedestal pole type support structures and new foundations, re-installing the required conduits and pull boxes as per latest SCE standards. Remove three (3) existing risers and foundations and replace with three (3) new weighted risers and foundations. -Install grounding for all new and re-installed structures and equipment per the latest SCE standards. 220kV Transformer Banks 1A Bank -Replace high side bushings -Upgrade anchorage to 1g -Brace radiator -Reconductor to add slack between three (3) 1A bank surge arresters and overhead conductors 3A Bank -Reconductor to add slack between the 3A bank transformer high side bushings and overhead conductors 4A Bank Transformer -Replace high side bushings -Reconductor to add slack between three (3) 4A bank surge arresters and overhead conductors 220kV North and South Operating Buses -Modify bus dead end structures to provide a brace and install triangular jumper assembly to a total of eighteen (18) suspended weights to limit sideways movement. -Relocate the three (3) existing CCVT’s on the North bus with new pedestal pole type support structures and new foundations. Remove three (3) existing spring risers and foundations and replace with three (3) new weighted risers and foundations. -Relocate the three (3) existing CCVT’s on the North bus with new pedestal pole type support structures and new foundations. Remove three (3) existing spring risers and foundations and replace with three (3) new weighted risers and foundations. Control Room/building -Install six (6) new frames with span of 10 FT maximum to re-enforce the relay racks. This new frame support will be located at the front side of the relay racks. | New | None | Other - See Notes | Age/Condition | July 2016 : Note Inspection date is of seismic inspection and not compliance driven inspection date | 20+ years | Fragility and seismic analyses | The alternative option considered is to keep the substation as is and potentially recover post seismic event. This has no upfront cost. Cost incurred would be in recovery time and effort that varies by size of seismic event. | Non-HFRA | See Note 16C | Aside from typical weathering of components, seismic activity can impact retrofits, requiring re-inspection | Roderick Dela Cruz, Integrate System Strategy | See Note 19B | 13.8 | 220kV | 220 kV | See Note 23B | 902214367 | COS-00-SP-TD-000000 | 7392 | See Note 27A | Yes | 2017 | Pre-2017 | FRM/CRT | No | N/A | N/A | N/A | See Col.37 | 2022 = 4,854 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2019-05-01 | Yes | 2019-12-31 | 2022-05-27 | Coordination with Other Work and Outages | 2832 | 2832 | See Note 53A | 4854.2917 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 231.5718 | 1345.4711 | 1715.7635 | 1282.2054 | 279.2799 | 4854.2917 | 1683.148 | See Note 57A | N/A | No Cost Benefit performed. Analysis identified possible loss of functionality and potential repair cost and times that could be caused by an earthquake that can be avoided through retrofit of substation components | -1.2469e-12 | None | 100% | 0% | Column 9: Seismic mitigation Column 52: Source= Unverified system estimate
N/A | PB-25.14 | Valley Substation Seismic Mitigation Project | 33.740, -117.157 | Romoland, Riverside County | Valley Substation: 500kV Positions -Position 1X, reconductor to add slack between disconnect switch 71X3 and disconnect switch 91X3. -Position 3X, reconductor to add slack between disconnect switch 83X3 and disconnect switch 73X1. -Position 5X, reconductor to add slack between disconnect switch 85X1 and disconnect switch 75X3. -Position 6X, reconductor to add slack between disconnect switch 76X3 and adjacent bus supports. -Position 7XN, reconductor to add slack between disconnect switch 77X3 and disconnect switch 87X1. -Position 7XS, reconductor to add slack between disconnect switch 97X3 and adjacent bus supports. -Position 8X, reconductor to add slack between disconnect switch 98X3 and adjacent bus supports. -Position 9X, reconductor to add slack between disconnect switch 89X1 and adjacent bus supports near the line dead end. 500kV Busses -500kV North Bus: Brace twelve (12) weighted risers at top of bus dead end to prevent side sway with triangular insulators -500kV North Bus: Brace twelve (12) weighted risers at top of bus dead end to prevent side sway with triangular insulators | Valley Substation: 500kV Positions -Position 1X, reconductor to add slack between disconnect switch 71X3 and disconnect switch 91X3. -Position 3X, reconductor to add slack between disconnect switch 83X3 and disconnect switch 73X1. -Position 5X, reconductor to add slack between disconnect switch 85X1 and disconnect switch 75X3. -Position 6X, reconductor to add slack between disconnect switch 76X3 and adjacent bus supports. -Position 7XN, reconductor to add slack between disconnect switch 77X3 and disconnect switch 87X1. -Position 7XS, reconductor to add slack between disconnect switch 97X3 and adjacent bus supports. -Position 8X, reconductor to add slack between disconnect switch 98X3 and adjacent bus supports. -Position 9X, reconductor to add slack between disconnect switch 89X1 and adjacent bus supports near the line dead end. 500kV Busses -500kV North Bus: Brace twelve (12) weighted risers at top of bus dead end to prevent side sway with triangular insulators -500kV North Bus: Brace twelve (12) weighted risers at top of bus dead end to prevent side sway with triangular insulators | New | None | Other - See Notes | Age/Condition | August 2015 : Note Inspection date is of seismic inspection and not compliance driven inspection date | 20+ years | Fragility and seismic analyses | The alternative option considered is to keep the substation as is and potentially recover post seismic event. This has no upfront cost. Cost incurred would be in recovery time and effort that varies by size of seismic event. | Non-HFRA | See Note 16C | Aside from typical weathering of components, seismic activity can impact retrofits, requiring re-inspection | Roderick Dela Cruz, Integrate System Strategy | See Note 19B | 57.4 | See Note 21A | 500 kV, 115 kV, 33 kV, 12 kV | See Note 23B | 902214600 | COS-00-SP-TD-000000 | 7392 | See Note 27A | Yes | 2017 | Pre-2017 | FRM/CRT | No | N/A | N/A | N/A | See Col. 37 | 2020 = 1,375 2022 = -201 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2019-04-22 | No | 2019-12-31 | 2020-02-28 | N/A | 2646 | 1024.7543 | See Note 53A | 1173.8097 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 103.0438 | 1227.3344 | 44.5332 | 0.34047 | -201.4421 | 1173.8097 | 238.8808 | See Note 57A | N/A | No Cost Benefit performed. Analysis identified possible loss of functionality and potential repair cost and times that could be caused by an earthquake that can be avoided through retrofit of substation components | -5.1602e-14 | None | 100% | 0% | Column 9: Seismic mitigation Column 52: Source= Unverified system estimate
N/A | PB-25.15 | Victor Substation Seismic Mitigation | 34.505936, -117.38768 | Victorville, San Bernardino County | Victor Sub: 220/115kV Transformers 1. Bank No.3 a. Upgrade anchorage 220kV Positions 1. Position 2N-Caldwell | Victor Sub: 220/115kV Transformers 1. Bank No.3 a. Upgrade anchorage 220kV Positions 1. Position 2N-Caldwell | New | None | Other - See Notes | Age/Condition | June 2016 : Note Inspection date is of seismic inspection and not compliance driven inspection date | 20+ years | Fragility and seismic analyses | The alternative option considered is to keep the substation as is and potentially recover post seismic event. This has no upfront cost. Cost incurred would be in recovery time and effort that varies by size of seismic event. | Non-HFRA | See Note 16C | Aside from typical weathering of components, seismic activity can impact retrofits, requiring re-inspection | Roderick Dela Cruz, Integrate System Strategy | See Note 19B | 33.3 | See Note 21A | 220kV, 115kV and 33kV | See Note 23B | 902391704 | COS-00-SP-TD-000000 | 7392 | See Note 27A | Yes | 2017 | 2017 | FRM/CRT | No | N/A | N/A | N/A | See Col. 37 | 2021 = 1,515 2022 = 38 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2020-08-31 | No | 2020-12-31 | 2021-04-16 | N/A | 1545 | 1545 | See Note 53A | 1552.8513 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 7.9973 | 103.7946 | 1145.9284 | 257.4897 | 37.6413 | 1552.8513 | 237.3683 | See Note 57A | N/A | See Note 59A | -1.0448e-12 | None | 100% | 0% | Column 9: Seismic mitigation Column 36 & 37: Not operational at time of data pull (late March) Column 52: Source= PMWIF (v0 Proj Summary)
N/A | PB-25.16 | Alamitos Seismic Mitigation | 33.772, -118.101 | Long Beach, Los Angeles County | Alamitos Sub: 220kV Positions 1. Position 5 – Lighthipe a. Replace three (3) existing CCVT on new pedestal pole type support structures and new foundations. b. Remove three (3) existing risers and foundations and replace with three (3) new weighted risers and foundations. | Alamitos Sub: 220kV Positions 1. Position 5 – Lighthipe a. Replace three (3) existing CCVT on new pedestal pole type support structures and new foundations. b. Remove three (3) existing risers and foundations and replace with three (3) new weighted risers and foundations. | New | None | Other - See Notes | Age/Condition | May 2016 : Note Inspection date is of seismic inspection and not compliance driven inspection date | 20+ years | Fragility and seismic analyses | The alternative option considered is to keep the substation as is and potentially recover post seismic event. This has no upfront cost. Cost incurred would be in recovery time and effort that varies by size of seismic event. | Non-HFRA | See Note 16C | Aside from typical weathering of components, seismic activity can impact retrofits, requiring re-inspection | Roderick Dela Cruz, Integrate System Strategy | See Note 19B | 22.5 | See Note 21A | 220kV and 66kV | See Note 23B | 902506173 | COS-00-SP-TD-000000 | 7392 | See Note 27A | Yes | 2017 | 2017 | FRM/CRT | No | N/A | N/A | N/A | See Col. 37 | 2020 = 2,120 2021 = 328 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2020-04-22 | No | 2020-12-31 | 2020-11-05 | N/A | 1335 | 1335 | See Note 53A | 2447.756 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 0.5743 | 345.0246 | 1773.9325 | 328.2246 | 0 | 2447.756 | 344.1776 | See Note 57A | N/A | See Note 59A | -4.7066e-13 | None | 100% | 0% | Column 9: Seismic mitigation Column 52: Source= PMWIF (v0 Proj Summary)
N/A | PB-25.17 | Olinda Seismic Mitigation | 33.946164, -117.921303 | La Habra, Los Angeles County | Olinda 220/66 - Seismic Mitigation project. Please see PMWIF for more details. 220kV Positions 1. Position 1E – Bank No.1A a. Reconductor to add slack between tie downs and adjacent disconnect switches | Olinda 220/66 - Seismic Mitigation project. Please see PMWIF for more details. 220kV Positions 1. Position 1E – Bank No.1A a. Reconductor to add slack between tie downs and adjacent disconnect switches | New | None | Other - See Notes | Age/Condition | July 2016 : Note Inspection date is of seismic inspection and not compliance driven inspection date | 20+ years | Fragility and seismic analyses | The alternative option considered is to keep the substation as is and potentially recover post seismic event. This has no upfront cost. Cost incurred would be in recovery time and effort that varies by size of seismic event. | Tier 2 | See Note 16C | Aside from typical weathering of components, seismic activity can impact retrofits, requiring re-inspection | Roderick Dela Cruz, Integrate System Strategy | See Note 19B | 11.5 | See Note 21A | 220kV, 115kV and 12kV | See Note 23B | 902506491 | COS-00-SP-TD-000000 | 7392 | See Note 27A | Yes | 2017 | 2017 | FRM/CRT | No | N/A | N/A | N/A | See Col. 37 | 2020 = 1,072 2021 = 24 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2020-05-12 | No | 2020-12-31 | 2020-11-05 | N/A | 1115 | 1048.1 | See Note 53A | 1096.5022 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 3.4816 | 234.8446 | 834.1151 | 24.0609 | 0 | 1096.5022 | 242.2434 | See Note 57A | N/A | See Note 59A | 1.5944e-13 | None | 100% | 0% | Column 9: Seismic mitigation Column 52: Source= PMWIF (v0 Proj Summary)
N/A | PB-25.18 | Rio Honda Seismic Mitigation | 34.105, -117.981 | Irwindale, Los Angeles County | Rio Hondo Sub: 220kV Positions 1. Position 45 - Laguna Bell a. Replace three (3) existing CCVT on new pedestal pole type support structures and new foundations. b. Remove three (3) existing risers and foundations and replace with three (3) new weighted risers and foundations. | Rio Hondo Sub: 220kV Positions 1. Position 45 - Laguna Bell a. Replace three (3) existing CCVT on new pedestal pole type support structures and new foundations. b. Remove three (3) existing risers and foundations and replace with three (3) new weighted risers and foundations. | New | None | Other - See Notes | Age/Condition | June 2016 : Note Inspection date is of seismic inspection and not compliance driven inspection date | 20+ years | Fragility and seismic analyses | The alternative option considered is to keep the substation as is and potentially recover post seismic event. This has no upfront cost. Cost incurred would be in recovery time and effort that varies by size of seismic event. | Non-HFRA | See Note 16C | Aside from typical weathering of components, seismic activity can impact retrofits, requiring re-inspection | Roderick Dela Cruz, Integrate System Strategy | See Note 19B | 21.1 | See Note 21A | 220kV and 66kV | See Note 23B | 902506607 | COS-00-SP-TD-000000 | 7392 | See Note 27A | Yes | 2017 | 2018 | FRM/CRT | No | N/A | N/A | N/A | See Col. 37 | 2021 = 2,325 2022 = 47 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2020-10-01 | No | 2020-12-31 | 2021-04-19 | N/A | 840 | 840 | See Note 53A | 2372.091 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 0 | 370.0818 | 1339.5994 | 615.803 | 46.6068 | 2372.091 | 258.782 | See Note 57A | N/A | See Note 59A | 9.9618e-14 | None | 100% | 0% | Column 9: Seismic mitigation Column 36 & 37: Not operational at time of data pull (late March) Column 52: Source= PMWIF (v0 Proj Summary)
N/A | PB-25.19 | Springville Seismic Mitigation | 36.108, -118.938 | Porterville, Tulare County | Springville Sub: 2. Position 3S – Rector a. Relocate three (3) existing CCVTs on new pedestal pole type support structures and new foundations. b. Remove three (3) existing risers and foundations and replace with three (3) new weighted risers and foundations. c. Relocate pull box per latest SCE standards. 3. Position 4S – No.2A Bank a. Reconductor to add slack between tie downs and disconnect switches. 4. Position 5S – Magunden No.1 a. Replace three (3) existing CCVTs on new pedestal pole type support structures and new foundations. b. Remove three (3) existing risers and foundations and replace with three (3) new weighted risers and foundations. c. Relocate pull box per latest SCE standards | Springville Sub: 2. Position 3S – Rector a. Relocate three (3) existing CCVTs on new pedestal pole type support structures and new foundations. b. Remove three (3) existing risers and foundations and replace with three (3) new weighted risers and foundations. c. Relocate pull box per latest SCE standards. 3. Position 4S – No.2A Bank a. Reconductor to add slack between tie downs and disconnect switches. 4. Position 5S – Magunden No.1 a. Replace three (3) existing CCVTs on new pedestal pole type support structures and new foundations. b. Remove three (3) existing risers and foundations and replace with three (3) new weighted risers and foundations. c. Relocate pull box per latest SCE standards | New | None | Other - See Notes | Age/Condition | July 2016 : Note Inspection date is of seismic inspection and not compliance driven inspection date | 20+ years | Fragility and seismic analyses | The alternative option considered is to keep the substation as is and potentially recover post seismic event. This has no upfront cost. Cost incurred would be in recovery time and effort that varies by size of seismic event. | Tier 2 | See Note 16C | Aside from typical weathering of components, seismic activity can impact retrofits, requiring re-inspection. Moderate Seismic Area | Roderick Dela Cruz, Integrate System Strategy | See Note 19B | 10.4 | See Note 21A | 220kV and 66kV | See Note 23B | 902506610 | COS-00-SP-TD-000000 | 7392 | See Note 27A | Yes | 2017 | 2018 | FRM/CRT | No | N/A | N/A | N/A | See Col. 37 | 2021 = 1,363 2022 = 2 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2020-11-23 | No | 2020-12-31 | 2021-01-26 | N/A | 840 | 840 | See Note 53A | 1364.7401 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 0 | 44.3388 | 1009.7299 | 309.1464 | 1.525 | 1364.7401 | 148.4991 | See Note 57A | N/A | See Note 59A | 9.8998e-13 | None | 100% | 0% | Column 9: Seismic mitigation Column 52: Source= PMWIF (v0 Proj Summary)
N/A | PB-25.20 | DEL AMO SEISMIC MITI | 33.848225, -118.097168 | Cerritos, Los Angeles County | Del Amo Sub: 220kV Positions 1. Position 1 - Hinson a. Replace three (3) existing CCVTs and three (3) TRVs on new pedestal pole type support structures and new foundations. a. Remove three (3) existing risers and foundations and replace with three (3) new weighted risers and foundations. | Del Amo Sub: 220kV Positions 1. Position 1 - Hinson a. Replace three (3) existing CCVTs and three (3) TRVs on new pedestal pole type support structures and new foundations. a. Remove three (3) existing risers and foundations and replace with three (3) new weighted risers and foundations. | New | None | Other - See Notes | Age/Condition | July 2016 : Note Inspection date is of seismic inspection and not compliance driven inspection date | 20+ years | Fragility and seismic analyses | The alternative option considered is to keep the substation as is and potentially recover post seismic event. This has no upfront cost. Cost incurred would be in recovery time and effort that varies by size of seismic event. | Non-HFRA | See Note 16C | Aside from typical weathering of components, seismic activity can impact retrofits, requiring re-inspection | Roderick Dela Cruz, Integrate System Strategy | See Note 19B | 15 | See Note 21A | 220kV, 66kV and 16kV | See Note 23B | 902506619 | COS-00-SP-TD-000000 | 7392 | See Note 27A | Yes | 2017 | 2017 | FRM/CRT | No | N/A | N/A | N/A | See Col. 37 | 2021 = 2,007 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2020-08-10 | No | 2020-12-31 | 2021-02-19 | N/A | 1775 | 1519.4 | See Note 53A | 2007.3915 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 1.1463 | 106.9072 | 1504.5604 | 394.5541 | 0.22354 | 2007.3915 | 482.9568 | See Note 57A | N/A | See Note 59A | -4.4065e-13 | None | 100% | 0% | Column 9: Seismic mitigation Column 52: Source= PMWIF (v0 Proj Summary)
N/A | PB-25.21 | Moorpark Substation Seismic Mitigation Project | 34.280609;-118.903093 | Moorpark, Ventura County | Moorpark Sub - Seismic Mitigation Project Reconductor/Slack: 200kV Pos. 3, 6, 7, 11S, 12N, 12S three (3) existing weight-type tie downs shall be modified to field weld steel tabs to the existing structure to support new weights. 220kV Pos. 4, 11N, 13 each replace three (3) spring type tie downs with three (3) weight-type tie downs w/new foundations 200kV Pos. 7, 11N, 11S, 13 each Install three (3) CCVTs on new steel pedestal structures w/new foundation 200kV Pos. 8, 9, 12 each Install six (6) CCVTs on new steel pedestal structures w/new foundations. 200kV Pos. 8, 9, 11N, 12N, 12S each C-phase wave trap and tuner on support structure and foundation | Moorpark Sub - Seismic Mitigation Project Reconductor/Slack: 200kV Pos. 3, 6, 7, 11S, 12N, 12S three (3) existing weight-type tie downs shall be modified to field weld steel tabs to the existing structure to support new weights. 220kV Pos. 4, 11N, 13 each replace three (3) spring type tie downs with three (3) weight-type tie downs w/new foundations 200kV Pos. 7, 11N, 11S, 13 each Install three (3) CCVTs on new steel pedestal structures w/new foundation 200kV Pos. 8, 9, 12 each Install six (6) CCVTs on new steel pedestal structures w/new foundations. 200kV Pos. 8, 9, 11N, 12N, 12S each C-phase wave trap and tuner on support structure and foundation | New | None | Other - See Notes | Age/Condition | July 2016 : Note Inspection date is of seismic inspection and not compliance driven inspection date | 20+ years | Fragility and seismic analyses | The alternative option considered is to keep the substation as is and potentially recover post seismic event. This has no upfront cost. Cost incurred would be in recovery time and effort that varies by size of seismic event. | Tier 3 | See Note 16C | Aside from typical weathering of components, seismic activity can impact retrofits, requiring re-inspection | Roderick Dela Cruz, Integrate System Strategy | See Note 19B | 40 | See Note 21A | 220kV/66kV/12kV | See Note 23B | 902149133 | COS-00-SP-TD-000000 | 7392 | See Note 27A | Yes | 2017 | Pre-2018 | FRM/CRT | No | N/A | N/A | N/A | See Col.37 | 2019 = 3,410 2020 = 40 2021 = 1 2022 = 2 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2018-08-20 | No | 2019-12-31 | 2019-04-02 | Difficulties in Design and Coordination | 1531.037 | 1531.037 | See Note 53A | 3451.9866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2436.4874 | 973.2179 | 39.9532 | 0.65021 | 1.6779 | 3451.9866 | 725.4733 | See Note 57A | N/A | See Note 59A | -2.8878e-12 | None | 100% | 0% | Column 52: Source = PMWIF (V.0 Project Summary)
N/A | PB-25.22 | El Nido Substation Seismic Mitigation Project | 33.895426;-118.371913 | Hawthorne, Los Angeles County | El Nido Substation: 220kV Positions -Position 1, replace the three (3) existing CCVT’s with three (3) new CCVT’s on new pedestal pole type support structures and new foundations, install the required conduits and pull boxes as per latest SCE standards. Remove three (3) existing risers and foundations and replace with three (3) new weighted risers and foundations. -Positions 2, and 9, relocate the three (3) existing CCVT’s on new pedestal pole type support structures and new foundations. Remove three (3) existing risers and foundations and replace with three (3) new weighted risers and foundations. Install the CCVT’s with the required conduits and pull boxes as per latest SCE standards. -Position 8, relocate the three (3) existing CCVT’s on new pedestal pole type support structures and new foundations. Remove three (3) existing risers and foundations and replace with three (3) new weighted risers and foundations. Install the CCVT’s with the required conduits and pull boxes as per latest SCE standards. Reconductor to add slack between the North bus surge arresters and the adjacent disconnect switch on two phases. -Position 1X, replace the three (3) existing CCVT’s with three (3) new CCVT’s on new pedestal pole type support structures and new foundations, install the required conduits and pull boxes as per latest SCE standards. Remove three (3) existing risers and foundations and replace with three (3) new weighted risers and foundations. Reconductor to add slack between the A-phase bus support under the North 220kv bus and the adjacent disconnect switch 220kV Transformer -Spare A transformer: Anchor spare transformer for 1g 220kV Busses -220kV North Bus: Brace nine (9) weighted risers at top of bus dead end to prevent side sway with triangular insulators -220kV South Bus: Brace three (3) weighted risers at top of bus dead end to prevent side sway with triangular insulators 220kV Capacitor bank -Reconductor to add slack between the cap bank CB and the adjacent surge arresters | El Nido Substation: 220kV Positions -Position 1, replace the three (3) existing CCVT’s with three (3) new CCVT’s on new pedestal pole type support structures and new foundations, install the required conduits and pull boxes as per latest SCE standards. Remove three (3) existing risers and foundations and replace with three (3) new weighted risers and foundations. -Positions 2, and 9, relocate the three (3) existing CCVT’s on new pedestal pole type support structures and new foundations. Remove three (3) existing risers and foundations and replace with three (3) new weighted risers and foundations. Install the CCVT’s with the required conduits and pull boxes as per latest SCE standards. -Position 8, relocate the three (3) existing CCVT’s on new pedestal pole type support structures and new foundations. Remove three (3) existing risers and foundations and replace with three (3) new weighted risers and foundations. Install the CCVT’s with the required conduits and pull boxes as per latest SCE standards. Reconductor to add slack between the North bus surge arresters and the adjacent disconnect switch on two phases. -Position 1X, replace the three (3) existing CCVT’s with three (3) new CCVT’s on new pedestal pole type support structures and new foundations, install the required conduits and pull boxes as per latest SCE standards. Remove three (3) existing risers and foundations and replace with three (3) new weighted risers and foundations. Reconductor to add slack between the A-phase bus support under the North 220kv bus and the adjacent disconnect switch 220kV Transformer -Spare A transformer: Anchor spare transformer for 1g 220kV Busses -220kV North Bus: Brace nine (9) weighted risers at top of bus dead end to prevent side sway with triangular insulators -220kV South Bus: Brace three (3) weighted risers at top of bus dead end to prevent side sway with triangular insulators 220kV Capacitor bank -Reconductor to add slack between the cap bank CB and the adjacent surge arresters | New | None | Other - See Notes | Age/Condition | July 2016 : Note Inspection date is of seismic inspection and not compliance driven inspection date | 20+ years | Fragility and seismic analyses | The alternative option considered is to keep the substation as is and potentially recover post seismic event. This has no upfront cost. Cost incurred would be in recovery time and effort that varies by size of seismic event. | Not applicable - No HFRA | See Note 16C | Aside from typical weathering of components, seismic activity can impact retrofits, requiring re-inspection | Roderick Dela Cruz, Integrate System Strategy | See Note 19B | 13.6 | See Note 21A | 220kV/66kV/12kV | See Note 23B | 902214370 | COS-00-SP-TD-000000 | 7392 | See Note 27A | Yes | 2017 | Pre-2018 | FRM/CRT | No | N/A | N/A | N/A | See Col. 37 | 2019 = 1,311 2020 = 24 2021 = -117 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2018-08-20 | No | 2019-12-31 | 2019-04-03 | N/A | 1004.232 | 1004.232 | See Note 53A | 1217.4385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 195.6161 | 1115.0996 | 23.553 | -116.9496 | 0.1194 | 1217.4385 | 256.123 | See Note 57A | N/A | See Note 59A | -1.2274e-12 | None | 100% | 0% | Column 52: Source = PMWIF (V.0 Project Summary)
N/A | PB-25.23 | Ellis Substation Seismic Mitigation Project | 33.685538;-117.942986 | Huntington Beach, Orange County | Ellis Substation: 220kV North and South Operating Buses -Modify bus dead end structures to provide a brace and install triangular jumper assembly to a total of twelve (12) suspended weights to limit sideways movement. Control Room/building -Install six (6) new frames with span of 10 FT maximum to re-inforce the relay racks. | Ellis Substation: 220kV North and South Operating Buses -Modify bus dead end structures to provide a brace and install triangular jumper assembly to a total of twelve (12) suspended weights to limit sideways movement. Control Room/building -Install six (6) new frames with span of 10 FT maximum to re-inforce the relay racks. | New | None | Other - See Notes | Age/Condition | July 2016 : Note Inspection date is of seismic inspection and not compliance driven inspection date | 20+ years | Fragility and seismic analyses | The alternative option considered is to keep the substation as is and potentially recover post seismic event. This has no upfront cost. Cost incurred would be in recovery time and effort that varies by size of seismic event. | Not applicable - No HFRA | See Note 16C | Aside from typical weathering of components, seismic activity can impact retrofits, requiring re-inspection | Roderick Dela Cruz, Integrate System Strategy | See Note 19B | 13.1 | See Note 21A | 220kV/66kV/12kV | See Note 23B | 902214371 | COS-00-SP-TD-000000 | 7392 | See Note 27A | Yes | 2017 | Pre-2018 | FRM/CRT | No | N/A | N/A | N/A | See Col. 37 | 2019 = 2,314 2020 = 171 2021 = 3 2022 = 3 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2019-05-20 | No | 2019-12-31 | 2019-12-11 | N/A | 2395.397 | 2131.9033 | See Note 53A | 2490.4371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 654.6967 | 1659.4769 | 171.0498 | 2.5853 | 2.6284 | 2490.4371 | 760.1117 | See Note 57A | N/A | See Note 59A | -4.6884e-13 | None | 100% | 0% | Column 52: Source = PMWIF (V.0 Project Summary)
N/A | PB-25.24 | Etiwanda Substation Seismic Mitigation Project | 34.088956;-117.527584 | Rancho Cucamonga, San Bernardino County | Etiwanda Substation: 220kV North and South Operating Buses -Replace the two (2) existing CCVT’s on new pedestal pole type support structures, re-installing the CCVT’s with the required conduits and pull boxes as per latest SCE standards. -A new foundation will be required for the pedestals. -Modify buses dead end structures to provide braces to total of twelve (12) suspended weights to limit sideways movement. -Install grounding for all new and re-installed structures and equipment according to the latest SCE standards. | Etiwanda Substation: 220kV North and South Operating Buses -Replace the two (2) existing CCVT’s on new pedestal pole type support structures, re-installing the CCVT’s with the required conduits and pull boxes as per latest SCE standards. -A new foundation will be required for the pedestals. -Modify buses dead end structures to provide braces to total of twelve (12) suspended weights to limit sideways movement. -Install grounding for all new and re-installed structures and equipment according to the latest SCE standards. | New | None | Other - See Notes | Age/Condition | July 2016 : Note Inspection date is of seismic inspection and not compliance driven inspection date | 20+ years | Fragility and seismic analyses | The alternative option considered is to keep the substation as is and potentially recover post seismic event. This has no upfront cost. Cost incurred would be in recovery time and effort that varies by size of seismic event. | Not applicable - No HFRA | See Note 16C | Aside from typical weathering of components, seismic activity can impact retrofits, requiring re-inspection | Roderick Dela Cruz, Integrate System Strategy | See Note 19B | 14.44 | See Note 21A | 220kV/66kV | See Note 23B | 902214372 | COS-00-SP-TD-000000 | 7392 | See Note 27A | Yes | 2017 | Pre-2018 | FRM/CRT | No | N/A | N/A | N/A | See Col. 37 | 2019 = 1,499 2020 = 283 2021 = 1 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2019-04-10 | No | 2019-12-31 | 2019-12-23 | N/A | 2450.47 | 2279.9173 | See Note 53A | 1782.7312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340.8394 | 1158.6214 | 282.7075 | 0.56285 | 9.304e-06 | 1782.7312 | 304.6749 | See Note 57A | N/A | See Note 59A | 2.3231e-13 | None | 100% | 0% | Column 52: Source = PMWIF (V.0 Project Summary)
N/A | PB-25.25 | Hinson Substation Seismic Mitigation Project | 33.818287;-118.222465 | Long Beach, Los Angeles County | Hinson Substation: 220kV Positions -Position 8N, replace the three (3) existing CCVT’s with three (3) new CCVT’s on new pedestal pole type support structures and new foundations, install the required conduits and pull boxes as per latest SCE standards. Remove three (3) existing risers and foundations and replace with three (3) new weighted risers and foundations. Reconductor to add slack between the disconnect switch south of Arcogen No. 2 line drop and disconnect switch north of Arcogen line drop. Reconductor to add slack between disconnect switch north of CB 482 and adjacent A-phase bus support under 220kv bus. -Position 8S, replace the three (3) existing CCVT’s with three (3) new CCVT’s on new pedestal pole type support structures and new foundations, install the required conduits and pull boxes as per latest SCE standards. Remove three (3) existing risers and foundations and replace with three (3) new weighted risers and foundations. -Position 9, relocate the three (3) existing CCVT’s on new pedestal pole type support structures and new foundations. Install the CCVT’s with the required conduits and pull boxes as per latest SCE standards. Reconductor to add slack between bus support under north 220kv bus and bus supports adjacent to 220kv disconnect switch. SL&P Transformer -Strengthen existing support 220kV Busses -220kV North Bus: Brace three (3) weighted risers at top of bus dead end to prevent side sway with triangular insulators -220kV South Bus: Brace nine (9) weighted risers at top of bus dead end to prevent side sway with triangular insulators | Hinson Substation: 220kV Positions -Position 8N, replace the three (3) existing CCVT’s with three (3) new CCVT’s on new pedestal pole type support structures and new foundations, install the required conduits and pull boxes as per latest SCE standards. Remove three (3) existing risers and foundations and replace with three (3) new weighted risers and foundations. Reconductor to add slack between the disconnect switch south of Arcogen No. 2 line drop and disconnect switch north of Arcogen line drop. Reconductor to add slack between disconnect switch north of CB 482 and adjacent A-phase bus support under 220kv bus. -Position 8S, replace the three (3) existing CCVT’s with three (3) new CCVT’s on new pedestal pole type support structures and new foundations, install the required conduits and pull boxes as per latest SCE standards. Remove three (3) existing risers and foundations and replace with three (3) new weighted risers and foundations. -Position 9, relocate the three (3) existing CCVT’s on new pedestal pole type support structures and new foundations. Install the CCVT’s with the required conduits and pull boxes as per latest SCE standards. Reconductor to add slack between bus support under north 220kv bus and bus supports adjacent to 220kv disconnect switch. SL&P Transformer -Strengthen existing support 220kV Busses -220kV North Bus: Brace three (3) weighted risers at top of bus dead end to prevent side sway with triangular insulators -220kV South Bus: Brace nine (9) weighted risers at top of bus dead end to prevent side sway with triangular insulators | New | None | Other - See Notes | Age/Condition | July 2016 : Note Inspection date is of seismic inspection and not compliance driven inspection date | 20+ years | Fragility and seismic analyses | The alternative option considered is to keep the substation as is and potentially recover post seismic event. This has no upfront cost. Cost incurred would be in recovery time and effort that varies by size of seismic event. | Non-HFRA | See Note 16C | Aside from typical weathering of components, seismic activity can impact retrofits, requiring re-inspection | Roderick Dela Cruz, Integrate System Strategy | See Note 19B | 12.2 | See Note 21A | 220kV/66kV | See Note 23B | 902214374 | COS-00-SP-TD-000000 | 7392 | See Note 27A | Yes | 2017 | Pre-2018 | FRM/CRT | No | N/A | N/A | N/A | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Construction more than 50% completed | See Note 46A | 2018-11-12 | No | 2019-12-31 | 2024-12-31 | Outage Coordination with Customer Substations | 1851.645 | 1296.1515 | See Note 53A | 2773.4739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 499.9758 | 507.4781 | 1236.3179 | 479.3714 | 50.3306 | 2773.4739 | 580.6491 | See Note 57A | N/A | See Note 59A | 2450.0895 | None | 100% | 0% | Column 52: Source = PMWIF (V.0 Project Summary)
N/A | PB-25.26 | La Fresa Substation Seismic Mitigation Project | 33.869437;-118.333165 | Torrance, Los Angeles County | 1.1PROJECT OBJECTIVE To revise CCVT/TRV mounting and provide slack to bus support cables in accordance with the latest Seismic Mitigation recommendations.1.2GENERAL SCOPE AND DESCRIPTION OF PROJECTA.Replace the three (3) existing coupling capacitor voltage transformers (CCVTs) on new pedestal pole-type support structures and foundations for each 220 kV Positions 3X and4.B.Relocate the three (3) existing CCVTs on new pedestal pole-type support structures and foundations for each 220 kV Positions 1X,2, 2X, 9, and 10. | 1.1PROJECT OBJECTIVE To revise CCVT/TRV mounting and provide slack to bus support cables in accordance with the latest Seismic Mitigation recommendations.1.2GENERAL SCOPE AND DESCRIPTION OF PROJECT A.Replace the three (3) existing coupling capacitor voltage transformers (CCVTs) on new pedestal pole-type support structures and foundations for each 220 kV Positions 3X and4.B.Relocate the three (3) existing CCVTs on new pedestal pole-type support structures and foundations for each 220 kV Positions 1X,2, 2X, 9, and 10. | New | None | Other - See Notes | Age/Condition | July 2016 : Note Inspection date is of seismic inspection and not compliance driven inspection date | 20+ years | Fragility and seismic analyses | The alternative option considered is to keep the substation as is and potentially recover post seismic event. This has no upfront cost. Cost incurred would be in recovery time and effort that varies by size of seismic event. | Not applicable - No HFRA | See Note 16C | Aside from typical weathering of components, seismic activity can impact retrofits, requiring re-inspection | Roderick Dela Cruz, Integrate System Strategy | See Note 19B | 22.7 | See Note 21A | 220kV/66kV | See Note 23B | 902214375 | COS-00-SP-TD-000000 | 7392 | See Note 27A | Yes | 2017 | Pre-2018 | FRM/CRT | No | N/A | N/A | N/A | See Col.37 | 2019 = 2,113 2020 = -73 2021 = -122 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Completed | See Note 46A | 2018-11-12 | No | 2019-12-31 | 2019-12-10 | Outage Coordination with Customer Substations | 1124.281 | 1124.281 | See Note 53A | 1917.7646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 309.2339 | 1803.8761 | -73.3257 | -122.0195 | 0 | 1917.7646 | 259.9228 | See Note 57A | N/A | See Note 59A | 2.1779e-13 | None | 100% | 0% | Column 52: Source = PMWIF (V.0 Project Summary)
N/A | PB-25.27 | Vista Substation Seismic Mitigation Project | 34.04042;-117.320291 | Grand Terrace, San Bernardino County | 220kV Busses -220kV North Bus: Brace nine (9) weighted risers at top of bus dead end to prevent side sway with triangular insulators -220kV South Bus: Brace nine (9) weighted risers at top of bus dead end to prevent side sway with triangular insulators | 220kV Busses -220kV North Bus: Brace nine (9) weighted risers at top of bus dead end to prevent side sway with triangular insulators -220kV South Bus: Brace nine (9) weighted risers at top of bus dead end to prevent side sway with triangular insulators | New | None | Other - See Notes | Age/Condition | July 2016 : Note Inspection date is of seismic inspection and not compliance driven inspection date | 20+ years | Fragility and seismic analyses | The alternative option considered is to keep the substation as is and potentially recover post seismic event. This has no upfront cost. Cost incurred would be in recovery time and effort that varies by size of seismic event. | HFTD Tier 2 | See Note 16C | Aside from typical weathering of components, seismic activity can impact retrofits, requiring re-inspection | Roderick Dela Cruz, Integrate System Strategy | See Note 19B | 29.3 | See Note 21A | 220kV/115kV/66kV | See Note 23B | 902214601 | COS-00-SP-TD-000000 | 7392 | See Note 27A | Yes | 2017 | Pre-2018 | FRM/CRT | No | N/A | N/A | N/A | See Col. 37 | 2019 = 1,177 2020 = 369 2021 = 476 2022 = 16 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2019-03-11 | No | 2019-12-31 | 2019-12-11 | N/A | 3296.399 | 2703.0472 | See Note 53A | 2037.9631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168.0842 | 1008.6021 | 368.8206 | 476.2978 | 16.1584 | 2037.9631 | 406.6292 | See Note 57A | N/A | See Note 59A | -1.4507e-13 | None | 100% | 0% | Column 52: Source = PMWIF (V.0 Project Summary)
N/A | PB-25.28 | Walnut Substation Seismic Mitigation Project | 34.007905;-117.949704 | City of Industry, Los Angeles County | Walnut Substation: 220kV Positions -Positions 1X, relocate the three (3) existing CCVT’s on new pedestal pole type support structures and new foundations. Install three (3) new weighted riser steel structures on the existing foundation. Install the CCVT’s with the required conduits and pull boxes as per latest SCE standards. -Position 3, reconductor to add slack between the two disconnect switches adjacent to the line dead end. -Position 6, reconductor to add slack between the risers under the line dead end and the disconnect switch adjacent to the line dead end. -Position 2 and 7, replace the three (3) existing CCVT’s with three (3) new CCVT’s on new pedestal pole type support structures and new foundations, install the required conduits and pull boxes as per latest SCE standards. Remove three (3) existing risers and foundations and replace with three (3) new weighted risers and foundations. -Positions 8, replace the three (3) existing CCVT’s with three (3) new CCVT’s on new pedestal pole type support structures and new foundations, installing the required conduits and pull boxes as per latest SCE standards. Remove three (3) existing risers and foundations and replace with three (3) new weighted risers and foundations. | Walnut Substation: 220kV Positions -Positions 1X, relocate the three (3) existing CCVT’s on new pedestal pole type support structures and new foundations. Install three (3) new weighted riser steel structures on the existing foundation. Install the CCVT’s with the required conduits and pull boxes as per latest SCE standards. -Position 3, reconductor to add slack between the two disconnect switches adjacent to the line dead end. -Position 6, reconductor to add slack between the risers under the line dead end and the disconnect switch adjacent to the line dead end. -Position 2 and 7, replace the three (3) existing CCVT’s with three (3) new CCVT’s on new pedestal pole type support structures and new foundations, install the required conduits and pull boxes as per latest SCE standards. Remove three (3) existing risers and foundations and replace with three (3) new weighted risers and foundations. -Positions 8, replace the three (3) existing CCVT’s with three (3) new CCVT’s on new pedestal pole type support structures and new foundations, installing the required conduits and pull boxes as per latest SCE standards. Remove three (3) existing risers and foundations and replace with three (3) new weighted risers and foundations. | New | None | Other - See Notes | Age/Condition | July 2016 : Note Inspection date is of seismic inspection and not compliance driven inspection date | 20+ years | Fragility and seismic analyses | The alternative option considered is to keep the substation as is and potentially recover post seismic event. This has no upfront cost. Cost incurred would be in recovery time and effort that varies by size of seismic event. | Not applicable - No HFRA | See Note 16C | Aside from typical weathering of components, seismic activity can impact retrofits, requiring re-inspection | Roderick Dela Cruz, Integrate System Strategy | See Note 19B | 14.3 | See Note 21A | 220kV/66kV/12kV | See Note 23B | 902214602 | COS-00-SP-TD-000000 | 7392 | See Note 27A | Yes | 2017 | Pre-2018 | FRM/CRT | No | N/A | N/A | N/A | See Col. 37 | 2021 = 1,800 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2019-06-13 | No | 2019-12-31 | 2021-12-19 | Material Delays and Outage Constraints | 1855.875 | 1818.7575 | See Note 53A | 1800.1527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 447.1272 | 1378.6728 | -28.82 | 2.8425 | 0.33029 | 1800.1527 | 325.499 | See Note 57A | N/A | See Note 59A | -2.9037e-13 | None | 100% | 0% | Column 52: Source = PMWIF (V.0 Project Summary)
N/A | PB-25.29 | Goleta Substation Seismic Mitigation Project | 34.468104;-119.883939 | Goleta, Santa Barbara County | Goleta Substation: 220kV Positions -Position 2, Reconductor to add slack between CB 422 and adjacent disconnect switch south of CB 422. -Positions 4, relocate the three (3) existing CCVT’s on new pedestal pole type support structures and new foundations. Remove three (3) existing risers and foundations and replace with three (3) new weighted risers and foundations. Reconductor to add slack between CB 412 and disconnect switch -Position 6, relocate the three (3) existing CCVT’s on new pedestal pole type support structures and new foundations. Remove three (3) existing risers and foundations and replace with three (3) new weighted risers and foundations. Reconductor to add slack between disconnect switch 6063 and adjacent c-phase bus support. -Position 8, reconductor to add slack between disconnect switch north of CB 482 and bus support under North 220kv bus. Reconductor to add slack between disconnect switch south of CB 482 and bus supports North of the disconnect switch. -Install grounding for all new and re-installed structures and equipment per the latest SCE standard | Goleta Substation: 220kV Positions -Position 2, Reconductor to add slack between CB 422 and adjacent disconnect switch south of CB 422. -Positions 4, relocate the three (3) existing CCVT’s on new pedestal pole type support structures and new foundations. Remove three (3) existing risers and foundations and replace with three (3) new weighted risers and foundations. Reconductor to add slack between CB 412 and disconnect switch -Position 6, relocate the three (3) existing CCVT’s on new pedestal pole type support structures and new foundations. Remove three (3) existing risers and foundations and replace with three (3) new weighted risers and foundations. Reconductor to add slack between disconnect switch 6063 and adjacent c-phase bus support. -Position 8, reconductor to add slack between disconnect switch north of CB 482 and bus support under North 220kv bus. Reconductor to add slack between disconnect switch south of CB 482 and bus supports North of the disconnect switch. -Install grounding for all new and re-installed structures and equipment per the latest SCE standard | New | None | Other - See Notes | Age/Condition | July 2016 : Note Inspection date is of seismic inspection and not compliance driven inspection date | 20+ years | Fragility and seismic analyses | The alternative option considered is to keep the substation as is and potentially recover post seismic event. This has no upfront cost. Cost incurred would be in recovery time and effort that varies by size of seismic event. | HFTD Tier 3 | See Note 16C | Aside from typical weathering of components, seismic activity can impact retrofits, requiring re-inspection | Roderick Dela Cruz, Integrate System Strategy | See Note 19B | 13.04 | See Note 21A | 220kV/66kV/12kV | See Note 23B | 902214606 | COS-00-SP-TD-000000 | 7392 | See Note 27A | Yes | 2017 | Pre-2018 | FRM/CRT | No | N/A | N/A | N/A | See Col. 37 | 20119 = 1,527 2020 = 43 2021 = 1 2022 = 3 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2019-05-29 | No | 2019-12-31 | 2019-12-03 | N/A | 670.881 | 670.881 | See Note 53A | 1573.401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 303.7587 | 1222.8991 | 42.5067 | 0.78024 | 3.4563 | 1573.401 | 480.4326 | See Note 57A | N/A | See Note 59A | 8.7222e-13 | None | 100% | 0% | Column 52: Source = PMWIF (V.0 Project Summary)
N/A | PB-25.30 | Center Substation Seismic Mitigation Project | 33.928282;-118.106254 | Norwalk, Los Angeles County | Center Substation: 220kV Positions -Positions 2, 3, 4, and 10, relocate the three (3) existing CCVT’s on new pedestal pole type support structures and new foundations. Remove three (3) existing risers and foundations and replace with three (3) new weighted risers and foundations. -Position 6, relocate the three (3) existing CCVT’s on new pedestal pole type support structures and new foundations. Remove three (3) existing risers and foundations and replace with three (3) new weighted risers and foundations. Reconductor to add slack between disconnect switch 6063 and adjacent c-phase bus support. -Position 7, relocate the three (3) existing CCVT’s on new pedestal pole type support structures and new foundations. Remove three (3) existing risers and foundations and replace with three (3) new weighted risers and foundations. -Position 8, relocate the three (3) existing CCVT’s on new pedestal pole type support structures and new foundations. Remove three (3) existing risers and foundations and replace with three (3) new weighted risers and foundations. Reconductor to add slack between disconnect switch 6083 and adjacent c-phase bus support. -Install grounding for all new and re-installed structures and equipment per the latest SCE standard 220kV North and South Operating Buses -Modify bus dead end structures to provide a brace and install triangular jumper assembly to a total of six (6) suspended weights to limit sideways movement. | Center Substation: 220kV Positions -Positions 2, 3, 4, and 10, relocate the three (3) existing CCVT’s on new pedestal pole type support structures and new foundations. Remove three (3) existing risers and foundations and replace with three (3) new weighted risers and foundations. -Position 6, relocate the three (3) existing CCVT’s on new pedestal pole type support structures and new foundations. Remove three (3) existing risers and foundations and replace with three (3) new weighted risers and foundations. Reconductor to add slack between disconnect switch 6063 and adjacent c-phase bus support. -Position 7, relocate the three (3) existing CCVT’s on new pedestal pole type support structures and new foundations. Remove three (3) existing risers and foundations and replace with three (3) new weighted risers and foundations. -Position 8, relocate the three (3) existing CCVT’s on new pedestal pole type support structures and new foundations. Remove three (3) existing risers and foundations and replace with three (3) new weighted risers and foundations. Reconductor to add slack between disconnect switch 6083 and adjacent c-phase bus support. -Install grounding for all new and re-installed structures and equipment per the latest SCE standard 220kV North and South Operating Buses -Modify bus dead end structures to provide a brace and install triangular jumper assembly to a total of six (6) suspended weights to limit sideways movement. | New | None | Other - See Notes | Age/Condition | July 2016 : Note Inspection date is of seismic inspection and not compliance driven inspection date | 20+ years | Fragility and seismic analyses | The alternative option considered is to keep the substation as is and potentially recover post seismic event. This has no upfront cost. Cost incurred would be in recovery time and effort that varies by size of seismic event. | Not applicable - No HFRA | See Note 16C | Aside from typical weathering of components, seismic activity can impact retrofits, requiring re-inspection | Roderick Dela Cruz, Integrate System Strategy | See Note 19B | 25.5 | See Note 21A | 220kV/66kV/12kV | See Note 23B | 902214368 | COS-00-SP-TD-000001 | 7393 | See Note 27A | Yes | 2017 | Pre-2018 | FRM/CRT | No | N/A | N/A | N/A | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Construction more than 50% completed | See Note 46A | 2020-10-12 | Yes | 2019-12-31 | 2023-12-29 | Difficulties in Design and Coordination | 1531.037 | 964.5533 | See Note 53A | 2206.7846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 381.9993 | 142.9065 | 328.223 | 1003.2804 | 350.3754 | 2206.7846 | 503.1868 | See Note 57A | N/A | See Note 59A | 1952.9376 | None | 100% | 0% | Column 52: Source = PMWIF (V.0 Project Summary)
N/A | PB-26 | Seismic Mitigation Program - Trans Lines | Not applicable at program level | Not applicable at program level | Seismic assessment and mitigation of transmission lines/towers | Seismic assessment and mitigation of transmission lines/towers | New | Not applicable at program level | Other - See Notes | Age/Condition | Not applicable at program level | Not applicable at program level | None | Not applicable at program level | Not applicable at program level | See Note 16C | Not applicable at program level | Roderick Dela Cruz, Integrate System Strategy | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 23B | Not applicable at program level | COS-00-SP-TD-000002 | 7392 | See Note 27A | Yes | 2017 | 2017 | FRM/CRT | No | N/A | N/A | N/A | Not applicable at program level | Not applicable at program level | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Not applicable at program level | See Note 46A | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 53A | Not applicable at program level | 2501.089 | 2501.089 | 2501.089 | 2501.089 | 2501.089 | Not Available | 12505.4448 | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not applicable at program level | Not applicable at program level | See Note 57A | N/A | No Cost-Benefit analysis performed. Assessment identified possible risk of tower failure that could be caused by an earthquake/landslide. | See Note 60A | None | 100% | 0% | Column 9: Seismic Mitigation
N/A | PB-27 | Substation Facility Capital Maintenance | Not applicable at program level | Not applicable at program level | This program replaces or rebuilds failed or failing equipment at substation facilities, such as heating, ventilating, and air conditioning (HVAC) systems, plumbing, electrical, roof replacements, fencing, motorized gates, fuel tanks, carpet, flooring, and asphalt or concrete driveways which undergo regular wear and tear. | Substation Facility Maintenance | Replacement | Not applicable at program level | Other - See Notes | Age/Condition | Not applicable at program level | Not applicable at program level | Review is performed based on age, condition, and lifecycle of the asset | Not applicable at program level | Not applicable at program level | See Note 16C | Not applicable at program level | Roderick Dela Cruz, Integrate System Strategy | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 23B | Not applicable at program level | COS-00-RE-MA-NE7637 | 7637 | See Note 27A | Not applicable at program level | Not applicable at program level | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | Not applicable at program level | Not applicable at program level | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Not applicable at program level | See Note 46A | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 53A | Not applicable at program level | 4059.8511 | 4198.719 | 6263.6158 | 6420.2062 | 6580.7114 | Not Available | 27523.1035 | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not applicable at program level | Not applicable at program level | See Note 57A | N/A | No Cost-Benefit analysis performed. | See Note 60A | None | 100% | 0% | Column 9: Asset Condition
N/A | PB-27.01 | Lugo Substation Emergency Generator Replacement | 34.367, -117.369 | Hesperia, San Bernardino County | Lugo Substation (T): Replace the station's existing 250kW 3-phase, 120/240V emergency power generator with new 750kW power generator. Remove the existing propane fuel tank. Replace the existing main AC distribution switchboard panel with two (2) Automatic Transfer Switches (Z01 & Z02). Install one (1) Main AC Panel, 3-phase, 120/240V, 4-wire (SPD). Replace existing Power Panel "SP2" near the No. 2AA transformer bank, including homerun cables + jumper cables to the DC box #5. Replace existing Power Panel "PF" near the No. 1AA transformer bank, including homerun cables + jumper cables to the DC box #4. | Emergency Generator | Replacement | None | Other - See Notes | Age/Condition | 2019-11-26 | Not readily available -- Project addresses numerous pieces of smaller substation equipment. | Engineering analysis determined need to upgrade emergency generators | Emergent replacement after equipment failure | Tier 2 | See Note 16C | High Wind Events, Extreme Temperature Conditions, Air Particulate Levels, High Seismic Area, Desert Region | Don Neal, Corp Real Estate | See Note 19B | 46 | See Note 21A | 13.8kV, 12kV | See Note 23B | 901331775 | COS-00-RE-MA-NE7637 | 7637 | See Note 27A | Yes | 2014 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2015 = 1,858 2016 = 498 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2015-10-20 | No | 2015-12-31 | 2015-12-18 | N/A | 953 | 953 | See Note 53A | 2356.0437 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 2356.0437 | 0 | 0 | 0 | 0 | 2356.0437 | 225.6211 | See Note 57A | N/A | No Cost-Benefit analysis performed. | -1.4644e-12 | None | 100% | 0% | Column 9: Asset Condition Column 11: Inspection data for new asset. This particular date pertains to the station generator gear. Column 52: Source= PMWIF (v0 Project Summary)
N/A | PB-27.02 | Vincent Sub - R/R Asph Roadway | 34.486, -118.118 | Palmdale, Los Angeles County | This Project will replace the asphalt at the substation and install drainage. | Facility Upgrade | Upgrade | None | Other - See Notes | Age/Condition | 2020-05-14 | 10 years | Observation | Work was competitively bid | Tier 3 | See Note 16C | No specific factors outside of very extreme weather and environmental events that could compromise the integrity of the ground cover. | Don Neal, Corp Real Estate | See Note 19B | 900 linear feet of drains and 3,000 square feet of asphalt | See Note 21A | This project does not impact capacity | See Note 23B | 801711175 | COS-00-RE-MA-NE7637 | 7637 | See Note 27A | Yes | 2018 | 2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2020 = 1,072 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2020-06-01 | No | 2018-12-30 | 2020-08-30 | Held project until security wall around substation was complete to avoid rework. | Not readily available | Not Readily Available | See Note 53A | 1071.9867 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 93.221 | 17.1074 | 961.6583 | 0 | 0 | 1071.9867 | 64.0587 | See Note 57A | N/A | See Note 59A | 4.6833e-13 | None | 100% | 0% | Column 9: Asset Condition Column 23: SCE utilized Facility Condition Index analysis to evaluate facilities, including this facility, to prioritize facility work.
N/A | PB-27.03 | Eldorado Sub - R/R HVAC System (MEER) | 35.794, -115.006 | Boulder City, Clark County, Nevada | This project will install additional HVAC systems for equipment cooling. | Facility Upgrade | Upgrade | None | Infrastructure Enhancement | Substation Reliability | 2020-02-05 | N/A- New | Temperature tests | Alternative solution was to not address; however, that could cause equipment to stop and impact electrical services | Out of State | See Note 16C | No specific factors outside of very extreme weather and environmental events that could compromise the integrity of the system. | Don Neal, Corp Real Estate | See Note 19B | 18,400 square feet | See Note 21A | This project does not impact capacity | See Note 23B | 801927220 | COS-00-RE-MA-NE7637 | 7637 | See Note 27A | Yes | 2020 | 2019 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2020 = 1,369 2021 = -32 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2020-02-19 | No | 2020-12-10 | 2020-12-10 | N/A | Not readily available | Not Readily Available | See Note 53A | 1336.5931 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 0 | 0 | 1368.8363 | -32.2431 | 0 | 1336.5931 | 60.6693 | See Note 57A | N/A | See Note 59A | -1.0651e-12 | None | 100% | 0%
N/A | PB-28 | Physical Security System Upgrade | Not applicable at program level | Not applicable at program level | No Regrets Program: Implement physical access controls to meet NERC CIP-014 compliance requirements. The intent is to reduce security and operational risk to the Bulk Electric System (BES) and financial risk to the Company by designing, installing, and commissioning integrated physical security systems at locations which will fall under the impending NERC CIP-014 Physical Security standard (R5 - https://www.nerc.com/pa/Stand/Reliability%20Standards/CIP-014-2.pdf) , as identified by SCE and mandated by the North American Reliability Electric Corporation. | Substation | Replace / New | Not applicable at program level | Security | NERC CIP Compliance | Not applicable at program level | Not applicable at program level | N/A - To meet North American Electric Reliability Corporation (NERC) Critical Infrastructure Protection (CIP-014) Physical Security Reliability Standard Approved by the Federal Energy Regulatory Commission (FERC) Order 802 - (May 2014) SCE is required to implement NERC CIP-014 (Physical Security Protection) standards at vulnerable substations to protect them from foreseeable threats | Not applicable at program level | Not applicable at program level | See Note 16C | Not applicable at program level | Don Neal, Corp Real Estate | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 23B | Not applicable at program level | CET-ET-IR-ME-768101 | 7681 | See Note 27A | Yes | 2014 | Pre-2017 | FRM/CRT | No | N/A | N/A | N/A | Not applicable at program level | Not applicable at program level | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Not applicable at program level | See Note 46A | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 53A | Not applicable at program level | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 0 | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not applicable at program level | Not applicable at program level | See Note 57A | N/A | No specific cost benefit analysis performed – Activity is addressing NERC CIP-014 Physical Security compliance requirements | See Note 60A | None | 100% | 0%
N/A | PB-28.01 | CS-(ES-5080) Substation Physical Security System Upgrade |  |  | No Regrets Program - Location ES-5080 Substation: -Provide AC/DC power feeds to security equipment and yard/fence lighting. -Provide barriers around critical equipment as required. -Build new, or replace/modify, substation fence, walls, and/or gates. | Substation | Replace / New | None | Security | NERC CIP Compliance | N/A - New. The last corporate security inspection was performed in 2019. | N/A - Largely includes installation of new equipment/technology | N/A - To meet North American Electric Reliability Corporation (NERC) Critical Infrastructure Protection (CIP-014) Physical Security Reliability Standard Approved by the Federal Energy Regulatory Commission (FERC) Order 802 - (May 2014) SCE is required to implement NERC CIP-014 (Physical Security Protection) standards at vulnerable substations to protect them from foreseeable threats | Alternative – Security fence, proactive detection, active deterrence and EMS protection. Cost $85.0M Alternative – Block wall, proactive detection, active deterrence, EMS protection and multiple & redundant security systems. Cost $102.2M | Tier 2 | See Note 16C | Minimal besides catastrophic environmental events that would impact physical security measures | Demetric Brown, MPO - Programs | See Note 19B | 19.2 | See Note 21A | 500/220 (kV) | See Note 23B | 901333954 | CET-ET-IR-ME-768101 | 7681 | See Note 27A | Yes | 2014 | Pre-2017 | FRM/CRT | No | N/A | N/A | N/A | See Col. 37 | 2016 = 11,550 2017 = 53 2018 = 21 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2014-11-10 | No | 2014-12-31 | 2016-07-28 | Coordination with Other Work | 500 | 500 | See Note 53A | 11624.0331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11624.0271 | 0.00598 | 0 | 0 | 0 | 11624.0331 | 1652.9543 | See Note 57A | N/A | No specific cost benefit analysis performed – Activity is addressing NERC CIP-014 Physical Security compliance requirements | -6.854e-12 | None | 100% | 0% | Column 52: Source= PMWIF (V0 Proj Summary); Represents WO level cost estimate; total project cost including non-TD elements is $2M
N/A | PB-28.02 | CS-(ES-5069) Substation Physical Security System Upgrade |  |  | No Regrets Program - ES 5069 Substation: -Provide AC/DC power feeds to security equipment and yard/fence lighting. -Provide barriers around critical equipment as required. | Substation | Replace / New | None | Security | NERC CIP Compliance | N/A - New. The last corporate security inspection was performed in 2019. | N/A - Largely includes installation of new equipment/technology | N/A - To meet North American Electric Reliability Corporation (NERC) Critical Infrastructure Protection (CIP-014) Physical Security Reliability Standard Approved by the Federal Energy Regulatory Commission (FERC) Order 802 - (May 2014) SCE is required to implement NERC CIP-014 (Physical Security Protection) standards at vulnerable substations to protect them from foreseeable threats | Alternative – Security fence, proactive detection, active deterrence and EMS protection. Cost $85.0M Alternative – Block wall, proactive detection, active deterrence, EMS protection and multiple & redundant security systems. Cost $102.2M | Non-HFRA | See Note 16C | Minimal besides catastrophic environmental events that would impact physical security measures | Demetric Brown, MPO - Programs | See Note 19B | 102.1 | See Note 21A | 500 kV/ 220 kV | See Note 23B | 901333956 | CET-ET-IR-ME-768101 | 7681 | See Note 27A | Yes | 2014 | Pre-2017 | FRM/CRT | No | N/A | N/A | N/A | See Col. 37 | 2015 = 3,883 2016 = 380 2017 = -210 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2014-11-17 | No | 2014-12-31 | 2015-02-16 | N/A | 500 | 425.62 | See Note 53A | 190.4712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190.4712 | 0 | 0 | 0 | 0 | 190.4712 | 11.3239 | See Note 57A | N/A | No specific cost benefit analysis performed – Activity is addressing NERC CIP-014 Physical Security compliance requirements | 2.6892e-13 | None | 100% | 0% | Column 52: Source= PMWIF (V0 Proj Summary); Represents WO level cost estimate; total project cost including non-TD elements is $2M
N/A | PB-28.03 | CS-(ES-5067) Substation Physical Security System Upgrade |  |  | No Regrets Program - ES-5067 Substation: -Provide AC/DC power feeds to security equipment -Build new, or replace/modify, substation fence, walls, and/or gates. | Substation | Replace / New | None | Security | NERC CIP Compliance | N/A - New. The last corporate security inspection was performed in 2019. | N/A - Largely includes installation of new equipment/technology | N/A - To meet North American Electric Reliability Corporation (NERC) Critical Infrastructure Protection (CIP-014) Physical Security Reliability Standard Approved by the Federal Energy Regulatory Commission (FERC) Order 802 - (May 2014) SCE is required to implement NERC CIP-014 (Physical Security Protection) standards at vulnerable substations to protect them from foreseeable threats | Alternative – Security fence, proactive detection, active deterrence and EMS protection. Cost $85.0M Alternative – Block wall, proactive detection, active deterrence, EMS protection and multiple & redundant security systems. Cost $102.2M | Non-HFRA | See Note 16C | Minimal besides catastrophic environmental events that would impact physical security measures | Demetric Brown, MPO - Programs | See Note 19B | 98 | See Note 21A | 500 kV | See Note 23B | 901333958 | CET-ET-IR-ME-768101 | 7681 | See Note 27A | Yes | 2014 | Pre-2017 | FRM/CRT | No | N/A | N/A | N/A | See Col. 37 | 2017 = 16,426 2018 = 1 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2016-01-11 | No | 2014-12-31 | 2017-04-28 | Coordination with Other Work | 500 | 419.7513 | See Note 53A | 16426.4847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16426.4765 | 0.0081264 | 0 | 0 | 0 | 16426.4847 | 1870.416 | See Note 57A | N/A | No specific cost benefit analysis performed – Activity is addressing NERC CIP-014 Physical Security compliance requirements | 7.4957e-12 | None | 100% | 0% | Column 52: Source= PMWIF (V0 Proj Summary); Represents WO level cost estimate; total project cost including non-TD elements is $2M; SCE also notes that v2 Project Summary updated the estimate to $11M for WO level estimate and $13M for total project estimate
N/A | PB-28.04 | CS-(ES-5061) Substation Physical Security System Upgrade |  |  | No Regrets Program - ES-5061 Substation:-Provide AC/DC power feeds to security equipment and yard/fence lighting.-Provide ballistic barriers around critical equipment consisting of transformers banks and circuit breakers as required.-Build new, or replace/modify, substation fence, walls, and/or gates. | Substation | Replace / New | None | Security | NERC CIP Compliance | N/A - New. The last corporate security inspection was performed in 2020. | N/A - Largely includes installation of new equipment/technology | N/A - To meet North American Electric Reliability Corporation (NERC) Critical Infrastructure Protection (CIP-014) Physical Security Reliability Standard Approved by the Federal Energy Regulatory Commission (FERC) Order 802 - (May 2014) Substation Engineering Analysis SCE is required to implement NERC CIP-014 (Physical Security Protection) standards at vulnerable substations to protect them from foreseeable threats | Alternative – Security fence, proactive detection, active deterrence and EMS protection. Cost $85.0M Alternative – Block wall, proactive detection, active deterrence, EMS protection and multiple & redundant security systems. Cost $102.2M | Tier 2 | See Note 16C | Extreme Rain / Flooding, Extreme Temperature Conditions | Demetric Brown, MPO - Programs | See Note 19B | 46 | See Note 21A | 500 kV/ 220 kV | See Note 23B | 901333957 | CET-ET-IR-ME-768101 | 7681 | See Note 27A | Yes | 2014 | Pre-2017 | FRM/CRT | No | N/A | N/A | N/A | See Col. 37 | 2016 = 10,687 2017 = 303 2019 = -137 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2014-10-27 | No | 2014-12-31 | 2016-01-12 | Coordination with Other Work | 500 | 500 | See Note 53A | 10853.3151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10990.1411 | -136.8261 | 0 | 0 | 0 | 10853.3151 | 981.9949 | See Note 57A | N/A | No project specific cost benefit performed. This work is largely inspection-driven or performed ahead of asset failure to maintain the safety and reliability of the system. See Note 59A. | 0 | None | 100% | 0% | Column 52: Source= PMWIF (V0 Proj Summary); Represents WO level cost estimate; total project cost including non-TD elements is $2M
N/A | PB-29 | Substation Switchrack Upgrade & Related Line Work | Not applicable at program level | Not applicable at program level | A substation switchrack is the skeletal/structural system used to support substation assets such as circuit breakers, disconnects, and conductors. Substation structures degrade over time and need to be replaced and/or upgraded. The switchracks/structure needs are initially identified during a field inspection of circuit breakers and/or transformers, and in some cases disconnect switches. | Switchrack | Replacement | Not applicable at program level | Infrastructure Replacement | Age/Condition | Not applicable at program level | Not applicable at program level | The main analysis used to inform the health of the asset is the Health Index developed from the MDT (Maintenance Decision Tool). The health index is developed using specific data from the assets including fault interruption history, age, maintenance data etc. In addition to the health index, decisions are influenced by a Weibull analysis and subject matter input for conditions not included in the MDT, e.g. possible leaks. | Not applicable at program level | Not applicable at program level | See Note 16C | Not applicable at program level | Demetric Brown, MPO - Programs | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 23B | Not applicable at program level | CET-ET-IR-RB-771301 & -771304 | 7713 | See Note 27A | Not applicable at program level | Not applicable at program level | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | Not applicable at program level | Not applicable at program level | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Not applicable at program level | See Note 46A | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 53A | Not applicable at program level | 2194.0636 | 3961.2897 | 1192.9819 | 1005.2976 | 627.8708 | 0 | 8981.5036 | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not applicable at program level | Not applicable at program level | See Note 57A | N/A | No specific cost benefit analysis performed. | See Note 60A | None | 100% | 0% | Column 10: Various drivers that can trigger a switchrack rebuild include but are not limited to; Deteriorated condition of structures such as wood pole, lattice or pipe steel; Cubicle switchgear due to aged equipment, deteriorated enclosure and confined working space; Seismic needs; Feasibility of new equipment installation, such as Circuit Breaker or Transformer Replacements on or within the switchrack; Physical congestion and/or lack of required clearances that create unsafe operating conditions; and Non-standard electrical switchrack configurations.
N/A | PB-29.01 | Lighthipe Substation Switchrack Upgrade | 33.880, -118.175 | Long Beach , Los Angeles County | Lighthipe Substation: Substation Switchrack Rebuild/Upgrade | Switchrack | Replacement | PB-29.02 & PB-29.03 | Infrastructure Replacement | Age/Condition | 2020-05-03 | 10 - 50+ years | Short circuit duty analysis, Seismic analysis on switchrack | Retrofit- unknown final cost more than 100 Million, Breaker and a half configuration – 95 Million, Double breaker double buss – 88 Million; See Note 14A | Non-HFRA | See Note 16C | High Seismic, Salt Corrosion (Coastal Areas), Flooding | Demetric Brown, MPO - Programs | See Note 19B | Lighthipe: 20.2 Expansion: 2.6 Laydown Yard Remediation: 11 | See Note 21A | TR.BK No. 1A 280MVA/220-66kV TR.BK No. 3A 280MVA/220-66kV TR.BK No. 4A 280MVA/220-66kV | See Note 23B | 902694513 | CET-ET-IR-RB-771301 | 7713 | See Note 27A | Yes | 2019-02-22 | 2018 | FRM/CRT | No | N/A | N/A | N/A | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Construction more than 50% completed | See Note 46A | 2020-09-11 | No | 2022-04-29 | 2026-07-17 | Refinement of schedule for this project | 76096 | 16741.12 | See Note 53A | 6861.5537 | 1674.5216 | 979.9457 | 366.2289 | 211.3366 | 130.6248 | 27.059 | 3389.7166 | 0 | 250.7596 | 694.3588 | 927.2047 | 1599.514 | 3471.8371 | 637.8153 | See Note 57A | N/A | SCE performed a Present Value Revenue Requirement analysis for the proposed and alternative options considered. | 3281.2763 | None | 100% | 0% | Column 10: Various drivers Column 52: Source= C55
N/A | PB-29.02 | Del Amo-Laguna Bell 220 KV - Design/Construction of the Lighthipe 220kv TSPs | 33.880, -118.175 | Long Beach, Los Angeles County | Remove the existing 220kV tower and replace with new 3-TSPs (Del Amo-Laguna Bell 220kv T/L for the new MEER) | Tubular Steel Poles | Replacement | PB-29.01 & PB-29.03 | Infrastructure Replacement | Replace Other Substation Equipment | 2021-06-21 | 10 - 50+ years | Short circuit duty analysis, Seismic analysis on switchrack for 66kV Rebuild | Not upgrading Lighthipe Substation could lead to in-service failures causing extensive outages, safety hazards, and significant environmental, financial, and brand implications; See Note 14A | Non-HFRA | See Note 16C | No significant environmental factors | Demetric Brown, MPO - Programs | See Note 19B | See Note 20B | See Note 21A | 220kV | See Note 23B | 902865681 | CET-ET-IR-RB-771303 | 7713 | See Note 27A | Yes | 2019 | 2018 | FRM/CRT | No | N/A | N/A | N/A | See Col. 37 | 2021 = 3,485 2022 = 508 | TBD | N/A | TBD | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2021-07-06 | No | 2023-12-31 | 2021-11-16 | N/A | 500 | 500 | See Note 53A | 4020.389 | -31.119 | 0 | 0 | 0 | 59.298 | 0 | 28.179 | 0 | 3.5181 | 1100.5436 | 2380.6389 | 507.5094 | 3992.21 | 537.4348 | See Note 57A | N/A | See Note 59A | -2.3283e-12 | None | 100% | 0% | Column 23: While SCE does not have a utility-wide prioritization ranking system, please see tab "Supplement-Part 1" for additional details on how work is identified and prioritized for this area. Column 52: Source= C55
N/A | PB-29.03 | DEL AMO-HINSON 220 KV - Design/ Construction of the Lighthipe 220KV TSP'S | 33.880, -118.175 | Long Beach, Los Angeles County | Del Amo-Hinson 220kV Line: Remove the existing 220kV tower (Del Amo-Hinson 220kv T/L for the new MEER) | Tubular Steel Poles | Replacement | PB-29.01 & PB-29.02 | Infrastructure Replacement | Replace Other Substation Equipment | 2020-12-30 | 10 - 50+ years | Short circuit duty analysis, Seismic analysis on switchrack for 66kV Rebuild | Not upgrading Lighthipe Substation could lead to in-service failures causing extensive outages, safety hazards, and significant environmental, financial, and brand implications; See Note 14A | Non-HFRA | See Note 16C | No significant environmental factors | Demetric Brown, MPO - Programs | See Note 19B | See Note 20B | See Note 21A | 220kV | See Note 23B | 902865683 | CET-ET-IR-RB-771300 | 7713 | See Note 27A | Yes | 2019-05-22 | 2018 | FRM/CRT | No | N/A | N/A | N/A | See Col. 37 | 2022 = 4,367 | TBD | N/A | TBD | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2021-07-06 | Yes | 2023-12-31 | 2022-03-30 | N/A | 500 | 500 | See Note 53A | 4386.7219 | -16.228 | 0 | 0 | 0 | 35.464 | 0 | 19.236 | 0 | 2.9559 | 1155.4676 | 1298.1548 | 1910.9076 | 4367.4859 | 597.248 | See Note 57A | N/A | See Note 59A | -1.397e-12 | None | 100% | 0% | Column 3: Start and End Point of Circuit Column 23: While SCE does not have a utility-wide prioritization ranking system, please see tab "Supplement-Part 1" for additional details on how work is identified and prioritized for this area. Column 52: Source= C55
N/A | PB-29.04 | El Segundo 66/4kV: Rebuild of West Perimeter Wall & (4) Dead End Structures | 33.910, -118.425 | Manhattan Beach, Los Angeles County | El Segundo: Replace West Perimeter Wall 350 linear ft Replace (4) Dead Ends Chevmain line dead end Chevmain bus dead end S/W El Nido bus dead end S/E El Nido line dead end | IR-Substation Rebuild | Upgrade | None | Compliance Upgrade | Age/Condition - Replace Other Substation Equipment | 05/08/2023 | 60 | National Association of Corrosion Engineers (NACE) rating system | See Note 14A | Non HFRA | See Note 16C | Salt Corrosion (Coastal Areas) | Demetric Brown, MPO - Programs | See Note 19B | 2.1 | See Note 21A | 66/4 kV | See Note 23B | 903465284 | CET-ET-IR-RB-771301 | 7713 | See Note 27A | Yes | 2021 | 2022 | Annual Capital Operating Plan Process | N/A | N/A | N/A | N/A | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Construction more than 50% completed | See Note 46A | 2023-01-30 | Yes | 2023-12-31 | 2023-10-27 | N/A | 7100 | 7100 | See Note 53A | 1248.3575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.9952 | 1237.3623 | 1248.3575 | 97.2491 | See Note 57A | N/A | See Note 59A | 1248.3575 | None | 100% | 0% | Column 52: Source = PMWIF (06/17/2021 Investment Summary)
0: N/A; Project Description 1: PB-29.05; Project Description 2: Lighthipe - Alamitos 66/220kV - Replace Lighthipe 220 kV Position 5 line relays; Project Description 4: Long Beach, Los Angeles County; Project Description 5: Alamitos Sub: Replace Lighthipe 220 kV Position 5 line relays; Project Description 6: Substation; see "Project description; Project Description 7: Replacement; Project Description (Cont.) 24: 902694518; Project Description (Cont.) 25: CET-ET-IR-RB-771301; Project Description (Cont.) 26: 7713; Project Status 45: Pre-construction; Project Status 50: 2025-02-18; Costs 52: 920.338; Costs 52.1: 920.338; Costs 54: 1102.7004 | [16 empty] | 49 and 52 Origination = Verified PMWIF PMWIF Approval Date = 05/22/2019 Latest Approved Investment Summary Version = Pulled on 10/23/2023
0: N/A; Project Description 1: PB-29.06; Project Description 2: Lighthipe - Harborgen- Replace 220 kV line relays Harborgen 220/12kV - Replace Lighthipe 220 kV line relays due to Lighthipe Rebuild Replace Lighthipe 220 kV line relays due to Lighthipe Rebuild; Project Description 4: Long Beach, Los Angeles County; Project Description 5: Harborgen 220/12kV - Replace Lighthipe 220 kV line relays due to Lighthipe Rebuild; Project Description 6: Substation; see "Project description; Project Description 7: Replacement; Project Description (Cont.) 24: 902694722; Project Description (Cont.) 25: CET-ET-IR-RB-771301; Project Description (Cont.) 26: 7713; Project Status 45: Engineering more than 50% completed; Project Status 50: 2025-04-14; Costs 52: 1293.445; Costs 52.1: 1293.445; Costs 54: 1512.0761 | [16 empty] | 49 and 52 Origination = Verified PMWIF PMWIF Approval Date = 05/22/2019 Latest Approved Investment Summary Version = Pulled on 10/23/2023
0: N/A; Project Description 1: PB-29.07; Project Description 2: Lighthipe - Hinson 220/66kV - Rplc 220kV line relays Hinson 220/66kV - Replace Lighthipe 220 kV Position 1S line relays due to Lighthipe Rebuild Replace Lighthipe 220 kV Position 1S line relays due to Lighthipe Rebuild; Project Description 4: Long Beach, Los Angeles County; Project Description 5: Hinson 220/66kV - Replace Lighthipe 220 kV Position 1S line relays due to Lighthipe Rebuild; Project Description 6: Substation; see "Project description; Project Description 7: Replacement; Project Description (Cont.) 24: 902694726; Project Description (Cont.) 25: CET-ET-IR-RB-771301; Project Description (Cont.) 26: 7713; Project Status 45: Engineering more than 50% completed; Project Status 50: 2025-02-03; Costs 52: 855.627; Costs 52.1: 855.627; Costs 54: 1017.3253 | [16 empty] | 49 and 52 Origination = Verified PMWIF PMWIF Approval Date = 05/22/2019 Latest Approved Investment Summary Version = Pulled on 10/23/2023
0: N/A; Project Description 1: PB-29.08; Project Description 2: Vincent 500/200 kV: Rebuild Detention Basin Retaining Wall Retrofit existing one basin retaining wall; Project Description 4: Palmdale, Los Angeles County; Project Description 5: Vincent 500/200 kV: Rebuild Detention Basin Retaining Wall Retrofit existing one basin retaining wall; Project Description 6: Substation; see "Project description; Project Description 7: Replacement; Project Description (Cont.) 24: 904091225; Project Description (Cont.) 25: CET-ET-IR-RB-771301; Project Description (Cont.) 26: 7713; Project Status 45: Pre-construction; Project Status 50: 2024-05-31; Costs 52: 2068; Costs 52.1: 2068; Costs 54: 2068.494 | [16 empty] | 49 and 52 Origination = Verified PMWIF PMWIF Approval Date = 04/25/2023 Latest Approved Investment Summary Version = Pulled on 10/23/2023
N/A | PB-30 | Physical Security Enhancements | Not applicable at program level | Not applicable at program level | NERC CIP-14 Program: Implement physical access controls to meet NERC CIP-014 compliance requirements. The intent is to reduce security and operational risk to the Bulk Electric System (BES) and financial risk to the Company by designing, installing, and commissioning integrated physical security systems at locations which will fall under the impending NERC CIP-014 Physical Security standard (R5 - https://www.nerc.com/pa/Stand/Reliability%20Standards/CIP-014-2.pdf) , as identified by SCE and mandated by the North American Reliability Electric Corporation. | Substation Physical Security Measures | Replace / New | Not applicable at program level | Security | NERC CIP Compliance | Not applicable at program level | Not applicable at program level | N/A - To meet North American Electric Reliability Corporation (NERC) Critical Infrastructure Protection (CIP-014) Physical Security Reliability Standard Approved by the Federal Energy Regulatory Commission (FERC) Order 802 - (May 2014) SCE is required to implement NERC CIP-014 (Physical Security Protection) standards at vulnerable substations to protect them from foreseeable threats | Not applicable at program level | Not applicable at program level | See Note 16C | Not applicable at program level | Randy White, Corporate Security | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 23B | Not applicable at program level | COS-00-CS-CS-782000 | 7820 | See Note 27A | Yes | 2016 | Pre-2017 | FRM/CRT | No | N/A | N/A | N/A | Not applicable at program level | Not applicable at program level | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Not applicable at program level | See Note 46A | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 53A | Not applicable at program level | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 0 | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not applicable at program level | Not applicable at program level | See Note 57A | N/A | No specific cost benefit analysis performed – Activity is addressing NERC CIP-014 Physical Security compliance requirements | See Note 60A | None | 100% | 0%
N/A | PB-30.01 | CS-(ES-5061) Substation Physical Security Enhancements |  |  | NERC CIP-14: ES-5061 Substation ¦ Control Center: • Replace and or modify substation perimeter with concrete wall. • Replace and or modify gates with auto and manual gates. • Install AC panel and power, pole foundations, conduit and conductor for security requirements. • Install transformer fire walls as required. | Substation Physical Security Measures | Replace / New | PB-45.03 | Security | NERC CIP Compliance | The last corporate security inspection was performed in 2019. | Not readily available, and involves installation of new equipment/technology | N/A - To meet North American Electric Reliability Corporation (NERC) Critical Infrastructure Protection (CIP-014) Physical Security Reliability Standard Approved by the Federal Energy Regulatory Commission (FERC) Order 802 - (May 2014) SCE is required to implement NERC CIP-014 (Physical Security Protection) standards at vulnerable substations to protect them from foreseeable threats | Alternative – Security fence, proactive detection, active deterrence and EMS protection. Cost $85.0M Alternative – Block wall, proactive detection, active deterrence, EMS protection and multiple & redundant security systems. Cost $102.2M Option #3 – Block wall, proactive detection, active deterrence, EMS protection and multiple & redundant security systems. Cost $102.2M | Tier 2 | See Note 16C | Minimal besides catastrophic environmental events that would impact physical security measures | Randy White, Corporate Security | See Note 19B | 46 | See Note 21A | 500 kV/ 220 kV | See Note 23B | 801578594 | COS-00-CS-CS-782000 | 7820 | See Note 27A | Yes | 2017 | Pre-2017 | FRM/CRT | No | N/A | N/A | N/A | See Col. 37 | 2020 = 5,635 2021 = 451 2022 = -3 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2018-03-01 | No | 2020-03-31 | 2020-12-31 | Construction delay | 4721 | 4721 | See Note 53A | 6082.8648 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 4428.4436 | 517.8823 | 688.7511 | 450.7138 | -2.9259 | 6082.8648 | 1699.049 | See Note 57A | N/A | No specific cost benefit analysis performed – Activity is addressing NERC CIP-014 Physical Security compliance requirements | -1.7565e-13 | None | 100% | 0% | Column 52: Source= FRM (11/09/2016); Represents project cost with contingency Column 8: Related to PB-45.03 which is the T&D component of project
N/A | PB-30.02 | CS-(ES-5069) Substation Physical Security Enhancements |  |  | NERC CIP-14 Program: ES-5069 Substation ¦ Control Center: • Replace and or modify substation perimeter with concrete wall. • Replace and or modify gates with auto and manual gates. • Install AC panel and power, pole foundations, conduit and conductor for security requirements. • Install transformer fire walls as required. | Substation Physical Security Measures | Replace / New | PB-45.01 | Security | NERC CIP Compliance | The last corporate security inspection was performed in 2019. | Not readily available, and involves installation of new equipment/technology | N/A - To meet North American Electric Reliability Corporation (NERC) Critical Infrastructure Protection (CIP-014) Physical Security Reliability Standard Approved by the Federal Energy Regulatory Commission (FERC) Order 802 - (May 2014) SCE is required to implement NERC CIP-014 (Physical Security Protection) standards at vulnerable substations to protect them from foreseeable threats | Alternative – Security fence, proactive detection, active deterrence and EMS protection. Cost $85.0M Alternative – Block wall, proactive detection, active deterrence, EMS protection and multiple & redundant security systems. Cost $102.2M Option #3 – Block wall, proactive detection, active deterrence, EMS protection and multiple & redundant security systems. Cost $102.2M | Non-HFRA | See Note 16C | Minimal besides catastrophic environmental events that would impact physical security measures | Randy White, Corporate Security | See Note 19B | 102.1 | See Note 21A | 500 kV/ 220 kV | See Note 23B | 801578595 | COS-00-CS-CS-782000 | 7820 | See Note 27A | Yes | 2015 | Pre-2017 | FRM/CRT | No | N/A | N/A | N/A | See Col. 37 | 2022 = 5,644 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2018-03-26 | Yes | 2020-03-31 | 2022-11-09 | Scope realignment (video analytic deficiencies) | 4703 | 4003.3822 | See Note 53A | 5643.6694 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 3254.8563 | 688.2235 | 1176.8574 | 479.0184 | 44.7138 | 5643.6694 | 1512.3683 | See Note 57A | N/A | No specific cost benefit analysis performed – Activity is addressing NERC CIP-014 Physical Security compliance requirements | 4.6948e-12 | None | 100% | 0% | Column 52: Source= FRM (11/09/2016); Represents project cost with contingency Column 8: Related to PB-45.01 which is the T&D component of project
N/A | PB-30.03 | CS-(ES-5050) Substation Physical Security Enhancements |  |  | NERC CIP-14 Program: ES-5050 Substation ¦ Control Center: • Replace and or modify substation perimeter with concrete wall. • Replace and or modify gates with auto and manual gates. • Install AC panel and power, pole foundations, conduit and conductor for security requirements. • Install transformer fire walls as required. | Substation Physical Security Measures | Replace / New | PB-45.02 | Security | NERC CIP Compliance | The last corporate security inspection was performed in 2019. | Not readily available, and involves installation of new equipment/technology | N/A - To meet North American Electric Reliability Corporation (NERC) Critical Infrastructure Protection (CIP-014) Physical Security Reliability Standard Approved by the Federal Energy Regulatory Commission (FERC) Order 802 - (May 2014) SCE is required to implement NERC CIP-014 (Physical Security Protection) standards at vulnerable substations to protect them from foreseeable threats | Alternative – Security fence, proactive detection, active deterrence and EMS protection. Cost $85.0M Alternative – Block wall, proactive detection, active deterrence, EMS protection and multiple & redundant security systems. Cost $102.2M Option #4 – Block wall, proactive detection, active deterrence, EMS protection and multiple & redundant security systems. Cost $102.2M | Tier 3 | See Note 16C | Minimal besides catastrophic environmental events that would impact physical security measures | Randy White, Corporate Security | See Note 19B | 29.4 | See Note 21A | 220 kV | See Note 23B | 801578597 | COS-00-CS-CS-782000 | 7820 | See Note 27A | Yes | 2015 | Pre-2017 | FRM/CRT | No | N/A | N/A | N/A | See Col. 37 | 2020 = 4,420 2021 = 335 2022 = 2 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2018-06-15 | No | 2020-03-31 | 2020-12-31 | Scope realignment (video analytic deficiencies) | 3039 | 2646.656 | See Note 53A | 4756.3779 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 3359.0825 | 671.7319 | 388.7564 | 334.5181 | 2.289 | 4756.3779 | 1310.0286 | See Note 57A | N/A | No specific cost benefit analysis performed – Activity is addressing NERC CIP-014 Physical Security compliance requirements | -1.9561e-12 | None | 100% | 0% | Column 52: Source= FRM (11/09/2016); Represents project cost with contingency Column 8: Related to PB-45.02 which is the T&D component of project
N/A | PB-30.04 | CS-(ES-5054) Substation Physical Security Enhancements |  |  | NERC CIP-14 Program: ES-5054 Substation ¦ Control Center: • Replace and or modify substation perimeter with concrete wall. • Replace and or modify gates with auto and manual gates. • Install AC panel and power, pole foundations, conduit and conductor for security requirements. • Install transformer fire walls as required. | Substation Physical Security Measures | Replace / New | PB-45.04, PB-30.07 | Security | NERC CIP Compliance | The last corporate security inspection was performed in 2019. | Not readily available, and involves installation of new equipment/technology | N/A - To meet North American Electric Reliability Corporation (NERC) Critical Infrastructure Protection (CIP-014) Physical Security Reliability Standard Approved by the Federal Energy Regulatory Commission (FERC) Order 802 - (May 2014) SCE is required to implement NERC CIP-014 (Physical Security Protection) standards at vulnerable substations to protect them from foreseeable threats | Alternative – Security fence, proactive detection, active deterrence and EMS protection. Cost $85.0M Alternative – Block wall, proactive detection, active deterrence, EMS protection and multiple & redundant security systems. Cost $102.2M Option #4 – Block wall, proactive detection, active deterrence, EMS protection and multiple & redundant security systems. Cost $102.2M | Tier 3 | See Note 16C | Minimal besides catastrophic environmental events that would impact physical security measures | Randy White, Corporate Security | See Note 19B | 68 | See Note 21A | 500 kV/ 220 kV | See Note 23B | 801578598 | COS-00-CS-CS-782000 | 7820 | See Note 27A | Yes | 2015 | Pre-2017 | FRM/CRT | No | N/A | N/A | N/A | See Col. 37 | 2020 = 5,010 2021 = 397 2022 = 11 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2019-11-13 | NO | 2020-03-31 | 2020-12-31 | Permitting delays | 4722 | 4722 | See Note 53A | 5418.4171 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 1739.2397 | 768.8681 | 2501.7872 | 397.0241 | 11.4981 | 5418.4171 | 1187.906 | See Note 57A | N/A | No specific cost benefit analysis performed – Activity is addressing NERC CIP-014 Physical Security compliance requirements | 1.6682e-12 | None | 100% | 0% | Column 52: Source= FRM (11/09/2016); Represents project cost with contingency Column 8: Related to PB-45.04 which is the T&D component of project
N/A | PB-30.05 | CS-(ES-5090) Substation Physical Security Enhancements |  |  | NERC CIP-14 Program: ES-5090 Substation ¦ Control Center: • Replace and or modify substation perimeter with concrete wall. • Replace and or modify gates with auto and manual gates. • Install AC panel and power, pole foundations, conduit and conductor for security requirements. • Install transformer fire walls as required. | Substation Physical Security Measures | Replace / New | PB-45.05 | Security | NERC CIP Compliance | 03/2020 | Not readily available, and involves installation of new equipment/technology | N/A - To meet North American Electric Reliability Corporation (NERC) Critical Infrastructure Protection (CIP-014) Physical Security Reliability Standard Approved by the Federal Energy Regulatory Commission (FERC) Order 802 - (May 2014) SCE is required to implement NERC CIP-014 (Physical Security Protection) standards at vulnerable substations to protect them from foreseeable threats | Alternative – Security fence, proactive detection, active deterrence and EMS protection. Cost $85.0M Alternative – Block wall, proactive detection, active deterrence, EMS protection and multiple & redundant security systems. Cost $102.2M Option #4 – Block wall, proactive detection, active deterrence, EMS protection and multiple & redundant security systems. Cost $102.2M | Out of State | See Note 16C | High Wind Events, Air Particulate Levels, Desert Region, Extreme Temperature Conditions | Randy White, Corporate Security | See Note 19B | 86.7 | See Note 21A | 500 kV/ 220 kV | See Note 23B | 801578590 | COS-00-CS-CS-782000 | 7820 | See Note 27A | Yes | 2015 | Pre-2017 | FRM/CRT | No | N/A | N/A | N/A | See Col. 37 | 2020 = 4,593 2021 = 199 2022 = 48 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2017-01-23 | No | 2019-12-31 | 2020-12-31 | Scope realignment (video analytic deficiencies) | 4560 | 4560 | See Note 53A | 4839.3332 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 692.5422 | 2055.7357 | 1844.2733 | 198.6731 | 48.1089 | 4839.3332 | 939.7648 | See Note 57A | N/A | No specific cost benefit analysis performed – Activity is addressing NERC CIP-014 Physical Security compliance requirements | -9.5013e-12 | None | 100% | 0% | Column 52: Source= FRM (11/09/2016); Represents project cost with contingency Column 8: Related to PB-45.05 which is the T&D component of project
N/A | PB-30.06 | CS-(ES-9078) Physical Security Enhancements |  |  | NERC CIP-14 Program: ES-9078 Substation ¦ Control Center: • Replace and or modify substation perimeter with concrete wall. • Replace and or modify gates with auto and manual gates. • Install AC panel and power, pole foundations, conduit and conductor for security requirements. • Install transformer fire walls as required. | Substation Physical Security Measures | Replace / New | None | Security | NERC CIP Compliance | 02/2020 | Not readily available, and involves installation of new equipment/technology | N/A - To meet North American Electric Reliability Corporation (NERC) Critical Infrastructure Protection (CIP-014) Physical Security Reliability Standard Approved by the Federal Energy Regulatory Commission (FERC) Order 802 - (May 2014) SCE is required to implement NERC CIP-014 (Physical Security Protection) standards at vulnerable substations to protect them from foreseeable threats | Alternative – Security fence, proactive detection, active deterrence and EMS protection. Cost $85.0M Alternative – Block wall, proactive detection, active deterrence, EMS protection and multiple & redundant security systems. Cost $102.2M Option #4 – Block wall, proactive detection, active deterrence, EMS protection and multiple & redundant security systems. Cost $102.2M | Non-HFRA | See Note 16C | Extreme Temperature Conditions | Randy White, Corporate Security | See Note 19B | See Note 20B | See Note 21A | See Note 22A | See Note 23B | 801578592 | COS-00-CS-CS-782000 | 7820 | See Note 27A | Yes | 2015 | Pre-2017 | FRM/CRT | No | N/A | N/A | N/A | See Col. 37 | 2021 = 1,531 2022 = 2 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2017-01-23 | No | 2019-12-31 | 2021-09-01 | Scope of work redesign as a result of WECC audit. | 1560 | 1010.8047 | See Note 53A | 1532.4187 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 1255.4985 | 173.8998 | 88.1987 | 13.2182 | 1.6036 | 1532.4187 | 419.4342 | See Note 57A | N/A | No specific cost benefit analysis performed – Activity is addressing NERC CIP-014 Physical Security compliance requirements | 5.7064e-13 | None | 0% | 100% | Column 52: Source= FRM (11/09/2016); Represents project cost with contingency
N/A | PB-30.07 | CS-(ES-5054) Physical Security Enhancements |  |  | NERC CIP-14 Program: ES-5054 Substation ¦ Control Center: • Relocate some existing distribution facilities in order to make room for the installation of the Corp Security facilities (block wall, etc). | Substation Physical Security Measures | Replace / New | PB - 30.04 | Security | NERC CIP Compliance | 2019-07-21 | N/A - Involves relocation of assets | N/A - To meet North American Electric Reliability Corporation (NERC) Critical Infrastructure Protection (CIP-014) Physical Security Reliability Standard Approved by the Federal Energy Regulatory Commission (FERC) Order 802 - (May 2014) SCE is required to implement NERC CIP-014 (Physical Security Protection) standards at vulnerable substations to protect them from foreseeable threats | N/A - this is relocation costs for PB 30.04. | Non HFRA | See Note 16C | Not Applicable | Demetric Brown, MPO - Programs | N/A | N/A | N/A | N/A | See Note 23B | TD1369432 | CET-ET-IR-ME-782005 | 7820 | See Note 27A | Yes | 2015 | Pre-2017 | FRM/CRT | N/A | N/A | N/A | N/A | See Col. 37 | 2019 = 1,121 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2018-11-06 | No | 2017-12-31 | 2019-07-31 | Not readily available | 0 | 0 | See Note 53A | 1121.3651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 354.1299 | 767.2353 | -7.4522e-14 | 0 | 0 | 1121.3651 | 0 | See Note 57A | N/A | See Note 59A | 208.1577 | None | 100% | 0% | This work order is added scope to the original workorder (Ref:901656358). This is a Distribution scope (relocation of the Bootlegger 12 kV Distribution line) of work that was not captured with the original work order. Therefore the "Original Project Cost" for this element is $0.
N/A | PB-31 | NERC CIP V6 Physical Access Controls | Not applicable at program level | Not applicable at program level | Implement physical access controls to meet NERC CIP-006 V6 compliance requirements. Restrict physical access to NERC CIP-003 V6 Low Impact sites that were not covered under NERC CIP V5 (High and Medium Impact) to meet regulatory compliance. R2 Attachment 1 Section 2 – (https://www.nerc.com/pa/Stand/Reliability%20Standards/CIP-003-7.pdf). | Substation Physical Security Measures | New | Not applicable at program level | Security | NERC CIP Compliance | Not applicable at program level | Not applicable at program level | NERC CIP-002 defined three (3) Impact Ratings of Bulk Electric Systems based on “risk to the reliable operation of the BES”. Devices that provide electronic or physical security inherit the impact rating of the cyber system they protect. Impact Ratings: High, Medium and Low • High Impact (NERC CIP V5 Project) – Control centers used to perform load balancing, electric system reliability coordination, and transmission or generation operation (aka operation of the Energy Management System (EMS) and Generation Management System (GMS), respectively) • Examples: Switching Centers, Data Centers • Medium Impact (NERC CIP V5 Project) – Facilities that fall under the threshold for defined maximum reactive power rating or transmission facilities within the “bright-line” criteria • Medium with External Routable Connections (ERC) • Medium without External Routable Connectivity • Examples: 500kV, 220kV MEERs and Control Rooms • Low Impact (NERC CIP V6 Project) – Peaker plants, other non-medium substations • Examples: 66kV MEERs and Control Rooms, Low with External Routable Connectivity, Generation and Peaker plants | Not applicable at program level | Not applicable at program level | See Note 16C | Not applicable at program level | Randy White, Corporate Security | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 23B | Not applicable at program level | COS-00-CS-CS-745700 | 7948 | See Note 27A | Yes | 2017 | 2017 | FRM/CRT | No | N/A | N/A | N/A | Not applicable at program level | Not applicable at program level | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Not applicable at program level | See Note 46A | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 53A | Not applicable at program level | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 0 | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not applicable at program level | Not applicable at program level | See Note 57A | N/A | No specific cost benefit analysis performed – Activity is addressing NERC CIP-006 V6 Physical Security compliance requirements | See Note 60A | None | 97.03% | 2.971%
N/A | PB-31.01 | Bailey Substation Physical Access Controls Install | 34.777, -118.774 | Gorman, Los Angeles County | This project supports version 6 of NERC CIP requirements, restricting access to Low and Medium impact NERC CIP assets that have been identified by SCE NERC CIP Compliance. In the event card readers are rendered inoperable, Smart Key Technology provides additional restriction to Low and Medium impact assets. Smart Key Technology allows an end user to be assigned with appropriate access based on their qualifications and the impact to their basic job functions. In the event the card reads are rendered inoperable, Smart Key Technology restricts access to only end users who are qualified and trained to gain access to NERC CIP identified assets. This provides additional protection and restriction to NERC CIP Low and Medium Impact assets by restricting and controlling access regardless of the current status of any access control system. Implementation and deployment of Smart Key Technology that includes Smart Keys, Smart Locks for Doors, Gates and Cabinets, Programming Devices, and the necessary network structure to support the implementation and deployment of Smart Key Technology. Includes updating existing processes, procedures, and training (including NERC related documentation) to support Smart Key Technology. | Substation Physical Security Measures | New | None | Security | NERC CIP Compliance | N/A - New | N/A - Largely includes installation of new equipment/technology | NERC CIP-002 defined three (3) Impact Ratings of Bulk Electric Systems based on “risk to the reliable operation of the BES”. Devices that provide electronic or physical security inherit the impact rating of the cyber system they protect. Impact Ratings: High, Medium and Low • High Impact (NERC CIP V5 Project) – Control centers used to perform load balancing, electric system reliability coordination, and transmission or generation operation (aka operation of the Energy Management System (EMS) and Generation Management System (GMS), respectively) • Examples: Switching Centers, Data Centers • Medium Impact (NERC CIP V5 Project) – Facilities that fall under the threshold for defined maximum reactive power rating or transmission facilities within the “bright-line” criteria • Medium with External Routable Connections (ERC) • Medium without External Routable Connectivity • Examples: 500kV, 220kV MEERs and Control Rooms • Low Impact (NERC CIP V6 Project) – Peaker plants, other non-medium substations • Examples: 66kV MEERs and Control Rooms, Low with External Routable Connectivity, Generation and Peaker plants | Option 1 - Full Electronic Access Control Deployment and Smart Key Technology. Deploy full electronic access control at 31 buildings. Enclosures, perimeter gates, and secondary entry will be protected with smart key technology. Capital $16.2M, O&M $2.2M. Option 2 - Deploy Electronic Access Control, (as permissible by infrastructure) and Smart Key Technology. Deploy electronic access control at 18 buildings and smart key technology at 13 buildings. Enclosures, perimeter gates, and secondary entry will be protected with smart key technology. Capital $12.2M, O&M $1.6M. Option 3- Recommended - Smart Key Technology Deployment. Deploy smart key technology at 31 buildings. Enclosures, perimeter gates, and secondary entry will be protected with smart key technology. Capital $8.9M, O&M $1.9M. Option 4 - Re-Key with Traditional Keys. Re-key with traditional mechanical locks & keys. Enclosures and perimeter gates will be protected with traditional mechanical locks and keys. Capital $6.9M, O&M $3.9M. | Tier 2 | See Note 16C | Minimal besides catastrophic environmental events that would impact physical security measures | Randy White, Corporate Security | See Note 19B | 8.9 | See Note 21A | 220 kV/ 66 kV | See Note 23B | 801645218 | COS-00-CS-CS-745700 | 7948 | See Note 27A | Yes | 2017 | 2017 | FRM/CRT | No | N/A | N/A | N/A | See Col. 37 | 2019 = 1,141 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2017-10-19 | No | 2020-01-01 | 2019-03-22 | Project completed ahead of schedule to ensure NERC compliance controls are functioning properly prior to NERC V6 compliance enforcement date 1/1/2020. | 3000 | 3000 | See Note 53A | 1140.735 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 1019.4953 | 121.2397 | 0 | 0 | 0 | 1140.735 | 214.444 | See Note 57A | N/A | No specific cost benefit analysis performed – Activity is addressing NERC CIP-006 V6 Physical Security compliance requirements | -1.3073e-12 | None | 49% | 51% | Column 52: Source= Unverified estimate, documents not readily available
N/A | PB-32 | Grid Infrastructure Protection Program | Not applicable at program level | Not applicable at program level | Tier Program - Upgrade physical security technology (e.g., surveillance and analytics) and infrastructure based on SCE’s Grid Infrastructure Protection Standards. The Substation Security Perimeter Enhancement Program (SSPE) seeks to minimize physical security vulnerabilities at specified SCE substations by installing and upgrading equipment to deter, delay, respond, and monitor potential intrusions and attacks. • SSPE is a strategic, multi-site approach to secure SCE substations based on criticality and potential impact of breach (e.g., to the Bulk Electric System) by upgrading physical security technology (e.g., surveillance and analytics) and infrastructure based on SCE’s Grid Infrastructure Protection Standards. • Program originated with NERC CIP-014 Physical Security Protection Project that focused only on identified substations to meet NERC/FERC compliance requirements and now seeks to address remaining sites through a minimum level of security upgrades based on risk. • Physical security measures include a combination of access control, alarms, perimeter protection (e.g., fencing, walls, barbed wire, etc.), video surveillance, and other measures. | Substation Physical Security Measures | New | PB-46 | Security | Substation Reliability | Not applicable at program level | Not applicable at program level | Risk of substation attack was evaluated as part of SCE’s Risk Assessment and Mitigation Phase (RAMP) filed with CPUC in November 2018. | Not applicable at program level | Not applicable at program level | See Note 16C | Not applicable at program level | Demetric Brown, MPO - Programs | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 23B | Not applicable at program level | COS-00-CS-CS-745400 | 7949 | See Note 27A | Yes | Not applicable at program level | Currently on-hold | FRM/CRT | No | N/A | N/A | N/A | Not applicable at program level | Not applicable at program level | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Not applicable at program level | See Note 46A | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 53A | Not applicable at program level | 8372.5878 | 12218.8948 | 13387.0503 | 17216.731 | 20060.1929 | Not Available | 71255.4567 | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not applicable at program level | Not applicable at program level | See Note 57A | N/A | Program and alternatives were evaluated as part of SCE’s Risk Assessment and Mitigation Phase (RAMP) filed with CPUC in November 2018. | See Note 60A | None | 100% | 0% | Column 8: PB-46 is the associated T&D component of this project Column 30: Estimated year for inclusion in Op Plan
N/A | PB-32.01 | CS-(ES-5080) Substation Security System Install |  |  | Tier Program: ES-5080 Substation- Install new video surveillance and Gate control as security measures required by corporate security operations for this substation. Install video and access security system within the perimeter of substation to include cameras, camera poles, field enclosures, video recorders and access gate controls and intercom units. | Substation Physical Security Measures | New | PB-46.01, PB-46.09 | Security | Substation Reliability | N/A - New. The last corporate security inspection was performed in 2017. | N/A - Largely includes installation of new equipment/technology | Risk of Substation Attack was evaluated as part of SCE’s Risk Assessment and Mitigation Phase (RAMP) filed with CPUC in November 2018. | Alternative – Augmenting protection by installing new security poles on existing foundation locations, with new cameras, new video analytics, and new IT infrastructure. Option results in perimeter equipment and coverage decrease of up to 46% due to existing pods locations. Cost: Capital: $67.4M, 5 Year O&M: $3.6M. Alternative –Use the same standards for these substations as CIP 14 sites to provide for a single security level across all identified critical BES substations. Perimeter covered at 100% with enhanced threat detection and deterrence options. Cost: Capital: $88.3M, 5 Year O&M: $4.4M. | Tier 2 | See Note 16C | Minimal besides catastrophic environmental events that would impact physical security measures | Demetric Brown, MPO - Programs | See Note 19B | See Note 17 | See Note 21A | 500/220 (kV) | See Note 23B | 801602764 | COS-00-CS-CS-745400 | 7949 | See Note 27A | Yes | 2019 | Currently on-hold | FRM/CRT | No | N/A | N/A | N/A | See Col. 37 | 2021 = 3,271 2022 = 26 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2017-08-15 | No | 2017-12-23 | 2021-08-30 | After reapproval in Feb 2020, the new in-service date was 8/30/21 and treated as a different project with an updated scope compared to 2016. | 2482 | 2482 | See Note 53A | 3297.5724 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 1500.8921 | 201.3424 | 549.1863 | 1019.9301 | 26.2215 | 3297.5724 | 792.9769 | See Note 57A | N/A | Program and alternatives were evaluated as part of SCE’s Risk Assessment and Mitigation Phase (RAMP) filed with CPUC in November 2018. | -2.5497e-12 | None | 100% | 0% | Column 8: PB-46.01 is the associated T&D component of this project, PB-46.09 is the WO replacing PB-46.01 Column 30: Estimated year for inclusion in Op Plan Column 51: This project was determined to be out of scope for NERC CIP-14 due to regulatory criteria. As a result, the remaining work was reassessed and required an updated FRM approval to continue security upgrade and replace outdated security measures. Please see ES-5080 FRM (11/11/2019) deck for additional details. Column 52: Source= FRM (11/11/2019); Represents WO level costs (i.e., Corporate Security portion of costs), Total Original Project cost is $6.147M for Corporate Security, T&D, IT elements and contingency
N/A | PB-32.02 | CS-(ES-5067) Substation Security System Install |  |  | Tier Program: ES-5067 Substation- Install new video surveillance and Gate control as security measures required by corporate security operations for this type substation. | Substation Physical Security Measures | New | PB-46.02 | Security | Substation Reliability | N/A - New. The last corporate security inspection was performed in 2017. | N/A - Largely includes installation of new equipment/technology | Risk of Substation Attack was evaluated as part of SCE’s Risk Assessment and Mitigation Phase (RAMP) filed with CPUC in November 2018. | Alternative – Augmenting protection by installing new security poles on existing foundation locations, with new cameras, new video analytics, and new IT infrastructure. Option results in perimeter equipment and coverage decrease of up to 46% due to existing pods locations. Cost: Capital: $67.4M, 5 Year O&M: $3.6M. Alternative –Use the same standards for these substations as CIP 14 sites to provide for a single security level across all identified critical BES substations. Perimeter covered at 100% with enhanced threat detection and deterrence options. Cost: Capital: $88.3M, 5 Year O&M: $4.4M. | Non-HFRA | See Note 16C | Minimal besides catastrophic environmental events that would impact physical security measures | Randy White, Corporate Security | See Note 19B | See Note 17 | See Note 21A | 500 kV | See Note 23B | 801646204 | COS-00-CS-CS-745400 | 7949 | See Note 27A | Yes | 2021 | Currently on-hold | FRM/CRT | No | N/A | N/A | N/A | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Construction (90%) | See Note 46A | 2017-09-21 | Yes | 2017-12-31 | 2023-12-30 | After reapproval in June 2021, the new in-service date was 12/31/22 and treated as a different project with an updated scope compared to 2016. | 3845 | 3227.8872 | See Note 53A | 3033.1997 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 1181.2744 | 69.5638 | 24.203 | 87.3331 | 1670.8253 | 3033.1997 | 451.2646 | See Note 57A | N/A | Program and alternatives were evaluated as part of SCE’s Risk Assessment and Mitigation Phase (RAMP) filed with CPUC in November 2018. | 3033.1997 | None | 100% | 0% | Column 8: PB-46.02 is the associated T&D component of this project Column 30: Estimated year for inclusion in Op Plan Column 51: This project was determined to be out of scope for NERC CIP-14 due to regulatory criteria. As a result, the remaining work was reassessed and required an updated FRM approval to continue security upgrade and replace outdated security measures. Please see ES-5067 FRM (06/23/2021) deck for additional details. Column 52: Source= FRM (06/23/2021); Represents WO level costs (i.e., Corporate Security portion of costs), Total Original Project cost is $14.732M for Corporate Security, T&D, IT elements
N/A | PB-33 | Transmission EOI Capital Remediation Program | Not applicable at program level | Not applicable at program level | The EOI initiative is being implemented in addition to SCE’s regular compliance and safety inspections as an added measure to further strengthen the safety and reliability of SCE assets. SCE is conducting additional, enhanced inspections of its infrastructure in HFRA. 66kV, 115kV, 220kV, 550kV | Transmission Maintenance | Replacement | Not applicable at program level | Other - See Notes | T-Line Reliability | Not applicable at program level | Not applicable at program level | Inspections | Do not perform Enhanced Overhead Inspections & Remediation, and only rely upon compliance-based inspection and maintenance programs. | Tier 2, Tier 3 | See Note 16A | Not applicable at program level | Brent Gokbudak, MPO-Project Development & Execution | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 23B | Not applicable at program level | CET-PD-WM-TP-822400; CET-PD-WM-TP-822401; CET-PD-FR-TF-822600; CET-PD-FR-TF-822601 | 8224 | See Note 27A | Yes | 2018 | 2018 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | Not applicable at program level | Not applicable at program level | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Not applicable at program level | See Note 46A | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 53A | Not applicable at program level | 273.0919 | 278.6245 | 308.4498 | 296.5673 | 312.0331 | Not Available | 1468.7665 | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not applicable at program level | Not applicable at program level | See Note 57A | N/A | No specific cost benefit analysis performed, however, SCE used a risk model to help prioritize remediations based on wildfire risk. | See Note 60A | None | 100% | 0% | Column 9: Fire Mitigation
0: N/A; Project Description 1: PB-33.01; Project Description 2: Control-Silver Peak "C" EOI Pole Replacement; Project Description 4: Bishop, Inyo County; Project Description 5: SCE is replacing all wood poles and 4/0 ACSR conductor for 3.15 circuit miles along the Control-Silver Peak "C" 55kV subtransmission line with weathered lightweight steel poles and 336 ACSR to mitigate structure deterioration and wildfire risk.; Project Description 6: Subtransmission Line; Project Description 7: Reconductor; Project Description (Cont.) 24: 902823248; Project Description (Cont.) 25: CET-PD-WM-TP-822401; Project Description (Cont.) 26: 8224; Project Status 45: Canceled; Project Status 50: Canceled; Costs 52: 3500; Costs 52.1: 3500; Costs 54: -2.7711e-13 | [16 empty] | Column 45: Cancelled and transferred to TLRR (PIN 7298) Order TD1618682 Column 52: Source= Unverified estimate, documents not readily available
0: N/A; Project Description 1: PB-33.02; Project Description 2: Control-Silver Peak "A" EOI Pole Replacement; Project Description 4: Bishop, Inyo County; Project Description 5: SCE is replacing all wood poles and 4/0 ACSR conductor for 3.25 circuit miles along the Control-Silver Peak "A" 55kV subtransmission line with weathered lightweight steel poles and 336 ACSR to mitigate structure deterioration and wildfire risk.; Project Description 6: 55kV Subtransmission Line; Project Description 7: Reconductor; Project Description (Cont.) 24: 902823249; Project Description (Cont.) 25: CET-PD-WM-TP-822401; Project Description (Cont.) 26: 8224; Project Status 45: Canceled; Project Status 50: Canceled; Costs 52: 3500; Costs 52.1: 3500; Costs 54: -5.2225e-13 | [16 empty] | Column 45: Cancelled and transferred to TLRR (PIN 7298) Order TD1618683 Column 52: Source= Unverified estimate, documents not readily available
N/A | PB-34 | Substation Battery & Charger Replacement | Not applicable at program level | Not applicable at program level | This program replaces substation batteries, battery racks, battery chargers. Drivers are equipment failure, performance, age ,and obsolescence. Batteries: 50AH-3900AH; Chargers: 12A-200A. Input Voltage 120-480V | Substation batteries, battery racks, battery chargers | Replacement | Not applicable at program level | Infrastructure Replacement | Age/Condition | Not applicable at program level | Not applicable at program level | Maintenance Inspections (e.g. voltage test, conductance readings, etc) | Not applicable at program level | Not applicable at program level | See Note 16C | Not applicable at program level | Demetric Brown, MPO - Programs | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 23B | Not applicable at program level | CET-ET-IR-ME-771601 | 7716 | See Note 27A | Not applicable at program level | Not applicable at program level | 2020 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | Not applicable at program level | Not applicable at program level | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Not applicable at program level | See Note 46A | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 53A | Not applicable at program level | 334.453 | 649.944 | 0 | 0 | 0 | Not Available | 984.397 | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not applicable at program level | Not applicable at program level | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | See Note 60A | None | 100% | 0%
N/A | PB-35 | Transmission Unplanned Capital Maintenance | Not applicable at program level | Not applicable at program level | Transmission Maintenance unplanned includes the costs to remove, replace, and retire assets on an unplanned basis. Unplanned transmission maintenance is driven by equipment maintenance breakdown; | Transmission Maintenance | Repair/ Replace | Not applicable at program level | Other - See Notes | Age/Condition | Not applicable at program level | Not applicable at program level | •Visual inspection •Intrusive pole inspection • Pole Load Calculation | Not applicable at program level | Not applicable at program level | See Note 16C | Not applicable at program level | Randy White, Corporate Security | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 23B | Not applicable at program level | CET-PD-BM-TU-TRSJAC | 3364 | See Note 27A | Not applicable at program level | Not applicable at program level | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | Not applicable at program level | Not applicable at program level | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Not applicable at program level | See Note 46A | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 53A | Not applicable at program level | 715.139 | 727.1511 | 732.4237 | 736.8798 | 745.0968 | Not Available | 3656.6904 | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not applicable at program level | Not applicable at program level | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | See Note 60A | None | 100% | 0% | Column 9: Asset Condition
N/A | PB-35.01 | Rio Hondo-Vincent No.1 Wire Replacement | 34.105, -117.981 / 34.486, -118.118 | Monte Cristo Campground E, O Angeles Forest Hwy, Los Angeles County | Emergent project to replace 2,882' span of fallen phase | Transmission line conductor installation | Replacement | None | Emergency Replacement | Age/Condition - Replace Conductor | 2017-10-01 | 55 years | N/A | Emergent replacement after equipment failure | Non-HFRA/Tier 3 | See Note 16C | High elevation & ice loading may impact asset | Oscar Santos, Asset & Engineering Strategy; David Dickerson / Mike Quinn, Transmission Wildfire Program Management | 0.55 | See Note 20B | 220 kV | See Note 22A | See Note 23B | 902450997 | CET-PD-BM-TU-TRMETE | 3364 | See Note 27A | Yes | 2018 | 2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2018 = 1,861 2019 = 35 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2018-08-14 | No | Not readily available | 2018-09-25 | N/A | Not readily available | Not Readily Available | See Note 53A | 1895.2431 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 1860.6509 | 34.5922 | 0 | 0 | 0 | 1895.2431 | 377.9298 | See Note 57A | N/A | N/A | -7.5636e-13 | None | 100% | 0%
N/A | PB-36 | Transmission Grid-Based Maintenance | Not applicable at program level | Not applicable at program level | Transmission Maintenance includes the costs to remove, replace, and retire assets on a planned basis. Planned transmission maintenance is driven by regular equipment maintenance and inspection cycles; maintenance work identified and prioritized through overhead and underground inspection programs; maintenance identified through observations by field personnel, or other activities. | Transmission Maintenance | Repair/ Replace | Not applicable at program level | Other - See Notes | T-Line Reliability | Not applicable at program level | Not applicable at program level | •Visual inspection •Intrusive pole inspection • Pole Load Calculation | Not applicable at program level | Not applicable at program level | See Note 16B | Not applicable at program level | Brent Gokbudak, MPO-Project Development & Execution | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 23B | Not applicable at program level | CET-PD-IR-TG-TRSJAC | 3364 | See Note 27A | Not applicable at program level | Not applicable at program level | 2020 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | Not applicable at program level | Not applicable at program level | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Not applicable at program level | See Note 46A | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 53A | Not applicable at program level | 4767.5467 | 4862.5916 | 4894.7651 | 4924.7621 | 4979.8111 | Not Available | 24429.4766 | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not applicable at program level | Not applicable at program level | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | See Note 60A | None | 100% | 0% | Column 9: Asset Condition
N/A | PB-36.01 | Mira Loma No.2 FAA Marker Ball Replacement | 34.010, -117.565 | Fontana/ Hesperia, San Bernardino County | Install 135 FAA Marker Balls on 17 internally rated high risk spans on Lugo-Mira Loma #2 500kV, Lugo-Mira Loma #3 500kV, and Lugo-Rancho Vista 500kV Circuits. | Marker Balls | New | None | Safety | Other- See Notes | 2019-07-31 | Program contains several assets of various ages. | N/A | Lighted Markerballs - Safety risk and Maintenance concern with this alternative | Tier 3 (15 spans); Tier 2 (2 spans) | See Note 16C | No significant environmental factors | Brent Gokbudak, MPO-Project Development & Execution | 5.3 | See Note 20B | 500 kV | See Note 22A | See Note 23B | 902319892 | CET-PD-IR-TG-TREAST | 3364 | See Note 27A | Yes | 2019-05-14 | 2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2019 = 1,362 2020 = 151 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2019-05-10 | No | 2019-03-30 | 2019-08-13 | N/A | Not readily available | Not readily available | See Note 53A | 1513.2336 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 214.2281 | 1147.4415 | 151.35 | 0.21399 | 0 | 1513.2336 | 144.8361 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | -8.9369e-13 | None | 100% | 0% | Column 10: FAA Regulation/ Recommendations
N/A | PB-36.02 | Goleta-Santa Clara No.1 FAA Marker Ball Replacement | 34.468, -119.884 / 34.302, -119.186 | Goleta, Santa Barbara County | Install 18 Markerballs (7 Orange, 5 Yellow, and 6 White), on span between towers M42T5 and M43T1 on the Goleta-Santa Clara No.1, 220kV circuit. The installation of Markerballs follows the FAA Circular recommendation and the risk analysis performed by SCE Engineering and Air Operations. | Marker Balls | New | None | Safety | Other- See Notes | N/A - New | N/A - New | FAA Risk Analysis performed by SCE Engineering and Air Operations | Followed FAA recommendations | Tier 3 | See Note 16C | Mountainous Conditions - No severe Weather expected - normal service life. | Brent Gokbudak, MPO-Project Development & Execution | Approximately 1,500 feet for total span length. | See Note 20B | 220 kV | See Note 22A | See Note 23B | 902204869 | CET-PD-IR-TG-TRNCST | 3364 | See Note 27A | Yes | 2017 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2018 = 1,063 2019 = 62 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2018-01-02 | No | 2019-12-16 | 2018-09-20 | Original Planned in-service date was a placeholder | Not readily available | Not readily available | See Note 53A | 1125.572 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 1063.4746 | 62.0974 | 0 | 0 | 0 | 1125.572 | 60.9842 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | -1.1649e-12 | None | 100% | 0% | Column 10: FAA Regulation/ Recommendations Column 51: Planned in-service date for this project was input to open the Work Order. The project had no significant delays.
N/A | PB-36.03 | Mesa-Vincent No.1 220kV: Station Fire Re-Conductor | 34.0365, -118.1097/ 34.4869, -118.1182 | Palmdale, Los Angeles County | Remove & Replace assets damaged by wildfire (2.5 Miles of double bundled 1033 ACSR conductor & miscellaneous tower lattice on one tower) between M7-T2 to M4-T4 in the Angeles National Forest (ANF) | Re-conductor | Replacement | None | Emergency Replacement | Age/Condition | 2020-10-05 | 20 years (installed 2001) | N/A | No alternatives were available, as fire damaged assets needed to be replaced | Non-HFRA/Tier 3 | See Note 16D | No significant environmental factors | Brent Gokbudak, MPO-Project Development & Execution | 2.5 Circuit Miles | See Note 20B | 220 kV | 220kV | See Note 23B | 902554722 | CET-PD-IR-TG-TRMETE | 3364 | See Note 27A | Yes | 2018 | 2018 | Other- See Notes | No | N/A | N/A | N/A | See Col. 37 | 2021 = 2,280 | N/A | N/A | NA | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | Not Available | No | 2019-12-13 | 2021-05-25 | Original Planned in-service date was a placeholder | Not readily available | Not readily available | See Note 53A | 2280.077 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 0 | 19.8919 | 2112.9732 | 147.2118 | 0 | 2280.077 | 149.5684 | See Note 57A | N/A | See Note 59A | 8.6493e-13 | None | 100% | 0% | Column 3: Start and End Point of Circuit Column 29-31: Project was not PMWIF'd as was maintenance item as a result of station fire, so date reflects internal approval Column 51: Planned in-service date for this project was input to open the Work Order. The project had no significant delays.
N/A | PB-36.04 | Lugo-Mira Loma #2 FAA Tower Lighting | 34.0105, -117.5649/ 34.3672, -117.3693 | Hesperia/ San Bernardino/ Etiwanda/ Ontario, San Bernardino County | Lighting installation to meet FAA Compliance Requirements: M29-T2, M29-T1, M28-T5, M28-T4, M28-T3, M28-T2, M28-T1, M27-T3, M27-T2, M27-T1, M26-T6, M26-T3, M26-T2, M26-T1, M25-T4, M24-T4, M26-T4, M25-T3, M26-T5, M25-T2, M25-T1, M21-T1, M20-T4, M16-T3, M16-T2 | FAA lighting installed on existing 25 Transmission Towers | Modification/Upgrade | None | Safety | Other- See Notes | 2020-07-17 | 20 years (installed 2001) | N/A | Required for FAA compliance and safety | Non-HFRA/Tier 2 | See Note 16C | No significant environmental factors | Brent Gokbudak, MPO-Project Development & Execution | See Note 19B | See Note 20B | 500 kV | 500kV | See Note 23B | 902824615 | CET-PD-IR-TG-TREAST | 3364 | See Note 27A | Yes | 2018 | 2018 | Other- See Notes | No | N/A | N/A | N/A | See Col. 37 | 2021 = 1,629 2022 = 3 | N/A | N/A | NA | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | Not Available | No | 2019-08-16 | 2021-01-23 | Original Planned in-service date was a placeholder | Not readily available | Not Readily Available | See Note 53A | 1632.0401 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 0 | 1.5537 | 1548.9612 | 78.0642 | 3.461 | 1632.0401 | 183.7062 | See Note 57A | N/A | See Note 59A | -9.5171e-13 | None | 100% | 0% | Column 3: Start and End Point of Circuit Column 10: FAA Compliance Requirements to ensure safety Column 31: Does not follow traditional approval process due to FAA requirement
N/A | PB-37 | Transmission Tower Corrosion Program | Not applicable at program level | Not applicable at program level | A total of 2,235 transmission (220 kV and above) and sub-transmission (115 kV and below) steel structures have been selected for the structural Corrosion inspection and condition assessment. These structures include 1571 Lattice Steel Towers (LST), 588 Steel Poles, 31 Contemporary Towers, 41 Portal Frame Structures and 4 Steel H-Frames. Steel poles include tubular steel poles (TSP) and light weight steel poles (LWSP), Contemporary and Portal Frames are 2-pole legged structures, and the H-Frames will include at least one steel/concrete hybrid. Several of the selected structures are located on the same service lines but the remainder will be located on various transmission and sub-transmission lines within SCE’s service territory. Many of the structures are up to 30 years old and older. The selected structures are situated in three different zones classified as High, Medium and Low Corrosion zones. These zones were developed by considering factors such as soil pH, soil resistivity, soil moisture, pollution condition, distance to coastline. The selections include voltages from 66KV, 115KV | Transmission tower | Inspection/Assessment | Not applicable at program level | Other - See Notes | Age/Condition - Replace Other T-Line Equipment | Not applicable at program level | Not applicable at program level | •Visual inspection •UT SCAN • Steel loss measurement | Not applicable at program level | Not applicable at program level | See Note 16C | Climate, moisture, pollution, soil salinity | Brent Gokbudak, MPO-Project Development & Execution | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 23B | Not applicable at program level | CET-PD-IR-TS-TRSJAC | 3364 | See Note 27A | Not applicable at program level | Not applicable at program level | 2020 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | Not applicable at program level | Not applicable at program level | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Not applicable at program level | See Note 46A | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 53A | Not applicable at program level | 4839.2142 | 3993.2915 | 5719.7821 | 5759.2331 | 5826.1756 | Not Available | 26137.6965 | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not applicable at program level | Not applicable at program level | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | See Note 60A | None | 100% | 0% | Column 9: Asset Inspection
N/A | PB-37.01 | Moorpark-Santa Clara No.1: Tower Corrosion Betterment order for inspection pilot, holding order for all TRANS FERC locations. | 34.3021, -119.1863/ 34.2807, -118.9022 | Moorpark, Ventura County & Los Angeles County | Assess towers at multiple locations for underground and above ground corrosion on structures and footings | Assess towers for corrosion to identify appropriate mitigation effort to remedy | TBD - Scope In Progress | None | Infrastructure Enhancement | T-Line Reliability | Multiple | Multiple | Visual steel loss, bore scope and UT scan (ultrasonic) | Complete tower replacement at multiple locations | Tier 2 | See Note 16C | No significant environmental factors | Brent Gokbudak, MPO-Project Development & Execution | 19A | See Note 20B | 220 kV | 220kV | See Note 23B | 903049680 | CET-PD-IR-TS-TRNCST | 3364 | See Note 27A | Yes | 2020 | 2019 | FRM/CRT | No | N/A | N/A | N/A | See Col. 37 | 2021 = 0 | N/A | N/A | NA | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | Not Available | No | N/A | 2021-12-23 | N/A | Not readily available | Not Readily Available | See Note 53A | -0.00061 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 0 | 0 | 2863.126 | -2863.1266 | 0 | -0.00061 | 0 | See Note 57A | N/A | See Note 59A | 7.0656e-14 | None | 100% | 0% | Column 3: Start and End Point of Circuit Column 45: This is a "holding" work order intended as a collection WO only; therefore there is not a construction status or associated operational dates.
N/A | PB-38 | Pothead Replacement | Not applicable at program level | Not applicable at program level | Proactively and programmatically replace aging potheads at the end of their product lifecycle. This project is almost at conclusion now. | Potheads | Replacement | Not applicable at program level | Other - See Notes | Age/Condition | Not applicable at program level | Not applicable at program level | *Visual and date analysis | Not applicable at program level | Not applicable at program level | See Note 16C | No significant environmental factors | Demetric Brown, MPO - Programs | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 23B | Not applicable at program level | CET-PD-IR-TP-788800 | 7888 | See Note 27A | Not applicable at program level | Not applicable at program level | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | Not applicable at program level | Not applicable at program level | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Not applicable at program level | See Note 46A | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 53A | Not applicable at program level | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 0 | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not applicable at program level | Not applicable at program level | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | See Note 60A | None | 100% | 0% | Column 9: Asset Condition
N/A | PB-39 | Substation Security Upgrades | Not applicable at program level | Not applicable at program level | Metal Abatement Program - This program addresses the replacement of security fence to ensure the security of substation and substation assets | Physical Security Measures | Replacement | Not applicable at program level | Security | Substation Reliability | Not applicable at program level | Not applicable at program level | Risk of Substation Attack was evaluated as part of SCE’s Risk Assessment and Mitigation Phase (RAMP) filed with CPUC in November 2018 | Not applicable at program level | Not applicable at program level | See Note 16C | Not applicable at program level | Demetric Brown, MPO - Programs | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 23B | Not applicable at program level | CET-ET-IR-ME-757301 | 7573 | See Note 27A | Not applicable at program level | Not applicable at program level | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | Not applicable at program level | Not applicable at program level | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Not applicable at program level | See Note 46A | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 53A | Not applicable at program level | 10.4339 | 787.7497 | 3441.8526 | 0 | 0 | Not Available | 4240.0362 | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not applicable at program level | Not applicable at program level | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | See Note 60A | None | 100% | 0%
0: N/A; Project Description 1: PB-39.01; Project Description 2: Rector Substation Security Upgrade; Project Description 4: Visalia, Tulare County; Project Description 5: Rector: Upgrade Security Fence and Lights to Latest security standards (4389 feet of fence); Project Description 6: Project is cancelled.; Project Description 7: Replacement; Project Description (Cont.) 24: 902157753; Project Description (Cont.) 25: CET-ET-IR-ME-757301; Project Description (Cont.) 26: 7573; Project Status 45: Canceled; Project Status 50: Canceled; Costs 52: 3446; Costs 52.1: 1840.8532; Costs 54: 637.8843 | [16 empty] | Column 52: Source= PMWIF (v1 Proj Summary); SCE provided in its Dec 2020 SRP an estimate of $3.570M which represents an earlier v0 Proj Summary prior to PWMIF. Consistent with the methodology for the July SRP, SCE provides the original project estimate from PMWIF (v1 Proj Summary)
N/A | PB-39.02 | El Nido Substation Security Upgrade | 33.895426;-118.371913 | Hawthorne, Los Angeles County | El Nido 220/66 (S): UPG Security Fence & Lights to Latest security standards (3248 feet of fence) | Physical Security Measures | Replacement | N/A | Security | Substation Reliability | 2020-07-03 | New | Risk of Substation Attack was evaluated as part of SCE’s Risk Assessment and Mitigation Phase (RAMP) filed with CPUC in November 2018 and in the 2022 RAMP. | Alternatives considered include block walls around the perimeter of the substation would address the targeted risk, theft, but the cost would not justify when looking at return-on-risk mitigated. This prefer beta fence was more cost effective and provided the necessary mitigation for the target risk. | Not applicable - No HFRA | See Note 16C | No significant environmental factors | Demetric Brown, MPO - Programs | See Note 19B | 13.6 | See Note 21A | 220kV/66kV/12kV | See Note 23B | 902157756 | CET-ET-IR-ME-757301 | 7573 | See Note 27A | Yes | 2020 | 2019 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col.37 | 2021 = 1,493 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2020-07-13 | No | 2020-12-31 | 2021-06-07 | N/A | 2622 | 971.8505 | See Note 53A | 1492.5103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.6874 | 931.424 | 518.7752 | 0.62358 | 1492.5103 | 181.1469 | See Note 57A | N/A | See Note 59A | 1.2409e-13 | None | 100% | 0% | Column 52: Source= PMWIF (v0 Project Summary)
0: N/A; Project Description 1: PB-39.03; Project Description 2: Control Substation Security Upgrade; Project Description 4: Bishop, Inyo County; Project Description 5: Control 115/115 (T): UPG Security Fence & Lights to Latest security standards (2731 feet of fence); Project Description 6: Upgrade substation security fence and lighting due to high left and brake ins; Project Description 7: Replacement; Project Description (Cont.) 24: 902157757; Project Description (Cont.) 25: CET-ET-IR-ME-757301; Project Description (Cont.) 26: 7573; Project Status 45: Pre-construction; Project Status 50: 2024-05-31; Costs 52: 3083; Costs 52.1: 2556.8263; Costs 54: 1983.8384 | [16 empty] | Column 52: Source= PMWIF (v0 Project Summary)
0: N/A; Project Description 1: PB-39.04; Project Description 2: Magunden Substation Security Upgrade; Project Description 4: Bakersfield, Kern County; Project Description 5: Magunden 500/220 (T): UPG Security Fence & Lights to Latest security standards (5476 feet of fence); Project Description 6: Project is cancelled.; Project Description 7: Replacement; Project Description (Cont.) 24: 902157754; Project Description (Cont.) 25: CET-ET-IR-ME-757301; Project Description (Cont.) 26: 7573; Project Status 45: Canceled; Project Status 50: Canceled; Costs 52: 4390; Costs 52.1: 4184.3022; Costs 54: 0 | [16 empty] | Column 52: Source= C55
0: N/A; Project Description 1: PB-39.05; Project Description 2: Victor Substation Security Upgrade; Project Description 4: Victorville, San Bernardino County; Project Description 5: Victor 220/115 (S): Upgrade Security fence and lights; Project Description 6: Upgrade substation security fence and lighting due to high left and brake ins; Project Description 7: Replacement; Project Description (Cont.) 24: 902831766; Project Description (Cont.) 25: CET-ET-IR-ME-757301; Project Description (Cont.) 26: 7573; Project Status 45: Operational; Project Status 50: 2021-02-05; Costs 52: 73; Costs 52.1: 64.7755; Costs 54: 66.4671 | [16 empty] | Column 52: Source= PMWIF (C55)
N/A | PB-39.06 | Red Bluff Substation Security Upgrade | 33.672, -115.559 | Desert Center, Riverside County | Red Bluff: UPG Security Fence & Lights to Latest security standards | Substation Castle Spike Installation | Replacement | None | Security | Substation Reliability | 03/07/2022 | New | Risk of Substation Attack was evaluated as part of SCE’s Risk Assessment and Mitigation Phase (RAMP). | See Note 14A | Non HFRA | See Note 16C | High Wind Events, Extreme Temperature Conditions | Demetric Brown, MPO - Programs | See Note 19B | 75.7 | See Note 21A | 500kV - 220kV, 1120 MVA | See Note 23B | 903153733 | CET-ET-IR-ME-757300 | 7573 | See Note 27A | Yes | 2020 | 2021 | Annual Capital Operating Plan Process | N/A | N/A | N/A | N/A | See Col. 37 | 2022 = 1,059 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2022-03-29 | Yes | 2022-12-31 | 2022-08-22 | N/A | 668 | 668 | See Note 53A | 1059.477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5811 | 13.7381 | 1045.1578 | 1059.477 | 78.8207 | See Note 57A | N/A | See Note 59A | 6.9849e-13 | None | 100% | 0% | Column 52: Source = PMWIF (Investment Summary from 07/21/2020)
N/A | PB-39.07 | Santiago Substation Security Upgrade | 33.665, -117.768 | Irvine, Orange County | Santiago: UPG Security Fence & Lights to Latest security standards | Physical Security Measures | Replacement | None | Security | Substation Reliability | 08/06/2022 | New | Risk of Substation Attack was evaluated as part of SCE’s Risk Assessment and Mitigation Phase (RAMP). | See Note 14A | Non HFRA | See Note 16C | No Significant Environmental Factors | Demetric Brown, MPO - Programs | See Note 19B | 18.1 | See Note 21A | 230 kV | See Note 23B | 903153774 | CET-ET-IR-ME-757300 | 7573 | See Note 27A | Yes | 2020 | 2021 | Annual Capital Operating Plan Process | N/A | N/A | N/A | N/A | See Col. 37 | 2022 = 1,190 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2022-08-08 | Yes | 2022-12-31 | 2022-12-21 | N/A | 76 | 41.8 | See Note 53A | 1189.6496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1027 | 75.602 | 1112.945 | 1189.6496 | 90.6205 | See Note 57A | N/A | See Note 59A | 0 | None | 100% | 0% | Column 52: Source = PMWIF (Investment Summary from 08/31/2020)
0: N/A; Project Description 1: PB-39.08; Project Description 2: Laguna Bell 220/66 kV: Beta fence with automatic gate and perimeter security lights; Project Description 4: Commerce, Los Angeles County; Project Description 5: Laguna Bell 220/66kV: Replace existing chain link fence to beta fence for 5,000 linear ft, (1) automatic gate and lights; Project Description 6: CU Theft; Project Description 7: Upgrade; Project Description (Cont.) 24: 7573LagunaBell; Project Description (Cont.) 25: CET-ET-IR-ME-757300; Project Description (Cont.) 26: 7573; Project Status 45: Planning; Project Status 50: 2025-12-31; Costs 52: 4900; Costs 52.1: 1568; Costs 54: 1568.0349 | [16 empty] | Column 52: Source= PMWIF (v.0 Project Summary)
N/A | PB-40 | Colorado River Corridor RAS Program | Not applicable at program level | Not applicable at program level | Duplicate analytic functionality of the Colorado River Corridor RAS within SCE's Centralized Remedial Action Scheme (CRAS) platform. Monitors for outages of 500 kV transmission lines linking Colorado River, Red Bluff, and Devers Substations and trips generation at Colorado River Substation. Project is scalable and will evolve as needed to include future generation projects at Colorado River, Red Bluff, and other points of interconnection along the Eastern transmission corridor. This is a protection/IT project consisting of protective relays, telecom network circuits and terminal equipment, and central processing architecture at GCC and IOC. Protects 500 kV transmission lines from overloads caused by generation connected to the SCE grid at the Colorado River 230 kV bus, but is scalable to include interconnections at other locations and voltage levels. | RAS Platform | New | Not applicable at program level | Other - See Notes | Special Protection Scheme | Not applicable at program level | Not applicable at program level | Load Flow, Dynamic Stability | N/A - Project modernizes existing RAS to latest SCE standard CRAS platform | Not applicable at program level | See Note 16C | Not applicable at program level | Demetric Brown, MPO - Programs | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 23B | Not applicable at program level | CET-ET-GA-CR-766600 | 7666 | See Note 27A | Not applicable at program level | Not applicable at program level | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | Not applicable at program level | Not applicable at program level | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Not applicable at program level | See Note 46A | 2017-07-31 | Not applicable at program level | Not applicable at program level | Not applicable at program level | Delays to align schedule with generation interconnection customers; analytic change not included in original scope requested by SCE Grid Ops. | Not applicable at program level | Not applicable at program level | See Note 53A | Not applicable at program level | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 0 | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not applicable at program level | Not applicable at program level | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | See Note 60A | None | 100% | 0% | Column 9: Generator Interconnection Column 31:
N/A | PB-40.01 | Colorado River Substation RAS Project - Phase 1 | 33.589, -114.814 | Desert Center (to the east)/ North Palm Springs (to the west), Riverside County | Duplicate analytic functionality of the Colorado River Corridor RAS within SCE's Centralized Remedial Action Scheme (CRAS) platform. Monitors for outages of 500 kV transmission lines linking Colorado River, Red Bluff, and Devers Substations and trips generation at Colorado River Substation. Project is scalable and will evolve as needed to include future generation projects at Colorado River, Red Bluff, and other points of interconnection along the Eastern transmission corridor. This is a protection/IT project consisting of protective relays, telecom network circuits and terminal equipment, and central processing architecture at GCC and IOC. Protects 500 kV transmission lines from overloads caused by generation connected to the SCE grid at the Colorado River 230 kV bus, but is scalable to include interconnections at other locations and voltage levels. | Multiple relays for line outage monitoring and generator tripping; telecom circuits and terminal equipment | New | PB-05.01, PB-19.03, PB-40.02, PB-40.03, SP-02, SP-18, SP-21, SP-33, SP-37, SP-39, SP-42, SP-44, SP-55, SP-56, SP-63, SP-89, SP-90, SP-113 | Other - See Notes | Special Protection Scheme | 2019-05-08 | 2 years | Load Flow, Dynamic Stability | N/A - Project modernizes existing RAS to latest SCE standard CRAS platform | Non-HFRA | See Note 16C | High Wind Events, Extreme Temperature Conditions, High Seismic Area, Desert Region | Demetric Brown, MPO - Programs | See Note 19B | See Note 20B | See Note 21A | 220 kV | See Note 23B | 901292691 | CET-ET-GA-CR-766600 | 7666 | See Note 27A | Yes | 2016 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2019 = 3,462 2020 = 5 2021 = 1 2022 = 1 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2017-07-31 | No | 2018-05-02 | 2019-05-23 | Delays to align schedule with generation interconnection customers; analytic change not included in original scope requested by SCE Grid Ops. | 2435 | 2435 | See Note 53A | 3468.5057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2638.3403 | 823.9058 | 4.9416 | 0.56472 | 0.75329 | 3468.5057 | 1007.241 | See Note 57A | 1 | See Note 59A | -7.4835e-12 | None | 100% | 0% | Column 9: Generator Interconnection Column 52: Source= PMWIF (v1 Proj Summary); Represents WO level cost estimate; total project cost including non-TD elements is $22.299M
N/A | PB-40.02 | Devers Substation RAS Project - Phase 1 | 33.935, -116.578 | Desert Center (to the east)/ North Palm Springs (to the west), Riverside County | Duplicate analytic functionality of the Colorado River Corridor RAS within SCE's Centralized Remedial Action Scheme (CRAS) platform. Monitors for outages of 500 kV transmission lines linking Colorado River, Red Bluff, and Devers Substations and trips generation at Colorado River Substation. Project is scalable and will evolve as needed to include future 500/230 kV transformer outage contingencies and generation projects at Colorado River, Red Bluff, and other points of interconnection along the Eastern transmission corridor. This is a protection/IT project consisting of protective relays, telecom network circuits and terminal equipment, and central processing architecture at GCC and IOC. Protects 500 kV transmission lines from overloads caused by generation connected to the SCE grid at the Colorado River 230 kV bus, but is scalable to include interconnections at other locations and voltage levels. | Multiple relays for line outage monitoring and generator tripping; telecom circuits and terminal equipment | New | PB-05.01, PB-40.01, PB-40.03, SP-02, SP-18, SP-21, SP-33, SP-37, SP-39, SP-42, SP-44, SP-55, SP-56, SP-63, SP-89, SP-90, SP-113 | Other - See Notes | Special Protection Scheme | 2019-05-15 | 2 years | Load Flow, Dynamic Stability | N/A - Project modernizes existing RAS to latest SCE standard CRAS platform | Non-HFRA | See Note 16C | High Wind Events, Extreme Temperature Conditions, High Seismic Area, Desert Region | Demetric Brown, MPO - Programs | See Note 19B | See Note 20B | See Note 21A | 500kV, 220kV, 115kV, 33kV, 12kV | See Note 23B | 901292692 | CET-ET-GA-CR-766601 | 7666 | See Note 27A | Yes | 2016 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2019 = 1,679 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2017-09-21 | No | 2016-06-01 | 2019-05-23 | Delays to align schedule with generation interconnection customers; analytic change not included in original scope requested by SCE Grid Ops. | 2395 | 2395 | See Note 53A | 1678.8157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1409.3196 | 269.3576 | 0.13851 | 0 | 5.8208e-14 | 1678.8157 | 490.894 | See Note 57A | N/A | See Note 59A | 7.1557e-13 | None | 100% | 0% | Column 9: Generator Interconnection Column 52: Source= PMWIF (v1 Proj Summary); Represents WO level cost estimate; total project cost including non-TD elements is $22.299M; SCE provided in its Dec 2020 SRP an estimate of $66M which represents an earlier PMWIF v0 Proj Summary. Consistent with the July SRP methodology, SCE provides the estimate from the revised PMWIF (v1 Proj Summary)
N/A | PB-40.03 | Red Bluff Substation RAS Project - Phase 1 | 33.672, -115.559 | Desert Center (to the east)/ North Palm Springs (to the west), Riverside County | Duplicate analytic functionality of the Colorado River Corridor RAS within SCE's Centralized Remedial Action Scheme (CRAS) platform. Monitors for outages of 500 kV transmission lines linking Colorado River, Red Bluff, and Devers Substations and trips generation at Colorado River Substation. Project is scalable and will evolve as needed to include future 500/230 kV transformer outage contingencies and generation projects at Colorado River, Red Bluff, and other points of interconnection along the Eastern transmission corridor. This is a protection/IT project consisting of protective relays, telecom network circuits and terminal equipment, and central processing architecture at GCC and IOC. Protects 500 kV transmission lines from overloads caused by generation connected to the SCE grid at the Colorado River 230 kV bus, but is scalable to include interconnections at other locations and voltage levels. | Multiple relays for line outage monitoring and generator tripping; telecom circuits and terminal equipment | New | PB-05.01, PB-40.01, PB-40.03, SP-02, SP-18, SP-21, SP-33, SP-37, SP-39, SP-42, SP-44, SP-55, SP-56, SP-63, SP-89, SP-90, SP-113 | Other - See Notes | Special Protection Scheme | 2019-05-06 | 2 years | Load Flow, Dynamic Stability | N/A - Project modernizes existing RAS to latest SCE standard CRAS platform | Non-HFRA | See Note 16C | High Wind Events, Extreme Temperature Conditions, High Seismic Area, Desert Region | Demetric Brown, MPO - Programs | See Note 19B | See Note 20B | See Note 21A | 500kV, 220kV | See Note 23B | 901292693 | CET-ET-GA-CR-766602 | 7666 | See Note 27A | Yes | 2016 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2019 =2,941 2020 = 28 2021 = -5 2022 = 2 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2017-09-05 | No | 2016-06-01 | 2019-05-23 | Delays to align schedule with generation interconnection customers; analytic change not included in original scope requested by SCE Grid Ops. | 2746 | 2746 | See Note 53A | 2966.5688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2447.3421 | 493.7335 | 28.3929 | -4.7246 | 1.8249 | 2966.5688 | 911.5579 | See Note 57A | N/A | See Note 59A | -1.319e-12 | None | 100% | 0% | Column 9: Generator Interconnection Column 52: Source= PMWIF (v1 Proj Summary); Represents WO level cost estimate; total project cost including non-TD elements is $22.299M; SCE provided in its Dec 2020 SRP an estimate of $66M which represents an earlier PMWIF v0 Proj Summary. Consistent with the July SRP methodology, SCE provides the estimate from the revised PMWIF (v1 Proj Summary)
N/A | PB-41 | North of Lugo Corridor CRAS Program | Not applicable at program level | Not applicable at program level | Duplicate analytic functionality of the existing High Desert Power Plant (HDPP) RAS, existing Mojave Desert RAS and the proposed Calcite RAS within SCE's Centralized Remedial Action Scheme (CRAS) platform. Monitors for outages of 220 kV and 115 kV transmission lines linking Kramer, Victor, and Lugo Substations as well as both 500/220 kV transformers at Lugo substation and trips generations with Point of Interconnection (POI) at Kramer and Victor Substations. Project is scalable and will evolve as needed to include future generation projects with POI at Kramer, Victor, Roadway and Calcite Substations of interconnection within the North of Lugo (NOL) planning area. This is a protection/IT project consisting of protective relays, telecom network circuits and terminal equipment, and central processing architecture at GCC and IOC. Protects 220 and 115 kV transmission lines as well as both Lugo 500/220 kV transformers from overloads and system instability caused by generation connected to the SCE grid in the North of Kramer and Lugo Hub area, but is scalable to include future interconnections at other locations and voltage levels. | Multiple relays for line and transformer outage and monitoring and generator tripping; telecom circuits and terminal equipment | New | SP-01, SP-35, SP-40, SP-41, SP-45, SP-48, SP-51, SP-54, SP-57, SP-62, SP-64, SP-65, SP-73, SP-82, SP-86, SP-93, SP-95, SP-116 | Other - See Notes | Special Protection Scheme | Not applicable at program level | Not applicable at program level | Load Flow, Dynamic Stability, Short Circuit Duty | Not applicable at program level | Not applicable at program level | See Note 16C | Not applicable at program level | Demetric Brown, MPO - Programs | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 23B | Not applicable at program level | CET-ET-GA-CR-999999 | 9999 | Corr. From 8350 to 9999 | Not applicable at program level | Not applicable at program level | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | Not applicable at program level | Not applicable at program level | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Not applicable at program level | See Note 46A | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 53A | Not applicable at program level | 0 | 0 | 0 | 3000 | 3000 | Not Available | 6000 | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not applicable at program level | Not applicable at program level | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | See Note 60A | None | 100% | 0% | Column 9: Generator Interconnection
N/A | PB-42 | Tower Electrical Metallic Tubing (EMT) Program | Not applicable at program level | Not applicable at program level | Tower Extra High Voltage Medium Tanget Towers (EMT) had an inherent design flaw which under certain high wind- heavy loading conditions these structures had a tendency to fail. In 2006 a program was initiated to design and retrofit with a strengthening effort for these towers and called for the towers to be retro-fitted with additional thicker steal lattice members and doubled up steel members in some instances. The areas mostly effected were 500KV EMT towers in the outlying areas of the Mojave Desert and Palm Springs-Blythe service areas. | EMT Tower | Retrofit | Not applicable at program level | Other - See Notes | T-Line Reliability | Not applicable at program level | Not applicable at program level | Engineering structural analysis | Not applicable at program level | Not applicable at program level | See Note 16C | Not applicable at program level | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 23B | Not applicable at program level | CET-PD-IR-TP-789400 | 7894 | See Note 27A | Not applicable at program level | Not applicable at program level | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | Not applicable at program level | Not applicable at program level | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Not applicable at program level | See Note 46A | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 53A | Not applicable at program level | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 0 | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not applicable at program level | Not applicable at program level | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | See Note 60A | None | 100% | 0% | Column 9: Asset Condition
N/A | PB-42.01 | Chevron Refinery EMT Tower Replacement | 33.903, -118.402 / 33.895, -118.372 | El Segundo, CA, Los Angeles County | Chevmain-El Nido 220 kV: Pole Replace - EL SEGUNDO AESTHETIC TOWER REPLACEMENT ON CHEVRON PROPERTY Construct a retaining wall and remove/replace landscaping material at location of tower M0-2. | EMT Tower | Replacement | None | Infrastructure Replacement | Age/Condition | 2019-11-12 | > 50 Years | Engineering structural analysis | Structure replacement | Non-HFRA | See Note 16C | Salt Corrosion (Coastal Areas), Air particulate levels, High Seismic | Demetric Brown, MPO - Programs | 0.6 | See Note 20B | 220 kV | See Note 22A | See Note 23B | 902153644 | CET-PD-IR-TP-789400 | 7894 | See Note 27A | Yes | 2017-04-07 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2018 =15,287 2019 = 109 2020 = -1 2021 = -16 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2017-10-02 | No | 2018-03-01 | 2018-03-05 | N/A | 6626 | 6626 | See Note 53A | 15379.4762 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 15287.2064 | 108.8049 | -0.92183 | -15.6134 | 0 | 15379.4762 | 2262.8488 | See Note 57A | N/A | No specific project cost benefit performed; See note 59A | -2.1537e-12 | None | 100% | 0% | Column 52: Source= v2 Project Summary
N/A | PB-43 | Transmission Overhead Conductor Infrastructure Replacement | Not applicable at program level | Not applicable at program level | Proactive replacement of targeted overhead conductor sections. Reasons for replacement are referenced in the TIR overview | Overhead Conductor | Replacement | Not applicable at program level | Infrastructure Replacement | Age/Condition - Replace Conductor | Not applicable at program level | Not applicable at program level | • Visual inspection • IR/Corona scan • Pole loading • Load flow power calcs | Not applicable at program level | Not applicable at program level | See Note 16C | Not applicable at program level | Demetric Brown, MPO - Programs | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 23B | Not applicable at program level | CET-PD-IR-TP-789000 | 7890 | See Note 27A | Not applicable at program level | Not applicable at program level | 2018 | Annual Capital Operating Plan Process, Contractual arrangement with third-party | No | N/A | N/A | N/A | Not applicable at program level | Not applicable at program level | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Not applicable at program level | See Note 46A | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 53A | Not applicable at program level | 401 | 0 | 0 | 0 | 0 | Not Available | 401 | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not applicable at program level | Not applicable at program level | See Note 57A | N/A | See Note 59A | See Note 60A | None | 100% | 0%
0: N/A; Project Description 1: PB-43.01; Project Description 2: Chevmain-El Nido Reconductor; Project Description 4: Los Angeles County; Project Description 5: Chevmain-El Nido 220 kV lines: Reconductor will go from El Segundo Substation to Chevmain and from Chevmain to Parkway Station. Reconductor approximately 3600 feet of 2-1033.; Project Description 6: Overhead Conductor; Project Description 7: Reconductor; Project Description (Cont.) 24: 902182211; Project Description (Cont.) 25: CET-PD-IR-TP-789000; Project Description (Cont.) 26: 7890; Project Status 45: Engineering more than 50% completed; Project Status 50: 2025-04-25; Costs 52: 117; Costs 52.1: 117; Costs 54: 8.855 | [16 empty] | Column 52: Source= PMWIF (v0 Project Summary)
0: N/A; Project Description 1: PB-43.02; Project Description 2: Chevmain-El Segundo Reconductor; Project Description 4: Los Angeles County; Project Description 5: Chevmain-El Segundo 220 kV lines: Reconductor will go from El Segundo Substation to Chevmain and from Chevmain to Parkway Station. Reconductor approximately 3600 feet of 2-1033.; Project Description 6: Overhead Conductor; Project Description 7: Reconductor; Project Description (Cont.) 24: 902182209; Project Description (Cont.) 25: CET-PD-IR-TP-789000; Project Description (Cont.) 26: 7890; Project Status 45: Engineering more than 50% completed; Project Status 50: 2025-04-25; Costs 52: 117; Costs 52.1: 117; Costs 54: 121.9949 | [16 empty] | Column 52: Source= PMWIF (v0 Project Summary)
0: N/A; Project Description 1: PB-43.03; Project Description 2: El Nido-El Segundo Reconductor; Project Description 4: Los Angeles County; Project Description 5: El Nido-El Segundo 220 kV lines: Reconductor will go from El Segundo Substation to Chevmain and from Chevmain to Parkway Station. Reconductor approximately 3600 feet of 2-1033.; Project Description 6: Overhead Conductor; Project Description 7: Reconductor; Project Description (Cont.) 24: 902182210; Project Description (Cont.) 25: CET-PD-IR-TP-789000; Project Description (Cont.) 26: 7890; Project Status 45: Engineering more than 50% completed; Project Status 50: 2025-04-25; Costs 52: 117; Costs 52.1: 117; Costs 54: 7.3883 | [16 empty] | Column 52: Source= PMWIF (v0 Project Summary)
N/A | PB-43.04 | Rector-Springville Shield Wire Replacement | 36.107945;-118.938338 | Woodville to Frazier Valley (Tulare Co.) | Springville 220kV from M171-T4X to Springville Substation (approximately 25 circuit miles). Transmission Engineering recommends Transmission replace 25 miles of shield wire based on 3rd Party engineering evaluation. | Replace 25 miles of shield wire | Shield Wire Replacement | N/A | Infrastructure Enhancement | Age/Condition - Replace Conductor | 2019-03-14 | 95 | Circuit reliability history and 3rd party evaluation | There were not any alternative solutions or costs based on Engineering’s initial evaluation. | HFTD Tier 2 | See Note 16B | Extreme Temperature Conditions | Demetric Brown, MPO - Programs | 25 Miles | See Note 20B | 220kV | See Note 22A | See Note 23B | 903125790 | CET-PD-IR-TP-789000 | 7890 | See Note 27A | Yes | 2017 | 2020 | See Note 31A | No | N/A | N/A | N/A | See Col.37 | 2022 = 4,929 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2021-07-20 | Yes | 2021-12-31 | 2022-01-28 | N/A | 3243 | 3243 | See Note 53A | 4929.4998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.55905 | 3305.6339 | 1623.3068 | 4929.4998 | 312.1633 | See Note 57A | N/A | See note 59A | -2.3283e-12 | None | 100% | 0% | Column 52: Source = PMWIF (06/16/2020 Investment Summary)
N/A | PB-44 | Transmission Planned Maintenance - Pole Replacement | Not applicable at program level | Not applicable at program level | Replace poles not due to deterioration such as freeway crossing, major thoroughfare and critical crossings. Wood poles replaced with engineered steel poles for safety and reliability. | Transmission Poles | Replacement | Not applicable at program level | Safety | Age/Condition - Replace Wood Poles | Not applicable at program level | Not applicable at program level | • Visual inspection • Pole loading | Not applicable at program level | Not applicable at program level | See Note 16C | Not applicable at program level | Demetric Brown, MPO - Programs | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 23B | Not applicable at program level | CET-PD-IR-TP-789100 | 7891 | See Note 27A | Not applicable at program level | Not applicable at program level | Pre-2017 | Annual Capital Operating Plan Process, Contractual arrangement with third-party | No | N/A | N/A | N/A | Not applicable at program level | Not applicable at program level | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Not applicable at program level | See Note 46A | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 53A | Not applicable at program level | 0 | 0 | 0 | 0 | 0 | Not Available | 0 | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not applicable at program level | Not applicable at program level | See Note 57A | N/A | See Note 59A | See Note 60A | None | 0% | 100%
N/A | PB-44.01 | Kramer-Cool Water Pole Replacement | 34.989, -117.543 / 34.861, -116.854 | San Bernardino County | Replace 70-foot LST with 80-foot TSP at Route 58/395 at Kramer Junction; Install interset TSP and replace H-frame structure north of Route; Replace 3-pole structure with TSP South of I-15 FWY | Transmission Poles | Replacement | None | Infrastructure Replacement | Age/Condition - Replace Steel Poles | 2020-04-09 | 56 | N/A | Replace existing structures with engineered steel poles | Non-HFRA | See Note 16C | High Wind Events, Extreme Temperature Conditions, Air particulate levels | Demetric Brown, MPO - Programs | APPROXIMATELY 1,600 CIRCUIT FEET | See Note 20B | 115 kV | See Note 22A | See Note 23B | TD714268 | CET-PD-IR-TP-789100 | 7891 | See Note 27A | Yes | 2018-11-27 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2019 = 1,789 2020 = -129 | N/A | N/A | N/A | ADVICE 3876-E | 2018-10-12 | Exempt: Not subject to GO 131-D licensing | 2018 | Operational | See Note 46A | 2018-11-27 | No | 2018-12-31 | 2019-05-10 | Delay in receiving Cal Trans permit and availability of outage window | 149 | 149 | See Note 53A | 1659.7079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 828.7088 | 960.1497 | -129.1506 | 0 | 0 | 1659.7079 | 432.7242 | See Note 57A | N/A | See Note 59A | 2.3283e-13 | None | 0% | 100% | Column 9: Grid Hardening at transportation corridorColumn 52: Source= PMWIF (v1 Proj Summary); SCE provided in its Feb 2021 Supplement a cost estimate of $833k which represents a later project estimate (11/27/2018 from WO Plant Forecast). Consistent with the July SRP methodology, SCE provides the original cost from the PMWIF (v1 Proj Summary)
0: N/A; Project Description 1: PB-44.02; Project Description 2: Control-Silver Peak-Zack Pole Replacement; Project Description 4: San Bernardino County, City of Barstow, City of Apple Valley, City of Hesperia, City of Victorville, City of Adelanto, Clark County, Nevada, Boulder City, Nevada; Project Description 5: Control-Silver Peak-Zack 55 kV: Pole Replace - CAP ON RAMP CIRCUIT REBUILD CONTROL-SILV; Project Description 6: Transmission Poles; Project Description 7: Replacement; Project Description (Cont.) 24: TD788702; Project Description (Cont.) 25: CET-PD-IR-TP-789100; Project Description (Cont.) 26: 7891; Project Status 45: Planning; Project Status 50: 2024-12-05; Costs 52: 1351; Costs 52.1: 1351; Costs 54: 161.1251 | [16 empty] | Column 52: Source= Unverified system estimate
N/A | PB-44.03 | Kramer-Tortilla 115 kV: Pole Replacement | 34.989, -117.543 / 34.863, -117.031 | Barstow, San Bernardino County | Replace freeway crossings with double circuit Tubular Steel Poles | Transmission Poles | Replacement | None | Infrastructure Enhancement | T-Line Reliability | 2017-02-09 | Between 40 and 65 years | Routine visual and intrusive inspections | N/A | Non HFRA | See Note 16C | High Wind Events, Extreme Temperature Conditions, High Fire Area | Demetric Brown, MPO - Programs | See Note 19B | See Note 20B | See Note 21A | See Note 22A | See Note 23B | TD714263 | CET-PD-IR-TP-789100 | 7891 | See Note 27A | Yes | 2016 | 2018 | Annual Capital Operating Plan Process | N/A | N/A | N/A | N/A | See Col. 37 | 2022 = 1,319 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | Not Available | Yes | 2017-12-31 | 2022-02-10 | Material Delays, resource constraints, budget cut, and coordination with other projects | 10 | 10 | See Note 53A | 1318.6805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300.5686 | 247.9435 | 244.155 | 289.7816 | 236.2319 | 1318.6805 | 418.3323 | See Note 57A | N/A | See Note 59A | -1.8626e-12 | None | 0% | 100% | Column 52: Source = PMWIF (Project Summary V.0)
N/A | PB-45 | NERC CIP Physical Security Project | Not applicable at program level | Not applicable at program level | NERC CIP-14 Program: Substation ¦ Control Center: • Replace and or modify substation perimeter with concrete wall. • Replace and or modify gates with auto and manual gates. • Install AC panel and power, pole foundations, conduit and conductor for security requirements. | Physical Security Measures | New | PB-30 | Security | NERC CIP Compliance | Not applicable at program level | Not applicable at program level | N/A -- To meet North American Electric Reliability Corporation (NERC) Critical Infrastructure Protection (CIP-014) Physical Security Reliability Standard Approved by the Federal Energy Regulatory Commission (FERC) Order 802 - (May 2014) SCE is required to implement NERC CIP-014 (Physical Security Protection) standards at vulnerable substations to protect them from foreseeable threats | Alternative – Security fence, proactive detection, active deterrence and EMS protection. Cost $85.0M Alternative – Block wall, proactive detection, active deterrence, EMS protection and multiple & redundant security systems. Cost $102.2M | Not applicable at program level | See Note 16C | Minimal besides catastrophic environmental events that would impact physical security measures | Demetric Brown, MPO - Programs | Not applicable at program level | Various locations | See Note 21A | Not applicable at program level | See Note 23B | Not applicable at program level | 5 separate CWBS | 7820 | See Note 27A | Yes | 2015 | Pre-2017 | FRM/CRT | No | N/A | N/A | N/A | Not applicable at program level | Not applicable at program level | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Not applicable at program level | See Note 46A | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 53A | Not applicable at program level | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not applicable at program level | See Note 57A | N/A | No specific cost benefit analysis performed – Activity is addressing NERC CIP-014 Physical Security compliance requirements | See Note 60A | None | 100% | 0% | Column 1: Prior ID SP-20 in 12/1/2020 SRP, corrected to Program Blanket Column 5: Largely includes installation of new equipment/technology Column 8: Related to PB-30 which is the Corporate Security component of project Column 9: To reduce security and operational risk to the Bulk Electric System (BES) by designing, installing, and commissioning integrated physical security systems at locations which will fall under the impending NERC CIP-014 Physical Security standard (R5 - https://www.nerc.com/pa/Stand/Reliability%20Standards/CIP-014-2.pdf) , as identified by SCE and mandated by the North American
N/A | PB-45.01 | NERC CIP Physical Security Project (FERC Order 802): CS-(ES-5069) |  |  | ES 5069 Substation ¦ Control Center: • Replace and or modify substation perimeter with concrete wall. • Replace and or modify gates with auto and manual gates. • Install AC panel and power, pole foundations, conduit and conductor for security requirements. | Substation; see "Project description | New | PB-30.02 | Security | NERC CIP Compliance | N/A - Largely includes installation of new equipment/technology | N/A - Largely includes installation of new equipment/technology | N/A -- To meet North American Electric Reliability Corporation (NERC) Critical Infrastructure Protection (CIP-014) Physical Security Reliability Standard Approved by the Federal Energy Regulatory Commission (FERC) Order 802 - (May 2014) SCE is required to implement NERC CIP-014 (Physical Security Protection) standards at vulnerable substations to protect them from foreseeable threats | Recommended – Block wall, proactive detection, active deterrence and EMS protection. Cost $96.9M Alternative – Security fence, proactive detection, active deterrence and EMS protection. Cost $85.0M Alternative – Block wall, proactive detection, active deterrence, EMS protection and multiple & redundant security systems. Cost $102.2M | Non-HFRA | See Note 16C | Minimal besides catastrophic environmental events that would impact physical security measures | Demetric Brown, MPO - Programs | See Note 19B | 102.1 | See Note 21A | 500 kV/ 220 kV | See Note 23B | 901656354 | CET-ET-IR-ME-782001 | 7820 | See Note 27A | Yes | 2015 | Pre-2017 | FRM/CRT | No | N/A | N/A | N/A | See Col. 37 | 2018 = 13,435 2019 = 483 2020 = 176 2021 = 16 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2017-10-02 | No | 2018-11-16 | 2018-12-03 | N/A | 16008 | 13626.6514 | See Note 53A | 14110.9217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13434.9581 | 483.3674 | 176.3977 | 16.1984 | 0 | 14110.9217 | 1460.3868 | See Note 57A | N/A | No specific cost benefit analysis performed – Activity is addressing NERC CIP-014 Physical Security compliance requirements | -9.3055e-12 | None | 100% | 0% | Column 1: Prior ID SP-20 in 12/1/2020 SRP, corrected to Program Blanket Column 8: Related to PB-30.02 which is the Corporate Security component of project Column 9: To reduce security and operational risk to the Bulk Electric System (BES) by designing, installing, and commissioning integrated physical security systems at locations which will fall under the impending NERC CIP-014 Physical Security standard (R5 - https://www.nerc.com/pa/Stand/Reliability%20Standards/CIP-014-2.pdf) , as identified by SCE and mandated by the North American Column 52: Source= PMWIF (v0 Proj Summary); Represents WO level cost estimate; total project cost including non-TD elements is $19.198M
N/A | PB-45.02 | NERC CIP Physical Security Project (FERC Order 802): CS- (ES-5050) |  |  | ES 5050 Substation ¦ Control Center: • Replace and or modify substation perimeter with concrete wall. • Replace and or modify gates with auto and manual gates. • Install AC panel and power, pole foundations, conduit and conductor for security requirements. | Substation; see "Project description | New | PB-30.03 | Security | NERC CIP Compliance | N/A - Largely includes installation of new equipment/technology | N/A - Largely includes installation of new equipment/technology | N/A -- To meet North American Electric Reliability Corporation (NERC) Critical Infrastructure Protection (CIP-014) Physical Security Reliability Standard Approved by the Federal Energy Regulatory Commission (FERC) Order 802 - (May 2014) SCE is required to implement NERC CIP-014 (Physical Security Protection) standards at vulnerable substations to protect them from foreseeable threats | Recommended – Block wall, proactive detection, active deterrence and EMS protection. Cost $96.9M Alternative – Security fence, proactive detection, active deterrence and EMS protection. Cost $85.0M Alternative – Block wall, proactive detection, active deterrence, EMS protection and multiple & redundant security systems. Cost $102.2M | Tier 3 | See Note 16C | Minimal besides catastrophic environmental events that would impact physical security measures | Demetric Brown, MPO - Programs | See Note 19B | 29.4 | See Note 21A | 220 kV | See Note 23B | 901656355 | CET-ET-IR-ME-782002 | 7820 | See Note 27A | Yes | 2015-10-21 | Pre-2017 | FRM/CRT | No | N/A | N/A | N/A | See Col. 37 | 2018 = 10,300 2019 = 200 2020 = 205 2021 = 177 2022 = 53 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2017-08-25 | No | 2018-09-01 | 2018-09-17 | N/A | 13486 | 11744.9169 | See Note 53A | 10936.3292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10300.0661 | 200.3198 | 205.4528 | 177.2123 | 53.2782 | 10936.3292 | 1271.3278 | See Note 57A | N/A | No specific cost benefit analysis performed – Activity is addressing NERC CIP-014 Physical Security compliance requirements | 5.7568e-13 | None | 100% | 0% | Column 1: Prior ID SP-20 in 12/1/2020 SRP, corrected to Program Blanket Column 8: Related to PB-30.03 which is the Corporate Security component of project Column 9: To reduce security and operational risk to the Bulk Electric System (BES) and financial risk to the Company by designing, installing, and commissioning integrated physical security systems at locations which will fall under the impending NERC CIP-014 Physical Security standard (R5 - https://www.nerc.com/pa/Stand/Reliability%20Standards/CIP-014-2.pdf) , as identified by SCE and mandated by the North American Column 52: Source= PMWIF (v0 Proj Summary); Represents WO level cost estimate; total project cost including non-TD elements is $16.729M
N/A | PB-45.03 | NERC CIP Physical Security Project (FERC Order 802): CS-(ES-5061) |  |  | ES 5061 Substation: Install new and modify existing security poles foundations and conduit, install wire, AC power, grounding and security lighting for security equipment. Install concealment, modify block wall height, install wall topper and transmission tower anti-climb requirements. Install 3 camera poles. Install 4 camera pod foundations. Remove cable. Add wall concealment and wall foundation extension. Remove barbed wire along concealment area. Remove 10 existing foundations, remove & replace asphalt. | Substation; see "Project description | New | PB-30.01 | Security | NERC CIP Compliance | N/A - Largely includes installation of new equipment/technology | N/A - Largely includes installation of new equipment/technology | N/A -- To meet North American Electric Reliability Corporation (NERC) Critical Infrastructure Protection (CIP-014) Physical Security Reliability Standard Approved by the Federal Energy Regulatory Commission (FERC) Order 802 - (May 2014) SCE is required to implement NERC CIP-014 (Physical Security Protection) standards at vulnerable substations to protect them from foreseeable threats | Recommended – Block wall, proactive detection, active deterrence and EMS protection. Cost $96.9M Alternative – Security fence, proactive detection, active deterrence and EMS protection. Cost $85.0M Alternative – Block wall, proactive detection, active deterrence, EMS protection and multiple & redundant security systems. Cost $102.2M | Tier 2 | See Note 16C | No significant environmental factors | Demetric Brown, MPO - Programs | See Note 19B | 11.5 | See Note 21A | 500 kV/ 220 kV | See Note 23B | 902072001 | CET-ET-IR-ME-782009 | 7820 | See Note 27A | Yes | 2017-06-26 | Pre-2017 | FRM/CRT | No | N/A | N/A | N/A | See Col. 37 | 2018 = 5,058 2019 = 406 2020 = 177 2021 = 866 2022 = 4 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2017-09-18 | No | 2018-05-12 | 2018-06-08 | N/A | 4508 | 4508 | See Note 53A | 6511.7709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5058.1824 | 406.1114 | 176.9963 | 866.0126 | 4.4683 | 6511.7709 | 1113.5223 | See Note 57A | N/A | No specific cost benefit analysis performed – Activity is addressing NERC CIP-014 Physical Security compliance requirements | 5.4933e-12 | None | 100% | 0% | Column 1: Prior ID SP-20 in 12/1/2020 SRP, corrected to Program Blanket Column 8: Related to PB-30.01 which is the Corporate Security component of project Column 9: To reduce security and operational risk to the Bulk Electric System (BES) and financial risk to the Company by designing, installing, and commissioning integrated physical security systems at locations which will fall under the impending NERC CIP-014 Physical Security standard (R5 - https://www.nerc.com/pa/Stand/Reliability%20Standards/CIP-014-2.pdf) , as identified by SCE and mandated by the North American Column 52: Source= PMWIF (v1 Proj Summary); Represents WO level cost estimate; total project cost including non-TD elements is $11.342M
N/A | PB-45.04 | NERC CIP Physical Security Project (FERC Order 802): CS-(ES-5054) |  |  | ES-5054 Substation ¦ Control Center: • Replace and or modify substation perimeter with 10’ concrete wall. • Replace and or modify gates with auto and manual gates. • Install Power, pole foundations, conduit and conductor for security requirements. • Install transformer fire walls as required. | Substation; see "Project description | New | PB-30.04 | Security | NERC CIP Compliance | N/A - Largely includes installation of new equipment/technology | N/A - Largely includes installation of new equipment/technology | N/A -- To meet North American Electric Reliability Corporation (NERC) Critical Infrastructure Protection (CIP-014) Physical Security Reliability Standard Approved by the Federal Energy Regulatory Commission (FERC) Order 802 - (May 2014) SCE is required to implement NERC CIP-014 (Physical Security Protection) standards at vulnerable substations to protect them from foreseeable threats | Recommended – Block wall, proactive detection, active deterrence and EMS protection. Cost $96.9M Alternative – Security fence, proactive detection, active deterrence and EMS protection. Cost $85.0M Alternative – Block wall, proactive detection, active deterrence, EMS protection and multiple & redundant security systems. Cost $102.2M | Tier 3 | See Note 16C | Minimal besides catastrophic environmental events that would impact physical security measures | Demetric Brown, MPO - Programs | See Note 19B | 55 | See Note 21A | 500 kV/ 220 kV | See Note 23B | 901656358 | CET-ET-IR-ME-782005 | 7820 | See Note 27A | Yes | 2015-10-09 | Pre-2017 | FRM/CRT | No | N/A | N/A | N/A | See Col. 37 | 2020 = 24,620 2021 = 19 2022 = 1 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2018-10-04 | No | 2017-12-31 | 2020-05-22 | Permitting delays and scope change | 16271 | 16271 | See Note 53A | 24639.5874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4678.0563 | 16007.5952 | 3934.5426 | 18.5475 | 0.8457 | 24639.5874 | 3196.9371 | See Note 57A | N/A | No specific cost benefit analysis performed – Activity is addressing NERC CIP-014 Physical Security compliance requirements | 6.0282e-11 | None | 100% | 0% | Column 1: Prior ID SP-20 in 12/1/2020 SRP, corrected to Program Blanket Column 8: Related to PB-30.05 which is the Corporate Security component of project Column 9: To reduce security and operational risk to the Bulk Electric System (BES) and financial risk to the Company by designing, installing, and commissioning integrated physical security systems at locations which will fall under the impending NERC CIP-014 Physical Security standard (R5 - https://www.nerc.com/pa/Stand/Reliability%20Standards/CIP-014-2.pdf) , as identified by SCE and mandated by the North American Column 52: Source= PMWIF (v0 Proj Summary); Represents WO level cost estimate; total project cost including non-TD elements is $20.090M
N/A | PB-45.05 | NERC CIP Physical Security Project (FERC Order 802): CS-(ES-5090) |  |  | ES-5090 Substation ¦ Control Center: • Replace and or modify substation perimeter with 10’ block wall. • Replace and or modify gates with auto and manual gates. • Install Power, pole foundations, conduit and conductor for security requirements. • Install transformer fire walls as required. | Substation; see "Project description | New | PB-30.05 | Security | NERC CIP Compliance | N/A - Largely includes installation of new equipment/technology | N/A - Largely includes installation of new equipment/technology | N/A -- To meet North American Electric Reliability Corporation (NERC) Critical Infrastructure Protection (CIP-014) Physical Security Reliability Standard Approved by the Federal Energy Regulatory Commission (FERC) Order 802 - (May 2014) SCE is required to implement NERC CIP-014 (Physical Security Protection) standards at vulnerable substations to protect them from foreseeable threats | Recommended – Block wall, proactive detection, active deterrence and EMS protection. Cost $96.9M Alternative – Security fence, proactive detection, active deterrence and EMS protection. Cost $85.0M Alternative – Block wall, proactive detection, active deterrence, EMS protection and multiple & redundant security systems. Cost $102.2M | Out of State | See Note 16C | Minimal besides catastrophic environmental events that would impact physical security measures | Demetric Brown, MPO - Programs | See Note 19B | 86.7 | See Note 21A | 500 kV/ 220 kV | See Note 23B | 901657121 | CET-ET-IR-ME-782008 | 7820 | See Note 27A | Yes | 2015-11-02 | Pre-2017 | FRM/CRT | No | N/A | N/A | N/A | See Col. 37 | 2020 = 21,432 2021 = 55 2022 = 38 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2019-05-09 | No | 2017-12-31 | 2020-05-13 | Construction and material delay | 15946 | 15946 | See Note 53A | 21525.4366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 635.8436 | 14016.0459 | 6779.9735 | 55.304 | 38.2696 | 21525.4366 | 1794.6614 | See Note 57A | N/A | No specific cost benefit analysis performed – Activity is addressing NERC CIP-014 Physical Security compliance requirements | 5.1463e-11 | None | 100% | 0% | Column 1: Prior ID SP-20 in 12/1/2020 SRP, corrected to Program Blanket Column 8: Related to PB-30.05 which is the Corporate Security component of project Column 9: To reduce security and operational risk to the Bulk Electric System (BES) and financial risk to the Company by designing, installing, and commissioning integrated physical security systems at locations which will fall under the impending NERC CIP-014 Physical Security standard (R5 - https://www.nerc.com/pa/Stand/Reliability%20Standards/CIP-014-2.pdf) , as identified by SCE and mandated by the North American Column 52: Source= PMWIF (v1 Proj Summary); Represents WO level cost estimate; total project cost including non-TD elements is $13.5M
N/A | PB-46 | Substation Perimeter Security Upgrade | Not applicable at program level | Not applicable at program level | Tier Program - This project seeks to minimize physical security vulnerabilities at identified SCE substations by installing and upgrading equipment to deter, delay, respond, and monitor potential intrusions and attacks. This is a strategic, multi-site approach to secure SCE substations based on criticality and potential impact of breach (e.g., to the Bulk Electric System) by upgrading physical security technology (e.g., surveillance and analytics) and infrastructure. For example, at Serrano Sub, SCE may perform the following - Install bollards, light motion sensors, spiked wall topper, wall signage. Install new and modify 10 existing Corp security camera pod foundations. | Physical security measures include a combination of access control, alarms, perimeter protection (e.g., fencing, walls, barbed wire, etc.), video surveillance, and other measures. | New | PB-32 | Security | Substation Reliability | Not applicable at program level | Not applicable at program level | Risk of substation attack was evaluated as part of SCE’s Risk Assessment and Mitigation Phase (RAMP) filed with CPUC in November 2018. | Alternative – Augmenting protection by installing new security poles on existing foundation locations, with new cameras, new video analytics, and new IT infrastructure. Option results in perimeter equipment and coverage decrease of up to 46% due to existing pods locations. Cost: Capital: $67.4M, 5 Year O&M: $3.6M. Alternative –Use the same standards for these substations as CIP 14 sites to provide for a single security level across all identified critical BES substations. Perimeter covered at 100% with enhanced threat detection and deterrence options. Cost: Capital: $88.3M, 5 Year O&M: $4.4M. | Not applicable at program level | See Note 16C | Minimal besides catastrophic environmental events that would impact physical security measures | Demetric Brown, MPO - Programs | Not applicable at program level | Multiple locations | See Note 21A | Not applicable at program level | See Note 23B | Not applicable at program level | 8 separate CWBS | 8042 | See Note 27A | Yes | N/A | 2018 | FRM/CRT | No | N/A | N/A | N/A | Not applicable at program level | Not applicable at program level | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Not applicable at program level | See Note 46A | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 53A | Not applicable at program level | 8025.0409 | 10798.1457 | 21002.8959 | 15964.2016 | 11509.0436 | Not Available | 67299.3277 | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not applicable at program level | See Note 57A | N/A | Program and alternatives were evaluated as part of SCE’s Risk Assessment and Mitigation Phase (RAMP) filed with CPUC in November 2018. | See Note 60A | None | 100% | 0% | Column 1: Prior ID SP-31 in 12/1/2020 SRP, corrected to Program Blanket Substation Modification as defined in GO 131-D, Section III.B. Not subject to PTC requirements Column 8: PB-32 is the associated Corporate Security component of this project Column 12: Cameras are typically >10 years old Column 28 & 29: Program must ultimately receive FRM approval prior to program implementation; FRM approval is pending Column 31: Pending FRM approval
0: N/A; Project Description 1: PB-46.01; Project Description 2: CS-(ES-5080) Physical Security; Project Description 5: ES 5080 Substation - Install conduit and AC feeds for Corp Security and Telecom in the MEER and substation, install bollards, light motion sensors, spiked wall topper, wall signage. Install new and modify 10 existing Corp security camera pod foundations; Project Description 6: Substation; see "Project description; Project Description 7: New; Project Description (Cont.) 24: 902158683; Project Description (Cont.) 25: CET-ET-IR-ME-804207; Project Description (Cont.) 26: 8042; Project Status 45: Operational; Project Status 50: 2021-04-19; Costs 52: 2076; Costs 52.1: 2076; Costs 54: 0 | [16 empty] | Column 1: Prior ID SP-31 in 12/1/2020 SRP, corrected to Program Blanket Substation Modification as defined in GO 131-D, Section III.B. Not subject to PTC requirements. Column 52: Source= FRM (11/11/2019); Represents WO level costs (i.e., T&D portion of costs), Total Original Project cost is $6.147M for Corporate Security, T&D, IT elements and contingency; This WO is replaced by WO#903158304 (See PB-46.09)
N/A | PB-46.02 | CS-(ES-5067) Physical Security |  |  | ES 5067 Substation: Install conduit, pull boxes/handholes, foundations and wiring to support Corporate Security requirements for camera pods, lights and security devices. Install motion activated switchrack lighting per current standard. Install/modify as required station service, grounding, rock surfacing. Remove/modify existing wire fence, tamper proof gates and install slope grading improvements adjacent to camera pod locations as required in order to support Corporate Security requirements | Substation; see "Project description | New | PB-32 | Security | Substation Reliability | 12/15/2021 | New Assets | Risk of substation attack was evaluated as part of SCE’s Risk Assessment and Mitigation Phase (RAMP) filed with CPUC in May 2022. | Alternative – Augmenting protection by installing new security poles on existing foundation locations, with new cameras, new video analytics, and new IT infrastructure. Option results in perimeter equipment and coverage decrease of up to 46% due to existing pods locations. Cost: Capital: $67.4M, 5 Year O&M: $3.6M. Alternative –Use the same standards for these substations as CIP 14 sites to provide for a single security level across all identified critical BES substations. Perimeter covered at 100% with enhanced threat detection and deterrence options. Cost: Capital: $88.3M, 5 Year O&M: $4.4M. | Non HFRA | See Note 16C | High Wind Events, Extreme Temperature Conditions | Demetric Brown, MPO - Programs | See Note 19B | 98 | 500kV | 500kV, 220kV, 115kV | See Note 23B | 902210275 | CET-ET-IR-ME-804200 | 8042 | See Note 27A | Yes | 2021-06-01 | 2018 | FRM/CRT | N/A | N/A | N/A | N/A | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Construction more than 50% completed | See Note 46A | 2022-01-03 | Yes | 2018-12-31 | 2023-09-26 | Scope Increase and FRM Approval | 9964 | 8170.48 | See Note 53A | 5217.0011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.8758 | 189.9352 | 17.0799 | 575.1284 | 4342.9818 | 5217.0011 | 642.333 | See Note 57A | N/A | See Note 59A | 4556.6864 | None | 100% | 0% | Column 1: Prior ID SP-31 in 12/1/2020 SRP, corrected to Program Blanket Column 38: Work expected to be exempt from GO 131-D licensing Column 52: Source= FRM (06/23/2021); Represents WO level costs (i.e., T&D portion of costs), Total Original Project cost is $14.732M for Corporate Security, T&D, IT elements
0: N/A; Project Description 1: PB-46.03; Project Description 2: CS-(ES-5052) Physical Security; Project Description 5: ES 5052 Substation: Install conduit, pull boxes/handholes, foundations and wiring to support Corporate Security requirements for camera pods, lights and security devices. Install motion activated switchrack lighting per current standard. Install wall topper on existing wall. Modify and tamper proof gate operators and hardware. Modify gates with heavy duty anticlimb, anti-cut screen material as required. Install/modify as required station service, grounding and rock surfacing in order to support Corporate Security requirements; Project Description 6: Substation; see "Project description; Project Description 7: New; Project Description (Cont.) 24: 902210276; Project Description (Cont.) 25: CET-ET-IR-ME-804201; Project Description (Cont.) 26: 8042; Project Status 45: Canceled; Project Status 50: Canceled; Costs 52: 4959; Costs 52.1: 4959; Costs 54: 2.1316e-14 | [16 empty] | Column 1: Prior ID SP-31 in 12/1/2020 SRP, corrected to Program Blanket Column 38: Work expected to be exempt from GO 131-D licensing Column 52: Source= PMWIF (v4 Proj Summary); Represents WO level cost estimate; total project cost including non-TD elements is $6.792M; Project will be approved by FRM and costs will be updated if/ when approved
N/A | PB-46.04 | CS-(ES-5047) Physical Security |  |  | ES 5047 Substation: Install conduit, pull boxes/handholes, foundations and wiring to support Corporate Security requirements for camera pods, lights and security devices. Install motion activated switchrack lighting per current standard. Install wall topper on existing wall. Modify and tamper proof gate operators and hardware. Modify gates with heavy duty anticlimb, anti-cut screen material as required. Install/modify as required station service, grounding and rock surfacing in order to support Corporate Security requirements | Substation; see "Project description | New | PB-32 | Security | Substation Reliability | 07/05/2022 | New Assets | Risk of substation attack was evaluated as part of SCE’s Risk Assessment and Mitigation Phase (RAMP) filed with CPUC in May 2022. | Alternative – Augmenting protection by installing new security poles on existing foundation locations, with new cameras, new video analytics, and new IT infrastructure. Option results in perimeter equipment and coverage decrease of up to 46% due to existing pods locations. Cost: Capital: $67.4M, 5 Year O&M: $3.6M. Alternative –Use the same standards for these substations as CIP 14 sites to provide for a single security level across all identified critical BES substations. Perimeter covered at 100% with enhanced threat detection and deterrence options. Cost: Capital: $88.3M, 5 Year O&M: $4.4M. | Non HFRA | See Note 16C | No Significant Environmental Factors | Demetric Brown, MPO - Programs | See Note 19B | 44.5 | See Note 21A | 500kV, 220kV | See Note 23B | 902210277 | CET-ET-IR-ME-804202 | 8042 | See Note 27A | Yes | 2022-05-01 | 2021 | FRM/CRT | N/A | N/A | N/A | N/A | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Construction more than 50% completed | See Note 46A | 2022-07-25 | Yes | 2019-06-01 | 2023-09-26 | Scope Increase and FRM Approval | 4216 | 4216 | See Note 53A | 5018.473 | 1802.414 | 129.8 | 0 | 0 | 0 | 0 | 1932.214 | 13.0747 | 0.34586 | 0 | 391.7421 | 2681.0963 | 3086.2589 | 358.1278 | See Note 57A | N/A | See Note 59A | 3073.4706 | None | 100% | 0% | Column 1: Prior ID SP-31 in 12/1/2020 SRP, corrected to Program Blanket Column 38: Work expected to be exempt from GO 131-D licensing Column 45: FRM Approved 5/2022 and Complete Engineering. Currently planning construction. Column 52: Source = PMWIF (Project Summary V.1); Includes 25% Contingency
0: N/A; Project Description 1: PB-46.05; Project Description 2: CS-(ES-8060) Physical Security; Project Description 5: ES 8060 Substation: Install conduit, pull boxes/handholes, foundations and wiring to support Corporate Security requirements for camera pods, lights and security devices. Install motion activated switchrack lighting per current standard. Install wall topper on existing wall. Modify and tamper proof gate operators and hardware. Modify gates with heavy duty anticlimb, anti-cut screen material as required. Install/modify as required station service, grounding and rock surfacing in order to support Corporate Security requirements; Project Description 6: Substation; see "Project description; Project Description 7: New; Project Description (Cont.) 24: 902210452; Project Description (Cont.) 25: CET-ET-IR-ME-804203; Project Description (Cont.) 26: 8042; Project Status 45: Construction less than 50% completed; Project Status 50: 2024-04-30; Costs 52: 5249; Costs 52.1: 5249; Costs 54: 4753.8119 | [16 empty] | Column 1: Prior ID SP-31 in 12/1/2020 SRP, corrected to Program Blanket Column 38: Work expected to be exempt from GO 131-D licensing Column 45: FRM Approved 5/2022 and Complete Engineering. Currently planning construction. Column 52: Include 25% Contingency
0: N/A; Project Description 1: PB-46.06; Project Description 2: CS-(ES-ES-5079) Physical Security; Project Description 5: ES-5079 Substation: Install conduit, pull boxes/handholes, foundations and wiring to support Corporate Security requirements for camera pods, lights and security devices. Install motion activated switchrack lighting per current standard. Install wall topper on existing wall. Modify and tamper proof gate operators and hardware. Modify gates with heavy duty anticlimb, anti-cut screen material as required. Install/modify station service, grounding and rock surfacing as required in order to support Corporate Security requirements; Project Description 6: Substation; see "Project description; Project Description 7: New; Project Description (Cont.) 24: 902210453; Project Description (Cont.) 25: CET-ET-IR-ME-804204; Project Description (Cont.) 26: 8042; Project Status 45: Pre-construction; Project Status 50: 2024-06-28; Costs 52: 4935; Costs 52.1: 4387.4757; Costs 54: 4184.6426 | [16 empty] | Column 1: Prior ID SP-31 in 12/1/2020 SRP, corrected to Program Blanket Column 38: Work expected to be exempt from GO 131-D licensing Column 45: FRM Approved 5/2022 and Complete Engineering. Currently planning construction. Column 52: Include 25% Contingency
0: N/A; Project Description 1: PB-46.07; Project Description 2: CS-(ES-ES-5064) Physical Security; Project Description 5: ES-5064 Substation: Install block wall or Beta type fence and wall topper around station perimeter. Install conduit, pull boxes/handholes, foundations and wiring to support Corporate Security requirements for camera pods, lights and security devices. Install motion activated switchrack lighting per current standard. Modify/replace and tamper proof gate operators and hardware as required. Modify/replace gates with heavy duty anticlimb, anti-cut screen material as required. Install/modify station service, grounding, drive ways, remove/modify existing fence, rock surfacing, drainage improvements and removals as required in order to support Corporate Security requirements; Project Description 6: Substation; see "Project description; Project Description 7: New; Project Description (Cont.) 24: 902210454; Project Description (Cont.) 25: CET-ET-IR-ME-804205; Project Description (Cont.) 26: 8042; Project Status 45: Canceled; Project Status 50: Canceled; Costs 52: 10639; Costs 52.1: 2287.6509; Costs 54: 20.6189 | [16 empty] | Column 1: Prior ID SP-31 in 12/1/2020 SRP, corrected to Program Blanket Column 38: Work expected to be exempt from GO 131-D licensing Column 52: Source= PMWIF (v1 Proj Summary); Represents WO level cost estimate; total project cost including non-TD elements is $12.572M
0: N/A; Project Description 1: PB-46.08; Project Description 2: CS-(ES-ES-5056) Physical Security; Project Description 5: ES-5056 Substation: Install block wall or Beta type fence and wall topper around station perimeter. Install conduit, pull boxes/handholes, foundations and wiring to support Corporate Security requirements for camera pods, lights and security devices. Install motion activated switchrack lighting per current standard. Modify/replace and tamper proof gate operators and hardware as required. Modify/replace gates with heavy duty anticlimb, anti-cut screen material as required. Install/modify station service, grounding, drive ways, remove/modify existing fence, and rock surfacing as required in order to support Corporate Security requirements.; Project Description 6: Substation; see "Project description; Project Description 7: New; Project Description (Cont.) 24: 902210455; Project Description (Cont.) 25: CET-ET-IR-ME-804206; Project Description (Cont.) 26: 8042; Project Status 45: Planning; Project Status 50: 2025-09-26; Costs 52: 9590; Costs 52.1: 1318.4223; Costs 54: 0.32229 | [16 empty] | Column 1: Prior ID SP-31 in 12/1/2020 SRP, corrected to Program Blanket Column 38: Work expected to be exempt from GO 131-D licensing Column 45: On hold pending FRM approval Column 52: Source= PMWIF (v2 Proj Summary); Represents WO level cost estimate; total project cost including non-TD elements is $11.666M
N/A | PB-46.09 | CS-(ES-ES-5080) Physical Security |  |  | ES-5080 - Install conduit and AC feeds for Corp Security and Telecom in the MEER and substation, install bollards, light motion sensors, spiked wall topper, wall signage. Install new and modify 10 existing Corp security camera pod foundations | Substation; see "Project description | New | PB-32.01, PB-46.01 | Security | Substation Reliability | 2020-07-20 | New | Risk of Substation Attack was evaluated as part of SCE’s Risk Assessment and Mitigation Phase (RAMP) filed with CPUC in November 2018. | Recommended – Installing new security poles on new foundation locations. This option provides for new cameras, new video analytics, and new pole infrastructure to meet detection requirements. Perimeter covered at 100% with this option. Cost: Capital: $82.0M, 5 Year O&M: $4.1M. Alternative – Augmenting protection by installing new security poles on existing foundation locations, with new cameras, new video analytics, and new IT infrastructure. Option results in perimeter equipment and coverage decrease of up to 46% due to existing pods locations. Cost: Capital: $67.4M, 5 Year O&M: $3.6M. Alternative –Use the same standards for these substations as CIP 14 sites to provide for a single security level across all identified critical BES substations. Perimeter covered at 100% with enhanced threat detection and deterrence options. Cost: Capital: $88.3M, 5 Year O&M: $4.4M. | Tier 2 | See Note 16C | Minimal besides catastrophic environmental events that would impact physical security measures | Demetric Brown, MPO - Programs | See Note 19B | 19.2 | See Note 21A | 500/220 (kV) | See Note 23B | 903158304 | CET-ET-IR-ME-804207 | 8042 | See Note 27A | Yes | 2020 | 2019 | FRM/CRT | No | N/A | N/A | N/A | See Col. 37 | 2021 = 3,964 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2020-08-17 | No | 2020-11-25 | 2021-04-21 | N/A | 2076 | 2076 | See Note 53A | 3963.9281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3173.2319 | 790.6434 | 0.05279 | 3963.9281 | 455.4152 | See Note 57A | N/A | Program and alternatives were evaluated as part of SCE’s Risk Assessment and Mitigation Phase (RAMP) filed with CPUC in November 2018. | -2.794e-12 | None | 100% | 0% | Column 1: This WO replaces WO#902158683 (See PB-46.01). Column 8: Related to PB-32.01 which is the Corporate Security component of this project; This WO replaces PB-46.01 Column 9: Safety: The Substation Security Perimeter Enhancement Program (SSPE) seeks to minimize physical security vulnerabilities at identified SCE substations by installing and upgrading equipment to deter, delay, respond, and monitor potential intrusions and attacks. • SSPE is a strategic, multi-site approach to secure SCE substations based on criticality and potential impact of breach (e.g., to the Bulk Electric System) by upgrading physical security technology (e.g., surveillance and analytics) and infrastructure based on SCE’s Grid Infrastructure Protection Standards. • Program originated with NERC CIP-014 Physical Security Protection Project that focused only on identified substations to meet NERC/FERC compliance requirements and now seeks to address remaining sites through a minimum level of security upgrades based on risk. • Physical security measures include a combination of access control, alarms, perimeter protection (e.g., fencing, walls, barbed wire, etc.), video surveillance, and other measures. Column 52: Source= FRM (11/11/2019); Represents WO level costs (i.e., T&D portion of costs), Total Original Project cost is $6.147M for Corporate Security, T&D, IT elements and contingency; WO#903158304 was not PMWIF’d as it was a work order that was opened to correct the settlement of charges related to WO#902158683.
0: N/A; Project Description 1: PB-46.10; Project Description 2: (ES-5070): Physical Security Tier 2; Project Description 5: ES-5070 - Install conduit and AC feeds for Corp Security and Telecom in the MEER and substation, install bollards, light motion sensors, spiked wall topper, wall signage. Input foundation for block wall implementation and drainage system; Project Description 6: Substation; see "Project description; Project Description 7: New; Project Description (Cont.) 24: 903511341; Project Description (Cont.) 25: CET-ET-IR-ME-804202; Project Description (Cont.) 26: 8042; Project Status 45: Engineering more than 50% completed; Project Status 50: 2024-06-25; Costs 52: 14885.074; Costs 52.1: 3243; Costs 54: 5412.366 | [16 empty] | Column 52: Source = PMWIF (V.3 Project Summary)
0: N/A; Project Description 1: PB-46.11; Project Description 2: (ES-8367): Physical Security Tier 2; Project Description 5: ES-8367 Substation: Install block wall or Beta type fence and wall topper around station perimeter. Install conduit, pull boxes/handholes, foundations and wiring to support Corporate Security requirements for camera pods, lights and security devices. Install motion activated switchrack lighting per current standard. Modify/replace and tamper proof gate operators and hardware as required. Modify/replace gates with heavy duty anticlimb, anti-cut screen material as required. Install/modify station service, grounding, drive ways, remove/modify existing fence, rock surfacing, drainage improvements and removals as required in order to support Corporate Security requirements.; Project Description 6: Substation; see "Project description; Project Description 7: New; Project Description (Cont.) 24: 903897669; Project Description (Cont.) 25: CET-ET-IR-ME-804200; Project Description (Cont.) 26: 8042; Project Status 45: Engineering more than 50% completed; Project Status 50: 2025-03-14; Costs 52: 4903; Costs 52.1: 4903; Costs 54: 3379.2463 | [16 empty] | Column 52: Source = PMWIF (Project Summary V.3)
0: N/A; Project Description 1: PB-46.12; Project Description 2: (ES-5071) Perimeter Refresh; Project Description 5: Civil construction in support of network and power infrastructure for poles, gates, security technology, foundation, and more.; Project Description 6: Substation; see "Project description; Project Description 7: New; Project Description (Cont.) 24: 903864281; Project Description (Cont.) 25: CET-ET-IR-ME-804206; Project Description (Cont.) 26: 8042; Project Status 45: Engineering more than 50% completed; Project Status 50: 2024-05-10; Costs 52: 4675; Costs 52.1: 1093.4825; Costs 54: 351.314 | [16 empty] | Column 52: Source = PMWIF (Project Summary V.0)
0: N/A; Project Description 1: PB-46.13; Project Description 2: (ES-8076): Physical Security; Project Description 5: ES-8076 Substation: Install block wall or Beta type fence and wall topper around station perimeter. Install conduit, pull boxes/handholes, foundations and wiring to support Corporate Security requirements for camera pods, lights and security devices. Install motion activated switchrack lighting per current standard. Modify/replace and tamper proof gate operators and hardware as required. Modify/replace gates with heavy duty anticlimb, anti-cut screen material as required. Install/modify station service, grounding, drive ways, remove/modify existing fence, rock surfacing, drainage improvements and removals as required in order to support Corporate Security requirements.; Project Description 6: Substation; see "Project description; Project Description 7: New; Project Description (Cont.) 24: 903853720; Project Description (Cont.) 25: CET-ET-IR-ME-804200; Project Description (Cont.) 26: 8042; Project Status 45: Engineering >50% Complete; Project Status 50: 2026-02-02; Costs 52: 361; Costs 52.1: 144.2556; Costs 54: 2839.6309 | [16 empty] | 49 and 52 Origination = Verified PMWIF (Project Summary V.1) PMWIF Approval Date = 09/19/2022 Latest Approved Project Summary Version = V.1
0: N/A; Project Description 1: PB-46.14; Project Description 2: (ES-5031): Physical Security; Project Description 5: ES-5031 Substation: Install block wall or Beta type fence and wall topper around station perimeter. Install conduit, pull boxes/handholes, foundations and wiring to support Corporate Security requirements for camera pods, lights and security devices. Install motion activated switchrack lighting per current standard. Modify/replace and tamper proof gate operators and hardware as required. Modify/replace gates with heavy duty anticlimb, anti-cut screen material as required. Install/modify station service, grounding, drive ways, remove/modify existing fence, rock surfacing, drainage improvements and removals as required in order to support Corporate Security requirements.; Project Description 6: Substation; see "Project description; Project Description 7: New; Project Description (Cont.) 24: 903897059; Project Description (Cont.) 25: CET-ET-IR-ME-804200; Project Description (Cont.) 26: 8042; Project Status 45: Planning; Project Status 50: 2024-10-18; Costs 52: 2711; Costs 52.1: 2548.0689; Costs 54: 7599.6921 | [16 empty] | 49 and 52 Origination = Verified PMWIF (Project Summary V.3) PMWIF Approval Date = 10/26/2022 Latest Approved Project Summary Version = V.3
0: N/A; Project Description 1: PB-46.15; Project Description 2: (ES-8369): Physical Security; Project Description 5: ES-8369 Substation: Install block wall or Beta type fence and wall topper around station perimeter. Install conduit, pull boxes/handholes, foundations and wiring to support Corporate Security requirements for camera pods, lights and security devices. Install motion activated switchrack lighting per current standard. Modify/replace and tamper proof gate operators and hardware as required. Modify/replace gates with heavy duty anticlimb, anti-cut screen material as required. Install/modify station service, grounding, drive ways, remove/modify existing fence, rock surfacing, drainage improvements and removals as required in order to support Corporate Security requirements.; Project Description 6: Substation; see "Project description; Project Description 7: New; Project Description (Cont.) 24: 903897060; Project Description (Cont.) 25: CET-ET-IR-ME-804200; Project Description (Cont.) 26: 8042; Project Status 45: Planning; Project Status 50: 2025-04-07; Costs 52: 507; Costs 52.1: 507; Costs 54: 3304.5916 | [16 empty] | 49 and 52 Origination = Verified PMWIF (Project Summary V.1) PMWIF Approval Date = 10/26/2022 Latest Approved Project Summary Version = V.1
0: N/A; Project Description 1: PB-46.16; Project Description 2: (ES-5042): Physical Security; Project Description 5: ES-5042 Substation: Install block wall or Beta type fence and wall topper around station perimeter. Install conduit, pull boxes/handholes, foundations and wiring to support Corporate Security requirements for camera pods, lights and security devices. Install motion activated switchrack lighting per current standard. Modify/replace and tamper proof gate operators and hardware as required. Modify/replace gates with heavy duty anticlimb, anti-cut screen material as required. Install/modify station service, grounding, drive ways, remove/modify existing fence, rock surfacing, drainage improvements and removals as required in order to support Corporate Security requirements.; Project Description 6: Substation; see "Project description; Project Description 7: New; Project Description (Cont.) 24: 903994629; Project Description (Cont.) 25: CET-ET-IR-ME-804200; Project Description (Cont.) 26: 8042; Project Status 45: Planning; Project Status 50: 2026-02-09; Costs 52: 598; Costs 52.1: 499.33; Costs 54: 9042.3895 | [16 empty] | 49 and 52 Origination = Verified PMWIF (Project Summary V.1) PMWIF Approval Date = 02/02/2023 Latest Approved Project Summary Version = V.1
N/A | PB-47 | Catastrophic Events Memorandum Account (CEMA) | Not applicable at program level | Not applicable at program level | The purpose of the CEMA is to record all costs incurred by SCE associated with a catastrophic event for: 1. restoring utility service to SCE's customers 2. repairing, replacing, or restoring damaged facilities 3. complying with governmental agency orders The CEMA is restricted to events declared as disasters by competent state or federal authorities (e.g., fire, storm, COVID-19, etc.) | Various work depending on type of catastrophe: Includes necessary items for repairing, replacing, or restoring damaged utility facilities | Various actions dependent on catastrophe (new, replacement, upgrade, etc.) | Not applicable at program level | Emergency Replacement | Emergency Response - Fire Related | Not applicable at program level | Not applicable at program level | Inspections are performed to assess damages and determine necessary repairs/replacements | Not applicable at program level | Not applicable at program level | See Note 16D | Not applicable at program level | Demetric Brown, MPO - Programs | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 23B | Not applicable at program level | CET-OT-CM-ST-CEMAST | 4057 | See Note 27A | Yes | 1991 | 2021 | Other- See Notes | No | N/A | N/A | N/A | Not applicable at program level | Not applicable at program level | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Not applicable at program level | See Note 46A | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | N/A | Not applicable at program level | Not applicable at program level | See Note 53A | Not applicable at program level | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 0 | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not applicable at program level | Not applicable at program level | See Note 57A | N/A | See Note 59A | See Note 60A | None | 100% | 0% | Column 10: Not limited to fire emergency response for fire, although current supporting WOs in SRP are fire-related. CEMA can be applied for various catastrophic events Column 31: Resolution No. E-3238 (Resolution), issued on July 24, 1991, and Public Utilities Code Section 454.9, which codified the CEMA process, set forth the criteria for utilities to use the CEMA, providing, among other things that its “use will be restricted to events declared disasters by competent state or federal authorities.” Column 31: External Affairs Committee (EAC) - CEMA Application 19-07-021 is pending before the CPUC-The CPUC issued decisions on Application 19-07-021 on August 24, 2021 and November 4, 2022.
N/A | PB-47.01 | Big Creek 230 kV System CEMA Creek Fire Restoration | 37.3096, -119.3134 | Shaver Lake/ Big Creek, Fresno County | Emergency work to replace damaged equipment resulting from Creek Fire: Replace wires and towers, patrol area | Tower and line replacement | Replacement | PB-47.02 | Emergency Replacement | Emergency Response - Fire Related | N/A | N/A | Crew patrolled lines to identify structures, helicopter, ground crews | N/A- Emergency work ensuring customer and employee safety | Tier 2 | See Note 16D | Mountainous Conditions; Fire | Demetric Brown, MPO - Programs | Not readily available | See Note 20B | 230 kV | See Note 22A | See Note 23B | 903186172 | CET-OT-CM-ST-CEMAST | 4057 | See Note 27A | Yes | 2020 | 2021 | Other- See Notes | No | N/A | N/A | N/A | See Col. 37 | 2021 = 15,974 2022 = 13 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2020-09-04 | No | N/A | 2021-04-28 | N/A | Not readily available | Not readily available | See Note 53A | 15987.6615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14892.585 | 1081.6191 | 13.4574 | 15987.6615 | 1263.9334 | See Note 57A | N/A | See Note 59A | 6.5193e-12 | None | 100% | 0% | Column 3: Center of burn scar Column 11: Replacement was due to fire, not based on inspection; therefore this is listed as N/A Column 19: Project spans a large territory; total length in miles is not readily available in system Column 28-31: Storm work orders are initiated by the Location/ Duty Manager, no other approval is needed to conduct this emergency work Column 49: Since this is emergency work that does not follow the traditional PMWIF/ FRM process, there is not an original estimated in-service date Column 52: Since this is emergency work that does not follow the traditional PMWIF/ FRM process, there is not an original cost estimate available
N/A | PB-47.02 | Erosion Control and Debris Flow Mitigation for Creek and Bobcat Fires | 37.3096, -119.3134/ 34.3145, -117.8933 | Shaver Lake/ Big Creek, Fresno County & Angeles National Forest, Los Angeles County | Emergency work to mitigate erosion and potential mudflow damage from Creek Fire and Bobcat Fire. At both locations, implementation of temporary erosion control best management practices (BMPs) (e.g., gravel bags, K-rail, silt fences, hydromulch, etc.). Creek Fire only, install debris flow barriers to mitigate against potential mudflow. Mitigation measures are aimed at protecting transmission and substations infrastructure. | Erosion Control and Debris Flow Measures | New | PB-47.01 | Infrastructure Enhancement | Emergency Response - Fire Related | 2021-05-20 | N/A- New | Desktop analysis referencing USGS Emergency Assessment of Post-fire Debris Flow Hazards Maps and Engineering Field Assessments for recommended temporary bmps for erosion control and debris flow mitigation to protect SCE facilities (includes limited Geotechnical field investigation and Debris Flow Specialist Field Evaluation to support Debris Flow Barrier Design Plans) | N/A- Emergency work | Tier 2/ Tier 3 | See Note 16D | Mountainous Conditions; Fire | Demetric Brown, MPO - Programs | See Note 19B | See Note 20B | 220 kV (Creek)/ 220 kV and 500 kV (Bobcat) | See Note 22A | See Note 23B | 903237253 | CET-OT-CM-ST-CEMAST | 4057 | See Note 27A | Yes | 2021 | 2021 | FRM/CRT | No | N/A | N/A | N/A | See Col.37 | 2022 = 8,105 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2021-11-08 | Yes | 2023-12-01 | 2022-12-27 | N/A | 10600 | 10600 | See Note 53A | 8105.0282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3937.777 | 2025.2736 | 2141.9776 | 8105.0282 | 1105.5851 | See Note 57A | N/A | See Note 59A | 1.8626e-12 | None | 100% | 0% | Column 3: Center of burn scar Column 11: Inspection date refers to temporary BMPs; Transmission voltage level provided references voltage of lines being protected by measures Column 47: Debris flow mitigation is not started, but implementation of the erosion control BMPs are nearly completed Column 52: Source- FRM (02/17/2021)
N/A | PB-48 | Corporate Real Estate (CRE) Building Renovation: Various Major Structure | Not applicable at program level | Not applicable at program level | This program addresses unplanned capital to protect the productivity, health and safety of SCE’s employees, our customers, and the general public; to deliver on SCE’s business objectives and values; and to meet the changing regulatory and business landscape. | Various Major Structures | Replacement | Not applicable at program level | Other - See Notes | Age/Condition | Not applicable at program level | Not applicable at program level | Review is performed based on age, condition, and lifecycle of the asset | Not applicable at program level | Not applicable at program level | See Note 16C | Not applicable at program level | Demetric Brown, MPO - Programs | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 23B | Not applicable at program level | COS-00-RE-BR-VM0001 | 3221 | See Note 27A | Not applicable at program level | Not applicable at program level | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | Not applicable at program level | Not applicable at program level | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Not applicable at program level | See Note 46A | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 53A | Not applicable at program level | 0 | 0 | 0 | 0 | 0 | Not Available | 0 | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not applicable at program level | Not applicable at program level | See Note 57A | N/A | See Note 59A | See Note 60A | None | 100% | 0% | Column 9: Asset condition, regulatory changes, environmental changes (e.g., draught), of significant facility failures
N/A | PB-48.01 | T&D Training Commercial Drive School and Crane Certification Center Training Relocation | 34.0871, -117.5316 | Rancho Cucamonga, San Bernardino County | This project will build a commercial vehicle driving school and crane certification site for training employees at the Rancho Vista site and retire the training at Mira Loma substation where the site is too small and has overhead hazards on site. | Facility New Construction | Replace | None | Other - See Notes | Other- See Notes | N/A - New | Not readily available | Observation | 1) Do nothing and risk fines and safety matters; 2) New Construction (<$1M) | Non-HFRA | See Note 16C | No specific factors outside of very extreme weather and environmental events that could compromise the integrity of the system. | Demetric Brown, MPO - Programs | See Note 19B | Site: 3 acres | See Note 21A | 500/220 (kV) | See Note 23B | 801665131 | COS-00-RE-BR-VM0001 | 3221 | See Note 27A | Yes | 2017 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2019 = 1,807 2020 = 15 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2017-10-01 | No | 2018-03-31 | 2019-05-29 | IT and Security implemented new standards which in turn caused delays related to Change Control Board approval of additional costs and procurement of new equipment extended the schedule to its recorded completion. | 845 | 845 | See Note 53A | 1821.3871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1043.1644 | 763.6312 | 14.5914 | 0 | 0 | 1821.3871 | 146.1774 | See Note 57A | N/A | See Note 59A | -6.2514e-13 | None | 100% | 0% | Column 9, 10: Safety and Regulation changes
N/A | PB-49 | Tower Lights and Marker Balls (FAA Standards) | Not applicable at program level | Not applicable at program level | Install new marker balls and lighting based on aerial risk analysis performed at SCE with Engineering, Air Operations, and Transmission. | Install new marker balls and lighting | New | Not applicable at program level | Infrastructure Enhancement | Other- See Notes | Not applicable at program level | Not applicable at program level | Aerial risk ranking performed by Engineering, Air Operations, and Transmission on all circuits and towers over 200'. | Not applicable at program level | Not applicable at program level | See Note 16C | Not applicable at program level | Demetric Brown, MPO - Programs | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 23B | Not applicable at program level | CET-PD-OT-LM-751101 | 7511 | See Note 27A | Not applicable at program level | Not applicable at program level | Pre-2017 | See Note 31A | No | N/A | N/A | N/A | Not applicable at program level | Not applicable at program level | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Not applicable at program level | See Note 46A | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 53A | Not applicable at program level | 0 | 0 | 0 | 0 | 0 | Not Available | 0 | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not applicable at program level | Not applicable at program level | See Note 57A | N/A | See Note 59A | See Note 60A | None | 100% | 0% | Column 10: FAA Regulation/ Recommendations
N/A | PB-49.01 | TRTP 1: Antelope-Pardee 500kV: Install Marker Balls and Lighting per FAA requirements for TRTP Segment 1. | 34.686, -118.575 / 34.422, -118.575 | Lancaster & Santa Clarita, Los Angeles County | TRTP 1: FIP Antelope-Pardee 500kV: Install Marker Balls and Lighting per FAA requirements for TRTP Segment 1 | Install new marker balls and lighting | New | None | Infrastructure Enhancement | Other- See Notes | N/A - New | Not applicable - New installs | Submitted FAA filing | N/A | Tier 2/Tier 3 | See Note 16C | Extreme Temperature Conditions, High Fire Area, High Wind Events | Demetric Brown, MPO - Programs | 17.44 | NA | 500 kV | See Note 22A | See Note 23B | 900719387 | CET-PD-OT-LM-751101 | 7511 | See Note 27A | Yes | N/A | Pre-2017 | See Note 31A | No | N/A | N/A | N/A | See Col. 37 | 2019 = 3,841 2020 = 774 2021 = 1,440 2022 = 5 | Final Certified | EIR/EIS | CPUC/ US Forest Service | CPCN A.04-12-007 | 2004 | Approved | 2007 | Operational | See Note 46A | 2018-02-22 | No | 2012-12-28 | 2019-12-31 | Permits from Angeles National Forest delayed project. | 4687.619 | 4687.619 | See Note 53A | 6060.7153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3805.9496 | 34.872 | 774.3184 | 1440.3492 | 5.226 | 6060.7153 | 1669.1799 | See Note 57A | N/A | See Note 59A | -1.4706e-12 | None | 100% | 0% | Column 10: FAA Regulation/ Recommendations Column 53: The maximum and reasonable prudent cost established in the Certificate of Public Convenience and Necessity pursuant to California Public Utilities Code Section 1005.5 (a) for this project, includes, but is not limited to: (1) $746 million (2008$) as noted in D.09-09-033 dated September 24, 2009 and issued on September 28, 2009, which amended D.07-03-012 and D.07-03-045 (For Segments 1-3); and (2) $1,522.92 million, excluding AFUDC which is estimated at $261.82 million for a total estimated project cost of $1,784.74 Million (2009$) as noted in CPUC Decision 09-12-044 dated December 17, 2009, and issued on December 24, 2009 (Segments 4-11); (3) the addition of $32.95 million (2013$), including Contracting Termination Charges, as noted in CPUC Decision D13-02-035 dated July 28, 2013 and issued on March 6, 2013 (for studies related to the feasibility of undergrounding Segment 8A); (4) the addition of $224 million (2013$) as noted in the CPUC Decision D13-07-018 dated July 11, 2013 and issued on July 16, 2013 (undergrounding of Segment 8A); and (5) the addition of $23 million (2013$) as noted in CPUC Decision D14-01-005 dated January 16, 2014 and issued on January 14, 2014 (the inclusion of voltage control equipment for UG5), as well as any adjustments to these amounts made in any of the Petitions for Modification filed in A.07-06-031 and any related dockets associated with the project. Further, as referenced above, these amounts are in different year nominal dollars and would need to be placed in current year dollars to determine the actual cost for the project
N/A | PB-50 | Transmission Small Civil Projects | Not applicable at program level | Not applicable at program level | Small Civil Capital Program (SCCP) is the deployment of non-electrical Capital assets that support Transmission facilities. The program comprises of projects that are either new construction or improvement of existing field conditions. Types of activities under the SCCP are: - Installation/Improvement of new and existing Access Roads - Installation/Improvement of Wet Crossings (Bridges) and Drainage - Implementation/Improvement of Laydown/Material Yards - Implementation/Replacement of Retaining Walls | Non-electrical Transmission capital assets | New and Upgrades | Not applicable at program level | Emergency Replacement, Infrastructure Enhancement, Operations Support, Security | Age/Condition | Not applicable at program level | Not applicable at program level | Visual Inspections | Not applicable at program level | Not applicable at program level | See Note 16C | Not applicable at program level | Demetric Brown, MPO - Programs | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 23B | Not applicable at program level | CET-PD-IR-TC-TRSJAC | 3364 | See Note 27A | Not applicable at program level | Not applicable at program level | 2021 | Annual capital operating plan process | No | N/A | N/A | N/A | Not applicable at program level | Not applicable at program level | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Not applicable at program level | See Note 46A | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 53A | Not applicable at program level | 5981.2062 | 7477.2038 | 1743.7769 | 1755.488 | 1776.5517 | Not Available | 18734.2266 | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not applicable at program level | Not applicable at program level | See Note 57A | N/A | See Note 59A | See Note 60A | None | 100% | 0% | Column 9: SCE Material Yards support various projects and operations for Transmission and Distribution
N/A | PB-50.01 | San Onofre-Viejo Access Road Restoration | 33.371, -117.557 / 33.667, -117.642 | Marine Corp Base Camp Pendleton, San Diego County | Access Road Restoration and Slope Repair | Restore access roads, slope repair, and environmental assessment; Potential for a 50 year permanent long term permit to conduct road maintenance and vegetation management work | Repair | None | Other - See Notes | Age/Condition | Circuit inspection: 9/16/2020 | N/A for road | N/A | N/A | Tier 2 | See Note 16C | No significant environmental factors | Blake Chalson, Elect Trans Ops | See Note 19A | See Note 20B | 220 kV | See Note 22A | See Note 23B | TD687331 | CET-PD-IR-TC-TRORAN | 3364 | See Note 27A | Yes | Pre-2014 | Pre-2017 | Annual capital operating plan process, See Note 31A | No | N/A | N/A | N/A | Not Yet Operational | Not Yet Operational | N/A | EA | DOD | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Pre-construction | See Note 46A | 2024-02-08 | No | 2021-03-26 | 2024-05-16 | Regulatory/Licensing/Permit Delay | 230 | 230 | See Note 53A | 5340.5491 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 2282.1274 | 322.3295 | 269.1533 | 283.0747 | 2183.8643 | 5340.5491 | 1837.1587 | See Note 57A | N/A | See Note 59A | 5340.5491 | None | 100% | 0% | Replaces PB-08.06 previously included in July 2021 SRP. Project has been shifted from PB-08 program blanket due to realignment of capital project structure. Existing access roads will be rehabilitated/repaired, some slope repair is also required, and an environmental assessment and formal consultation with the U.S. Fish & Wildlife Services for mitigation of impacts to affected biological and plant habitat/resources;
N/A | PB-51 | Substation HVAC Redundancy Program | Not applicable at program level | Not applicable at program level | SCE operates switching centers to provide reliable power to its customers. As the grid has become automated, analog equipment in switching center rooms has been replaced with digital equipment (e.g., electronic components and servers). As this digital equipment operates around the clock, it emits heat and requires cooling to maintain function. | Install HVAC systems | Upgrade | Not applicable at program level | Infrastructure Enhancement Protect Substation Equipment | N/A | N/A | Not applicable at program level | Not applicable | Not applicable at program level | Not applicable at program level | See Note 16C | Not applicable at program level | Sue DiBernardo, Regulatory Affairs | See Note 19B | Not applicable at program level | See Note 21A | Not applicable at program level | See Note 23B | Not applicable at program level | COS-00-RE-MA-SBHVAC | 6987 | See Note 27A | Not applicable at program level | Not applicable at program level | 2022 | Annual capital operating plan process | N/A | N/A | N/A | N/A | Not applicable at program level | Not applicable at program level | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Not applicable at program level | See Note 46A | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | Not applicable at program level | See Note 53A | Not applicable at program level | 0 | 0 | 2513 | 2577.89 | 2644.7267 | Not Available | 7735.6167 | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not applicable at program level | Not applicable at program level | See Note 57A | N/A | See Note 59A | See Note 60A | None | 0% | 100%
GIDAP | SP-01 | Calcite Substation Construction (TOT552_TOT640) | 34.547, -116.952 | Lucerne Valley, San Bernardino County | Construct new Calcite 230 kV Substation to interconnect renewable generation projects. Additional information can be found here: https://www.sce.com/about-us/reliability/upgrading-transmission/calcite. | Loop Calcite into existing Lugo-Pisgah No.1 220 kV T/L, New substation and supporting equipment (switchgear and protection) | New | SP-35, SP-93 | Work Requested by Others | GIDAP (Generation Interconnection) | N/A - New | N/A - New | ● Power Flow ● Transient ● Post Transient ● Short Circuit Duty | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Non-HFRA | See Note 16C | Desert Region, Extreme Temperature Conditions | Brent Gokbudak, MPO-Project Development & Execution | See Note 19B | ~10 | 220 kV | 220 kV | See Note 23B | 7 separate WOs/ Elements | 5 separate CWBS | 6902 | See Note 27A | Yes | 2010 | Pre-2017 | FRM/CRT | 2010 | N/A, considered under the CAISO Generation Interconnection Process | N/A, under the CAISO Generation Interconnection Process | N/A, under the CAISO Generation Interconnection Process | See Col. 37 | Incentive CWIP 2022 = 6,391 | Expected EIR 2023 | EIR | State Lands Commission/ San Bernardino County | PTC Expected | Not yet filed 2024 | N/A | N/A | Planning | See Note 46A | 2026-01-02 | Yes | 2021-03-04 | 2027-03-15 | At the request of the interconnection customer Siena Solar project was put on hold/suspension. Then in Apr 2023, CAISO and the Customer issued the ATP to recommence licensing for the Calcite Substation. | 60800 | 57113.6458 | See Note 53A | 55828.3076 | 500 | 3000 | 14708.63 | 14220.631 | 17007.9 | 0 | 49437.161 | 5220.4516 | 363.7474 | 188.3739 | 293.426 | 325.1476 | 6391.1466 | 1933.3558 | See Note 57A | 100% | See Note 59A | 6391.1466 | Abandoned Plant & CWIP Incentives (134 FERC ¶ 61,181) | 100% | 0% | Column 9: GIDAP (Generator Interconnection) Column 29 & 32: 2010 per Granite Wind GIA; 2016 (LGIA) Column 52: Source= v0 Project Summary; Represents PIN level estimate; PWMIF of $60.8M is listed under PIN 7885 as the project received an updated PIN, which was later reverted back to PIN 6902. Regarding the forecast cost, Column 55, SCE is in the process of updating forecast expenditures for this project to reflect interconnecting customers' licensing activities (e.g. the CEQA agency's delay in publishing the draft EIR). SCE anticipates the 2022 forecast to be ~$1million based on most recent information.
GIDAP | SP-02 | Colorado River Substation Expansion: Dracker Project (TOT276_Q294) | 33.589, -114.814 | Blythe, Riverside County | Install the 2nd 500/230 kV AA Transformer Bank at Colorado River Substation to accommodate new generation interconnections | ● Two (2) new 230 kV circuit breakers ● Two (4) new 230 kV disconnect switches ● Two (2) new 500 kV circuit breakers ● Two (4) new 500 kV disconnect switches ● One (1) new 1120 MVA 500/230 transformer bank ● Associated new protection relays ● Modify existing West of Colorado River CRAS | New, upgrade | SP-33, SP-21 | Work Requested by Others | GIDAP (Generation Interconnection) | 2019 | N/A - New Equipment to be installed. Existing substation constructed in 2013. | ● Power Flow ● Transient ● Post Transient ● Short Circuit Duty | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Non-HFRA | See Note 16C | High Wind Events, Extreme Temperature Conditions | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | 77 | 500 kV & 230 kV | 500kV - 220kV, 1120 MVA | See Note 23B | 2 separate WOs | 1 CWBS | 8169 | See Note 27A | Yes | 2010 | Pre-2017 | FRM/CRT | 2020 | N/A, considered under the CAISO Generation Interconnection Process | N/A, under the CAISO Generation Interconnection Process | N/A, under the CAISO Generation Interconnection Process | See Col. 37 | 2021 = 23,779 2022 = 1,157 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2021-02-01 | No | 2020-12-01 | 2021-11-05 | Schedule alignment with the development of generation projects on the Colorado River 230 kV Bus, triggering the project. | 34131 | 34131 | See Note 53A | 24935.8319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 301.2468 | 5026.585 | 18451.0663 | 1156.9338 | 24935.8319 | 2296.0846 | See Note 57A | 100% | See Note 59A | -2.3132e-11 | Abandoned Plant & CWIP Incentives (134 FERC ¶ 61,181) | 100% | 0% | Column 2: SCE has updated the Project name for alignment with current project. Formerly reported as "Colorado River Substation Expansion" Column 9: GIDAP (Generator Interconnection) Column 29 & 32: 2010 per Palo Verde Solar II / Blythe Solar Power/Dracker GIA Column 38: Work expected to be exempt from GO 131-D licensing Column 52: Source= PMWIF (v0 Proj Summary); Represents PIN & WO level estimate; CRT (2/29/2012) total project original estimate of $131M which includes additional scope
TPP | SP-03 | West of Devers Conductor Upgrade | Not applicable at program level | Riverside, San Bernardino County | Upgrade five 230 kV lines on the west side of Devers 230kV substation to deliver energy from renewable resources located in the East of Devers Area to the load center. Full description found here: https://www.cpuc.ca.gov/environment/info/aspen/westofdevers/westofdevers.htm. | Upgrade five 230 kV lines on the west side of Devers 230kV substation to 2B-1590 ACSR conductor. This project also includes partial upgrade to San Bernardino - Etiwanda and San Bernardino - Vista 220kV lines. | Replacement | SP-18, SP-21, SP-33, SP-44 | Infrastructure Enhancement | GIDAP (Generation Interconnection) | SCE performs annual patrols and triennial detailed inspections of its transmission circuits, which inspect the structures and lines on those circuits. Last inspections for the majority of these lines happened in 2019. | 30-40 Years | ● Power Flow ● Transient ● Post Transient ● Short Circuit Duty | Project alternatives are discussed in Section C of the Final EIR | Tier 2, Tier 3 | See Note 16C | High Wind Events, Extreme Temperature Conditions, Desert Region, High Seismic Area, Mountainous | Brent Gokbudak, MPO-Project Development & Execution | Approx. 181 circuit miles of existing 220 kV line facilities (per FEIR) | Project will upgrade substation equipment at Devers, El Casco, Etiwanda, San Bernardino, and Vista Substations to accommodate increased power transfer on 220 kV lines. Each substation is existing; no new disturbance will occur (total combined acreage of five substations is ~172 acres). Additional detail at: https://www.cpuc.ca.gov/environment/info/aspen/westofdevers/ntps/ntp002_062917.pdf (remove - check with Kyle) | 230 | See Note 22A | See Note 23B | 17 separate Wos/ Elements | 15 separate CWBS | 6420 | See Note 27A | Yes | 2013 | Pre-2017 | FRM/CRT | 2011 | 2011 to present | N/A | ONLY 2012-2013 TPP available online http://www.caiso.com/Documents/BoardApproved2012-2013TransmissionPlan.pdf | See Col. 37 | 2018 = 3,297 2019 = 109 2020 = 15,246 2021 = 306,701 2022 = 12,827 | Final Certified 2016 | EIR/EIS | CPUC/BLM | CPCN A.13.10-020 | 2013 | Approved | 2016 | Operational | See Note 46A | 2018-03-15 | Yes | 2019-12-31 | 2021-05-14 | Licensing delays | 1034000 | 981525.7078 | See Note 53A | 356429.1913 | 8217.021 | 10036.8749 | 0 | 0 | 0 | 0 | 18253.8959 | 233928.9807 | 248922.7013 | 199897.5982 | -349505.5744 | 4931.5896 | 338175.2954 | 62999.3698 | See Note 57A | 100% | See Note 59A | 974.7278 | Abandoned Plant & CWIP Incentives (134 FERC ¶ 61,181) | 100% | 0% | Column 53: The maximum and reasonable prudent cost established in the Certificate of Public Convenience and Necessity pursuant to California Public Utilities Code Section 1005.5 (a) for this project is $1,010 Million as noted in CPUC Decision 16-08-017 dated August 18, 2016 and issued on August 29, 2016. Cols. 54 and 56.2021: Transmission Capability Lease executed with Morongo Transmission LLC on July 12, 2021. As such, referenced columns reflect a reduction of $400 million from capital additions and plant in service. Additional information can be found in FERC Docket Nos. ER21-669 and ER21-1280.
GIDAP/ TPP | SP-04 | Alberhill Substation Loop-In | 33.736, -117.414 | Lake Elsinore/ Wildomar/ Menifee/, Riverside County | The load served by the Valley South 115 kV System is projected to exceed transformer capacity in 2022 (Peak Demand, 1 in 5 Heat Storm). Additionally, the Valley South subtransmission system has no ties to any other SCE 115 kV system which limits the operational flexibility of the system to allow for transfers of load during emergency conditions, or for necessary lines outages for routine maintenance or new facility construction. The scope of the Alberhill Project consists of the construction of an additional 500/115 kV system (substation and 115 kV lines with ties to the Valley South 115 kV System). This would allow for the existing Valley South load to be shared between the two 115 kV systems (Valley South & Alberhill), thus addressing the transformer overloads as well as the system operational flexibility concerns resulting in increased reliability. Initially there would be five substations transferred from the Valley South 115 kV System (Elsinore, Ivyglen, Fogarty, Skylark, and Newcomb Substations) which transfers approximately 360 MVA of load. The new 500/115 kV system would be served by looping the existing Serrano-Valley 500 kV Transmission Line. | Transmission: 500 kV line scope: Loop existing Valley-Serrano 500 kV line forming the new Alberhill-Serrano 500 kV Line and new Alberhill-Valley 500 kV Line. 115 kV line scope: Approximately 21 miles of 115 kV line construction and/or reconfiguration. Substation: Alberhill Substation: Construct a 500 kV GIS switchrack with an ultimate buildout of 6 positions. Initially equip 3 positions to accommodate (2) 500 kV lines and (2) 560 MVA 500/115 kV transformers. Install (2) 560 MVA 500/115 kV transformers. Construct an 8 position 115 kV open air rack with an ultimate buildout of 11 positions. Install a 46.8 MVAR capacitor bank connected to the 115 kV bus. | New | None | Capacity Increase | Reliability and Resiliency GIDAP (Generation Interconnection) | N/A - New | N/A - New | Bank Capacity, Power Flow, Short Circuit Duty SCE Subtransmission Planning Criteria and Guidelines | Project alternatives are discussed in Chapter 3 of the Final EIR. Additional alternatives are being evaluated as a result of the CPUC decision in August 2018, which directed SCE to supplement the record with additional analysis, including the response to 9 items. Item "g" outlines the requirements related to a cost/benefit analysis of several alternatives for enhancing reliability and providing additional capacity. SCE filed the last responses to the 9 items in January, 2020 | Tier 2, Tier 3 | See Note 16C | High Wind Events, Flooding, High Fire Risk Area, Extreme Temperature Conditions | John Keelin, MPO - Project Dev. & Execution | 500kV - ≈ 3 miles 115kV - ≈ 21 miles (Reference Chapter 2.1.2 of the Final EIR) | 34-40 | 500 | Initial - 1120MVA; Ultimate - 1680 MVA and 560MVA Spare | See Note 23B | 9 separate Wos/ Elements | 8 separate CWBS | 6092 | See Note 27A | Yes | 2009 | Pre-2017 | FRM/CRT | 2009 | 2009-present | N/A | Multiple URL (copy/paste in your web browser): http://www.caiso.com/Documents/091216-General-DecisiononAlberhillSubstationProject-MOTION.pdf http://www.caiso.com/Documents/091216DecisiononAlberhillSubstationProject-Memo.pdf | See Col. 37 | 2010 = 8,269 2022 = 46 Incentive CWIP 2022 = 26,671 | FEIR 2017 | EIR | CPUC | CPCN A.09-09-022 | 2009 | Filed and Under Review | 2019 | Planning | See Note 46A | 2026-06-01 | Yes | 2014 | 2029-06-30 | Licensing delays | 473000 | 247626.652 | See Note 53A | 240847.022 | 1100.9209 | 1572 | 1048 | 17117.0812 | 73950.3254 | 111072.1113 | 205860.4388 | 28653.1233 | 1661.5939 | 1817.0589 | 1492.7085 | 1362.0986 | 34986.5832 | 10468.0803 | See Note 57A | N/A | See Note 59A | 26679.8452 | Abandoned Plant (161 FERC ¶ 61,107 at P 21) & CWIP Incentives (161 FERC ¶ 61,107 at P35) | 100% | 0% | Column 9: Load Growth, Reliability Column 36: Project is not yet operational but FERC portion of Plant Held For Future Use amount is $6,392M, as reflected in SCE's TO2023 Draft Annual Update. Column 52: Source= CRT (04/2010);Project was approved at CRT (04/2010) previously for $315M. SCE provides the more recent update per CRT (06/27/2017) Original Project Cost updated per FRM
TPP | SP-05 | Eldorado-Lugo-Mohave RPS Upgrade | 35.798, -115.008 | San Bernardino County, California; Clark County, Nevada; the cities of Hesperia, California and Boulder City, Nevada; the unincorporated community of Lucerne Valley in California; and the unincorporated communities of Searchlight and Laughlin in Nevada. The Proposed Project would also cross lands under the jurisdiction of the Bureau of Land Management (BLM), the National Park Service (NPS), the Bureau of Reclamation, and the Department of Defense, as well as lands managed by the California State Lands Commission and the Nevada State Parks | Increase series compensation on the Eldorado-Lugo and Lugo-Mohave 500 kV transmission lines for the purpose of meeting the needs of the California Renewable Portfolio Standard (RPS) | The main activity associated with the Proposed Project involves the construction of two new 500 kilovolt (kV) mid-line series capacitors—the proposed Newberry Springs Series Capacitor and Ludlow Series Capacitor. As part of the Proposed Project, SCE would connect the proposed mid-line series capacitors to SCE’s existing system by installing transmission interface, as well as distribution and telecommunications facilities. In addition, the Proposed Project involves the modification of existing transmission, subtransmission, and distribution facilities along the Eldorado-Lugo, Eldorado-Mohave, and Lugo-Mohave 500 kV Transmission Lines. The Proposed Project would also include the installation of optical ground wire (OPGW) on approximately 235 miles of the Eldorado-Mohave and Lugo-Mohave 500 kV Transmission Lines. Lastly, the Proposed Project would include modifications within the existing Eldorado, Lugo, and Mohave Substations. | Upgrade | None | Other - See Notes | Meet the requirements of existing IA that require the Proposed Project to achieve Full Capacity Deliverability Status (FCDS) -Facilitate the FCDS of new renewable electric generation resources being developed in multiple areas within the CAISO controlled grid | Various - SCE performs annual patrols and triennial detailed inspections of its transmission circuits, which inspect the structures and lines on those circuits. Last inspections for the majority of these lines happened in 2019. | 30+ years | The Proposed Projects was performed taking into account NERC, WECC, and CAISO Planning Standards and/or Criteria. In addition the Propose Project was identified as a Policy Driven Transmission Solution by the CAISO. | Project alternatives are discussed in Chapter 5.2 of the PEA. | Tier 2 | See Note 16C | High Wind Events, Extreme Temperature Conditions, Mudslide, Mountainous, Desert Region | Brent Gokbudak, MPO-Project Development & Execution | N/A | See Note 20B | 500 kV | See Note 22A | See Note 23B | 19 separate Wos/ Elements | 11 separate CWBS | 7546 | See Note 27A | Yes | 2017 | Pre-2017 | FRM/CRT | 2013 | Eldorado-Lugo: 2012-2013 TPP to present Lugo-Mohave: 2013-2014 TPP to present | N/A | Multiple URL (copy/paste in your web browser): http://www.caiso.com/Documents/BoardApproved2012-2013TransmissionPlan.pdf http://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan_July162014.pdf | See Col. 37 | 2021 = 8,182 2022 = 2,775 Incentive CWIP 2021 = 224,967 | Final Certified 2020 | MND/EA | CPUC/BLM | CPCN A.18-05-007 | 2018 | Approved | 2020 | Construction more than 50% completed | See Note 46A | 2020-11-02 | Yes | 2016 | 2023-12-31 | Licensing delays MEER building delivery delay | 191000 | 177959.2534 | See Note 53A | 326907.5687 | 40777 | 36477 | 13728.66 | 0 | 0 | 0 | 90982.66 | 65665.3481 | 37101.2494 | 33244.9995 | 61859.8193 | 38053.4923 | 235924.9087 | 27545.7777 | See Note 57A | N/A | See Note 59A | 212122.9467 | Abandoned Plant (161 FERC ¶ 61,107 at P 21) & CWIP Incentives (161 FERC ¶ 61,107 at P35) | 100% | 0% | Column 9: The primary purpose of this project is to support the requirements of the California Renewable Standard (RPS) Column 32: Eldorado-Lugo: 2013; Lugo-Mohave: 2014; SCE provides the earlier date Column 52: Source= FRM (05/01/2017) The forecast for Eldorado-Lugo-Mohave Series Capacitor Project (ELM Project) does not include additional work that has been delineated and remains subject to ongoing analyses. This work is to protect nearby SoCalGas pipelines from the effects of induced alternating current (AC). SCE likely will have to install physical mitigation facilities, although the scope and cost of this mitigation is not yet known because SCE and SoCalGas are still evaluating the level of mitigation that will be necessary.
TPP | SP-06 | Mesa Substation Expansion | 34.036, -118.110 | Monterey Park, Los Angeles County | Expand existing Mesa 220 kV Substation to 500 kV. Construct new 500 kV switchrack and rebuild the 230/66/16 kV switchracks. Loop-in Mira Loma-Vincent 500 kV to Mesa. Loop-in Goodrich-Laguna Bell and Rio Hondo-Laguna Bell 230 kV lines into Mesa Substation. Additional detail can be found at: https://www.cpuc.ca.gov/Environment/info/ene/mesa/mesa.html. | Substation expansion; Switchrack | New, replacement | None | Other - See Notes | Substation Capacity | N/A - New. Last inspections at current Mesa Sub in 2019. | N/A - New Equipment to be installed. Existing substation constructed 60+ years | ● Power Flow ● Transient ● Post Transient ● Short Circuit Duty | Project alternatives are discussed in Chapter 5 of the Final EIR. | Non-HFRA | See Note 16C | High Seismic Area | Brent Gokbudak, MPO-Project Development & Execution | N/A, though project will include removal, relocation, modification, and/or construction of transmission, subtransmission, and distribution structures within SCE-owned properties, rights-of-way (ROW s), and franchise areas in the cities of Monterey Park, Montebello, and Commerce and portions of unincorporated Los Angeles County to accommodate the new substation configuration. | ~72.1 acreage total proposed project need; 86.2 total site acreage (per Final EIR) | 500 / 220 | 3360MVA / 500kV, 220kV, 840MVA /220kV, 66kV 56MVA /66kV, 16kV | See Note 23B | 51 separate WOs/ Elements | 50 separate CWBS | 7555 | See Note 27A | Yes | 2015 | Pre-2017 | FRM/CRT | 2014 | 2013-2014 TPP to present | N/A | http://www.caiso.com/Documents/Board-Approved2013-2014TransmissionPlan_July162014.pdf | See Col. 37 | 2017 = 1,657 2018 = 7,852 2019 = 146,170 2020 = 37,952 2021 = 6,967 2022 = 241,272 2023 =12,296 | Final Certified 2017 | EIR | CPUC | PTC A.15-03-003 | 2015 | Approved | 2017 | Operational | See Note 46A | 2017-10-02 | Yes | 2020-12-01 | 2023-01-11 | Delay in the regulatory process and obtaining notice to proceed from the CPUC. | 608000 | 395417.6632 | See Note 53A | 479580.463 | 17099.693 | 9093.56 | 1178.6987 | 0 | 0 | 0 | 27371.9517 | 139550.9258 | 71302.204 | 118922.9745 | 80612.5295 | 41819.8775 | 452208.5113 | 43117.7556 | See Note 57A | N/A | See Note 59A | 30.6929 | CWIP Incentive (161 FERC ¶ 61,107) | 100% | 0% | Column 4: Some work occurring in nearby cities and portions of unincorporated Los Angeles County Column 9: To provide safe and reliable service. To address reliability concerns, flexibility, and comply with all applicable reliability planning criteria required by the North American Electric Reliability Corporation, Western Electricity Coordinating Council, and CAISO while minimizing environmental impacts. Column 29: 2014 (Planning & Development); 2015 (Full Project Cost) Column 52: Source= CRT (04/2016);Project was approved at CRT (05/2014) previously for $54.8M. SCE provides the more recent update per CRT (04/2016)
N/A | SP-07 | Sylmar Electrode Upgrade (Land Segment) | 34.314, -118.493 | Sylmar/ North Hills/ Granada Hills/ Balboa Lake/ Los Angeles, Los Angeles County | Upgrade the Sylmar Electrode to compensate for the upgraded PDCI line. The land and submarine cables were under rated for operation and had sustained numerous failures. This would improve operation and reliability of the Electrode Line, provide operation and flexibility of the PDCI, increase emergency rating, reduce need for emergency repair and will help meet the current and future PDCI operating capacity. | Overhead lines, underground cables | Replacement | SP-08 | Work Requested by Others | Age/Condition | Performed by LADWP | 30-50 years old, replaced in 2018. | LADWP is the Operating Agent owner and driver of determining need and proposals of Capital projects, SCE performs engineering and cost analysis internally to verify need and cost validity of proposals. | Derate the line to 1550 MW to avoid WECC impacts but only result in very short duration use of the electrode. | Tier 2 | See Note 16C | Risk of corrosion due to ocean and wind. | Brent Gokbudak, MPO-Project Development & Execution | See Note 19B (Only affects HVDC grounding) | See Note 20B | See note 21A | See Note 22A | See Note 23B | 900250937 | CET-OT-OT-ME-313802 | 3138 | See Note 27A | Yes | 2010 | Pre-2017 | FRM/CRT | No | N/A | N/A | N/A | See Col. 37 | 2018 = 20,500 2019 = 51 2020 = 109 2021 = 8 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | Not Available | No | 2014 | 2018-11-16 | N/A | 24650 | 24650 | See Note 53A | 20668.6103 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 0 | 20500.0832 | 51.4434 | 108.5848 | 8.499 | 0 | 20668.6103 | 4574.7045 | See Note 57A | N/A | SCE is not currently aware of a project specific cost benefit performed. This activity largely performs reactive work in response to LADWP determinations. | 9.2063e-12 | None | 100% | 0% | Column 47, 49, 51: Managed by LADWP Column 52: Source= CRT (2010 & 04/04/2016); Represents SCE's portion of the project only (50%)- total project cost including LADWP portion $49.3M
N/A | SP-08 | Sylmar Electrode Upgrade (Ocean Segment) | 34.314, -118.493 | Pacific Palisades, Los Angeles County, CA | The Sylmar Ground Return System includes 31 miles of overhead lines, underground cables, and underwater cable segments that begin at the Sylmar Converter Station, the southern terminus of the PDCI. From the Gladstone Vault, the new marine cables would extend to a new electrode array in the Santa Monica Bay. The marine cables would be installed several feet beneath the ocean floor to approximately two miles offshore where the new electrode array would be located on the ocean floor at a depth of approximately 100 feet below mean sea level. The array would be composed of 36 concrete vaults, arranged in two rows of 18 vaults, resting directly on the ocean floor. | Overhead lines, underground and underwater cables | Modification/Upgrade | SP-07 | Work Requested by Others | Age/Condition | Performed by LADWP | 30-50 years old, replaced in 2018. | LADWP is the Operating Agent owner and driver of determining need and proposals of Capital projects, SCE performs engineering and cost analysis internally to verify need and cost validity of proposals. | Derate the line to 1550 MW to avoid WECC impacts but only result in very short duration use of the electrode. | Tier 2 | See Note 16C | Risk of corrosion. | Brent Gokbudak, MPO-Project Development & Execution | See Note 19B (Only affects HVDC grounding) | See Note 20B | See note 21A | See Note 22A | See Note 23B | 901653468 | CET-OT-OT-ME-313802 | 3138 | See Note 27A | Yes | 2014 | Pre-2017 | FRM/CRT | No | N/A | N/A | N/A | See Col. 37 | 2018 = 23,349 2019 = 5,222 2020 = 68 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | Not Available | No | Not readily available | 2018-11-16 | N/A | 40650 | 40650 | See Note 53A | 28639.3195 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 0 | 23349.4693 | 5222.0703 | 67.7798 | 0 | 0 | 28639.3195 | 283.5847 | See Note 57A | N/A | SCE is not currently aware of a project specific cost benefit performed. This activity largely performs reactive work in response to LADWP determinations. | 3.5179e-12 | None | 100% | 0% | Column 47, 49, 51: Managed by LADWP Column 52: Source= CRT (2014 & 04/04/2016); Represents SCE's portion of the project only (50%)- total project cost including LADWP portion $81.3M
N/A | SP-09 | Sylmar Converter Station AC/DC Filter Replacement | 34.314, -118.493 | Sylmar, Los Angeles County | Upgrade the existing AC&DC Filter Banks along with Control and Protection System for the Pacific DC Intertie (PDCI) at Sylmar Converter Station. | AC&DC Filter Banks | Replacement | None | Work Requested by Others | Age/Condition | Performed by LADWP | 30-50 years old, currently being replaced. | LADWP is the Operating Agent owner and driver of determining need and proposals of Capital projects, SCE performs engineering and cost analysis internally to verify need and cost validity of proposals. | SCE is not currently aware of alternatives considered (contractual) | Non-HFRA | See Note 16C | Risk of corrosion and earthquakes. | Brent Gokbudak, MPO-Project Development & Execution | See Note 19B | See Note 20B | See note 21A | 220 kV SCE; 230 kV LADWP (Project does not affect substation capacity) | See Note 23B | 900713761 | CET-OT-OT-ME-313803 | 3138 | See Note 27A | Yes | 2013 | Pre-2017 | FRM/CRT | No | N/A | N/A | N/A | See Col. 37 | 2020 = 118,074 2021 = 6.042 2022 = 2,524 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | Not Available | No | Not readily available | 2020-06-10 | N/A | 52000 | 52000 | See Note 53A | 126639.8472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60092.4123 | 37042.6897 | 20938.5841 | 6042.3823 | 2523.7787 | 126639.8472 | 10390.9034 | See Note 57A | N/A | SCE is not currently aware of a project specific cost benefit performed. This activity largely performs reactive work in response to LADWP determinations. | -5.9567e-12 | None | 100% | 0% | Column 47, 49, 51: Managed by LADWP Column 52: Source= CRT (01/29/2013 & 04/04/2016); Represents SCE's portion of the project only (50%)- total project cost including LADWP portion $104M
TPP | SP-10 | Riverside Transmission Reliability Project | Various Locations | Jurupa Valley, Riverside County | Increase capacity to the City of Riverside and provide a second point of service at the 220 kV transmission level. Full details can be found here: https://www.cpuc.ca.gov/Environment/info/panoramaenv/RTRP/index.html | • Approximately 6 miles of new overhead and 4 miles of new underground 230-kilovolt (kV) transmission line • New 230-kV Wildlife Substation • Modifications of existing overhead distribution lines; | New | None | Work Requested by Others | (IFA) Load Interconnection | N/A - New | N/A - New | Bank Capacity, Power Flow, Short Circuit Duty SCE Subtransmission Planning Criteria and Guidelines | Project alternatives are discussed in Chapter 6 of the Final Subsequent Environmental Impact Report | Tier 2 | See Note 16C | High Wind Events, Extreme Temperature Conditions | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | Double Circuit 6 miles OH and Double Circuit 4 miles UG | 3 | 220 kV | 560 MVA / 220kV | See Note 23B | 10 separate WOs/ Elements | 9 separate CWBS | 5450 | See Note 27A | Yes | 2015 | Pre-2017 | FRM/CRT | 2007 | 2007 to present | N/A | CAISO 2007 Trans. Plan page 51, line 9 (not available online, but can be provided upon request) | See Col. 37 | CWIP Incentive 2021 = 38,483 | Final Certified 2020 | Subsequent EIR | CPUC | CPCN A.15-04-013 | 2015 | Approved | 2020 | On Hold | See Note 46A | 2024-08-30 | Yes | 10/1/2009 (2007 CAISO Plan) February 2019 [Per CPCN Amended Application] | 2028-12-31 | Licensing delays | 249200 | 239158.4043 | See Note 53A | 586993.2818 | 899.9 | 899.9 | 75197.9617 | 212832.1302 | 61133.4575 | 197546.753 | 548510.1023 | 11798.2282 | 1831.9273 | 9977.8585 | 6463.3568 | 8411.8087 | 38483.1795 | 6204.6818 | See Note 57A | 100% | See Note 59A | 38483.1183 | CWIP (172 FERC ¶ 61,241 at P 31) and Abandoned Plant (172 FERC ¶ 61,241 at P 26) Incentives | 100% | 0% | Column 29: 2010 (Planning & Development); 2015 (Full Project Cost) Column 53: The maximum and reasonable prudent cost established in the Certificate of Public Convenience and Necessity pursuant to California Public Utilities Code Section 1005.5 (a) for this project is $408 Million as proposed by SCE and $521 Million if built as Alternative 1 as noted in CPUC Decision 20-03-001 dated March 12, 2020 and issued on March 18, 2020; Column 52: Source= CRT (03/27/2015)
TPP | SP-11 | Lugo Substation Transformer Bank Conversion | 34.367, -117.369 | Hesperia, San Bernardino County | This project involves conversion of the current bank-on-bus configuration to a double breaker configuration for 500/220 kV transformer banks. | Equip Lugo 2AA transformer bank with 500 kV circuit breakers. | New | None | Infrastructure Replacement | Substation Reliability | 2019 | N/A - New equipment. Bank age varies, 1 year and 20+ years | Bank Capacity, Power Flow, Short Circuit Duty SCE Subtransmission Planning Criteria and Guidelines | Equipping the banks in circuit breakers configuration aligns to SCE criteria. | Tier 2 | See Note 16C | Extreme Temperature Conditions, Desert Region, High Seismic Area | Brent Gokbudak, MPO-Project Development & Execution | See Note 19B | 46 | 500 kV | 500/220 kV | See Note 23B | 800308934 | CET-ET-TP-RL-679100 | 6791 | See Note 27A | Yes | 2010 | Pre-2017 | Annual Capital Operating Plan Process | 2008 | 2008-present | N/A | See Table 3-5, Item 3 and in Appendix B, SCE Service Area, Project No 3 | See Col. 37 | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Engineering more than 50% completed | See Note 46A | 2023-10-02 | No | 2011-12-01 | 2027-12-31 | This project has been deferred due to coordination of work at Lugo Substation. | 12000 | 12000 | See Note 53A | 12503.7781 | 20 | 50 | 765 | 920 | 0 | 0 | 1755 | 10180.8848 | 194.273 | 160.9797 | 110.6081 | 102.0324 | 10748.7781 | 5325.4607 | See Note 57A | N/A | See Note 59A | 10528.4134 | None | 100% | 0% | Column 9: To meet SCE substation reliability criteria and provide operational flexibility Column 52: Source= PMWIF
N/A | SP-12 | La Fresa Substation MEER Install | 33.869, -118.333 | Torrance, Los Angeles County | Install a new MEER and cut over existing protection and upgrade CTs on existing banks. Upgrade SAS from 5.5 to 6X. | MEER | New, upgrade | None | Capacity Increase | Substation Capacity | 2019 | Replaced asset age not available at the moment | Bank Capacity, Power Flow, Short Circuit Duty SCE Subtransmission Planning Criteria and Guidelines | SCE is not currently aware of alternatives considered for FERC portion of project | Non-HFRA | See Note 16C | High Seismic Area, Coastal Area | Demetric Brown, MPO - Programs | See Note 19B | 22.7 | See note 21A | 280MVA/220kV, 66kV | See Note 23B | 900522611 | CET-ET-LG-TS-682400 | 6824 | See Note 27A | Yes | 2011 | Pre-2017 | FRM/CRT | No | N/A | N/A | N/A | See Col. 37 | 2019 = 18,210 2020 = 592 2021 = 91 2022 = 95 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2013-07-01 | No | 2014-12-20 | 2019-12-23 | ​Construction Completion date extended to incorporate misc. remaining items and demolition of retired equipment and wiring. | 13700 | 2881.1239 | See Note 53A | 18987.0767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15633.1821 | 2576.3523 | 591.7662 | 90.9187 | 94.8574 | 18987.0767 | 7162.8433 | See Note 57A | N/A | See Note 59A | -1.9163e-11 | None | 100% | 0% | Column 52: Source= FRM (10/12/2011);Represents Phase 2 of project only which aligns with appropriate project scope
N/A | SP-13 | Johanna Substation Transformer Bank Conversion | 33.714, -117.852 | Santa Ana, Orange County | This project involves conversion of the current bank-on-bus configuration to a double breaker configuration for 220/66 kV transformer banks. | Equip Johanna 3A & 4A transformer banks with 220 kV circuit breakers. | New | None | Infrastructure Replacement | Substation Reliability | 2019 | N/A - New equipment. Substation constructed 35+ years. | Bank Capacity, Power Flow, Short Circuit Duty SCE Subtransmission Planning Criteria and Guidelines | Equipping the banks in circuit breakers configuration aligns to SCE criteria. | Non-HFRA | See Note 16C | High Seismic Area, Coastal Area | Demetric Brown, MPO - Programs | See Note 19B | 9.9 | 220 kV | N/A-No modification is being made to the existing substations transformer banks. There is no increase in the substation or transformer capacity | See Note 23B | 902067053 | CET-ET-TP-RL-711500 | 7115 | See Note 27A | Yes | 2017 | 2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col.37 | 2021 = 6,705 22022 = 756 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2021-07-06 | No | 2019-12-31 | 2021-12-22 | This project deferred due to coordination of work at Johanna Substation. | 6705 | 5423.6361 | See Note 53A | 7461.2416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2049.019 | 196.7249 | 247.2242 | 4212.0984 | 756.1751 | 7461.2416 | 1494.2618 | See Note 57A | N/A | See Note 59A | 9.9936e-12 | None | 100% | 0% | Column 9: To meet SCE substation reliability criteria and provide operational flexibility Column 52: Source= PMWIF (v10 Proj Summary); Represents PIN level estimate; WO level estimate is $6.504M
N/A | SP-14 | Chino Substation Transformer Bank Conversion | 33.999, -117.680 | Chino, San Bernardino County | This project involves conversion of the current bank-on-bus configuration to a double breaker configuration for 220/66 kV transformer banks. | Equip Chino 1A transformer bank with 220 kV circuit breakers | New | None | Infrastructure Replacement | Substation Reliability | 2019 | N/A - New equipment. Substation constructed 40+ years. | Bank Capacity, Power Flow, Short Circuit Duty SCE Subtransmission Planning Criteria and Guidelines | Equipping the banks in circuit breakers configuration aligns to SCE criteria. | Non-HFRA | See Note 16C | High Wind Events, Extreme Temperature Conditions, High Seismic Area | Demetric Brown, MPO - Programs | See Note 19B | 14.8 | 220kV | N/A-No modification is being made to the existing substations transformer banks. There is no increase in the substation or transformer capacity | See Note 23B | 3 separate WOs | 3 separate CWBS | 7120 | See Note 27A | Yes | 2014 | Pre-2017 | FRM/CRT | No | N/A | N/A | N/A | See Col. 37 | 2019 = 33,191 2020 = 4,022 2021 = 1,491 2022 = -2 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2015-11-16 | No | 2018-06-01 | 2020-12-31 | Permit delays from the city of Chino; construction challenges especially for the MEER building; outage and cutover windows for the both 220 and 66 kV switchracks | 97200 | 58161.9117 | See Note 53A | 38703.1808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29767.6166 | 3423.8074 | 4022.1728 | 1491.3105 | -1.7266 | 38703.1808 | 9836.0996 | See Note 57A | N/A | See Note 59A | -8.5249e-12 | None | 100% | 0% | Column 9: To meet SCE substation reliability criteria and provide operational flexibility Column 52: Source= CRT (09/23/2014);Represents total project cost estimate
N/A | SP-15 | Springville Substation Transformer Bank Conversion | 36.108, -118.938 | Strathmore, Tulare County | This project involves conversion of the current bank-on-bus configuration to a double breaker configuration for 220/66 kV transformer banks. | Equip Springville 1A transformer bank with 220 kV circuit breakers | New | None | Infrastructure Replacement | Substation Reliability | 2019 | N/A - New. Substation structure 70+ years | Bank Capacity, Power Flow, Short Circuit Duty SCE Subtransmission Planning Criteria and Guidelines | Equipping the banks in circuit breakers configuration aligns to SCE criteria. | Tier 2 | See Note 16C | Seismic - Moderate | Demetric Brown, MPO - Programs | See Note 19B | 10.4 | 220 kV | 220/66 kV | See Note 23B | 901007168 | CET-ET-TP-RL-751800 | 7518 | See Note 27A | Yes | 2013 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2019 = 9,622 2020 = -449 2021 = 191 2022 = 286 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2016-07-25 | No | 2015-06-01 | 2019-05-22 | Coordination with other projects in the area | 4700 | 3760 | See Note 53A | 9650.4948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7735.5305 | 1886.4522 | -448.5035 | 191.3282 | 285.6873 | 9650.4948 | 2104.8297 | See Note 57A | N/A | See Note 59A | 4.6808e-12 | None | 100% | 0% | Column 9: To meet SCE substation reliability criteria and provide operational flexibility Column 52: Source= PMWIF
N/A | SP-16 | Magunden-Springville No,1 & No.2 Tower Replacement | 35.361, -118.922 / 36.108, -118.938 | City of Porterville in Tulare County | Mitigate tower steel corrosion on the Magunden-Springville 230 kV lines Nos. 1 and 2 and G.O. 95 clearance infractions due to rising of water levels at Lake Success. | •Remove approximately 14 existing 220 kV lattice structures from the existing ROW, •Install approximately 9 new hybrid (concrete/steel) H-frame structures, 4 tall new hybrid structures and 1 new dead-end lattice structure in the existing ROW. | New | None | Infrastructure Replacement | Age/Condition - Replace Steel Poles | 2019 | ~100 years | Inspection | • Remove 16 existing lattice structures, install 15 new structures (LST and TSP), create an embankment (Berm) approximately 6,500 feet in length and 200 feet in width (top of the embankment). Cost $47.3M • Remove 16 existing lattice structures, install 13 new structures (LST and TSP), create an embankment (Berm) approximately 6,000 feet in length and 200 feet in width (top of the embankment). Cost $48.6M • Remove 16 existing lattice structures, install 18 new structures (LST and TSP), create an embankment (Berm) approximately 8,500 feet in length and 200 feet in width (top of the embankment) $79.4 M • Completely reroute the transmission line alignment from the current ROW to a new ROW around the lake area, remove 17 existing structures from their existing ROW and install 20 to 30 new structures in the new ROW. Cost $48.7M • Completely underground the transmission line for approximately 2 miles in the impacted area of the Lake. Cost >$100M | Tier 2 | See Note 16C | Flooding, Air Particulate Levels | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | 2 | See Note 20B | 220 kV | See Note 22A | See Note 23B | 3 separate WOs/ Elements | 2 separate CWBS | 7558 | See Note 27A | Yes | 2014 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2022 = 18,175 | Final Suppl EIR 2020 | EIR/EIS | Lower Tule River Irrigation Water District/USACE | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2021-09-03 | Yes | 2021-06-01 | 2022-02-25 | Multiple CEQA and NEPA agency coordination. | 27876 | 27876 | See Note 53A | 21224.6916 | 300 | 2750 | 0 | 0 | 0 | 0 | 3050 | 2564.3499 | 702.52 | 1089.3934 | 9866.2269 | 3952.2013 | 18174.6916 | 3541.3181 | See Note 57A | N/A | See Note 59A | 1.7212e-13 | None | 100% | 0% | Column 42: CEQA needs to be completed before filing with the CPUC Column 52: Source= PMWIF (v0 Proj Summary); PIN level estimate
GIDAP/ TPP | SP-18 | Desert Harvest Generation Project (TOT486_Q643AE) | 33.672, -115.559 | Desert Center, Riverside County | Interconnect a 150 MW Solar Photovoltaic Generating Facility to SCE's Red Bluff 500/220kV Substation; terminate the Desert Harvest 220kV gentie line in a new line 220kV position at Red Bluff Substation; install telecommunications facilities to support line protection and SPS; install RTU at the Generating Facility and expand RTU at Red Bluff Substation; expand the Red Bluff SPS (loss of transformer bank); expand the Colorado River Corridor SPS (loss of 500kV lines); install TRV capacitors on four 500kV circuit breakers at Vincent Substation; install 2nd AA Bank at Red Bluff Substation. | ● Two (2) 230 kV circuit breakers ● Four (4) 230 kV disconnect switches ● Two (2) relays for protection ● Two (2) relays and associated equipment to add the project to the West of Colorado River CRAS ● Associated metering, telecom, & RTU | New, upgrade | SP-37, SP-03 | Work Requested by Others | GIDAP (Generation Interconnection) | N/A - New | N/A - New | ● Power Flow ● Transient ● Post Transient ● Short Circuit Duty | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Non-HFRA | See Note 16C | High Wind Events, Extreme Temperature Conditions | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | 75.7 | 230 kV | 220kV | See Note 23B | 901395606 | CET-ET-TP-RN-772900 | 7729 | See Note 27A | Yes | 2014 | 2017 | LGIA | 2014 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, under the CAISO Generation Interconnection Process | See Col. 37 | 2021= 3,485 2022 = 7 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2020-03-16 | No | 2016-08-01 | 2021-02-03 | Pending completion of transmission deliverability upgrades. | 9661 | 2673.844 | See Note 53A | 3491.848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.4062 | 1228.8454 | 2073.6956 | 151.9415 | 6.9593 | 3491.848 | 669.0414 | See Note 57A | 100% | See Note 59A | 2.5077e-13 | None | 100% | 0% | Column 9: GIDAP (Generator Interconnection) Column 38: Work expected to be exempt from GO 131-D licensing Column 52: Source= PMWIF (v4 Proj Summary); Represents PIN level estimate; WO level estimate from v4 Proj Summary $3.543M
TPP | SP-19 | Lugo-Victorville RAS | Various Locations | Boulder City, Clark County, Nevada | Install required facilities necessary to protect the jointly owned Lugo-Victorville 500 kV T/L following outage conditions within the SCE East of Pisgah (EOP) Area. RAS action to include the tripping of generation facilities within the EOP Area to mitigate against the overload of the Lugo-Victorville 500 kV T/L. | ● Lugo Sub-Install 2 N60 relays, 1 ethernet switch, 1 satellite switch, PSC point additions & test, install necessary telecom ● Pisgah Sub-Install new telecom room ● Gale Sub-Expand Gale Sub, install terminal equipment, install pre-fab bldg ● Eldorado Sub-Install 10 N60 relays, 1 ethernet switch, 1 satellite switch, PSC point additions & test, install necessary telecom ● Mohave Sub-Install 2 N60 relays, 1 ethernet switch, 1 satellite switch, PSC point additions & test ● Install OPGW between CA/NV border and Pisgah Substation. | New | None | Other - See Notes | Special Protection Scheme | N/A - New. Varies, but last inspections performed in between 2017 to 2019. | > 40 Years | ● Power Flow ● Transient ● Post Transient | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered since the affected transmission line would have had to be upgraded to remediate the thermal overload. Considering the affected facility was not within the CAISO balancing authority and the upgrade would have involved a physical upgrade such as a new transmission line, the RAS alternative was considered the least impactful that could have been completed in the required period of time. | Non-HFRA | See Note 16C | Extreme Temperature Conditions, Mountainous, Desert Region, Air Particulate Levels, High Wind Events | Brent Gokbudak, MPO-Project Development & Execution | See Note 19B | Lugo: 46 ac w/o transmission laydown yard Pisgah: 1.8 Gale: 1 Eldorado: 86.7 Mohave: 11.5 | 500 kV | 500kV | See Note 23B | 10 separate WOs/ Elements | 9 separate CWBS | 7763 | See Note 27A | Yes | 2013 | Pre-2017 | LGIA | 2013 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | See Col. 37 | 2016 = 1,084 2017 = 1,330 2018 = 14 2019 = 459 2021 = 2 2022 = 3 | Expected MND 2022 | MND | CDFW/BLM | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Construction more than 50% completed | See Note 46A | 2017-06-21 | No | 2016 | 2024-12-31 | Phase 2 is delayed due to CEQA/NEPA permitting delays. | 15455 | 11933.5689 | See Note 53A | 52781.6182 | 2566 | 21520.76 | 7628.72 | 0 | 0 | 0 | 31715.48 | 9055.2332 | 1040.3876 | 3154.4465 | 2465.2553 | 5350.8156 | 21066.1382 | 5939.6578 | See Note 57A | 100% | See Note 59A | 17285.303 | None | 100% | 0% | Column 9: Generator Interconnection Column 10:1. CAISO Transmission Planning Standards (Extreme Event); 2. NERC Compliance (P1.2 Event, Table 1 Item 2(b)) Column 52: Source= PMWIF (v3 Proj Summary);PIN level estimate FRM approval for revised estimate pending as of 11/30/22
GIDAP/ TPP | SP-21 | Colorado River Substation Upgrade (TOT446_Q576) | 33.589, -114.814 | Blythe, Riverside County | Interconnect a 224 MW Solar PV Generating Facility to SCE's Colorado River 220kV Substation; terminate the Blythe Mesa 220kV gentie line in a new 220kV line position at Colorado River Substation; install special protection system and telecommunications to support line protection and the special protection system; install RTU at the Generating Facility; install RTUs at Red Bluff substation; expand the RTU at Colorado River Substation. | ● Two (2) 230 kV circuit breakers ● Four (4) 230 kV disconnect switches ● Two (2) relays for protection ● Two (2) relays and associated equipment to add the project to the West of Colorado River CRAS ● Associated metering, telecom, & RTU | New, upgrade | SP-02, SP-03 | Work Requested by Others | GIDAP (Generation Interconnection) | N/A - New. Inspection of existing eq. varies, but last inspections performed in between 2017 to 2019. | N/A - New | ● Power Flow ● Transient ● Post Transient ● Short Circuit Duty | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Non-HFRA | See Note 16C | High Wind Events, Extreme Temperature Conditions | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | 77 | 230 kV | 220 kV | See Note 23B | 901713069 | CET-ET-CR-WC-786101 | 7861 | See Note 27A | Yes | 2015 | Pre-2017 | LGIA | 2015 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, under the CAISO Generation Interconnection Process | See Col. 37 | 2022 = 465 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2022-03-30 | Yes | 2022-08-01 | 2022-08-31 | Per Customer Requests and licensing | 8366 | 479.386 | See Note 53A | 464.5898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2187 | 11.6126 | 27.219 | 71.3355 | 349.2039 | 464.5898 | 107.5218 | See Note 57A | 100% | See Note 59A | 464.5898 | None | 100% | 0% | Column 9: GIDAP (Generator Interconnection) Column 38: Work expected to be exempt from GO 131-D licensing Column 52: Source= PMWIF (v2 Project Summary); Represents PIN level estimate; WO level estimate is $3.084M
TPP | SP-22 | Big Creek Corridor Rating Upgrade | Various Locations | Bakersfield, Kern County/ Richgrove, Tulare County | Increase ratings on the Magunden-Vestal and Rector-Vestal No.1 and 2 lines in the Big Creek area to its full capacity 4 hour emergency ratings of 1,520 Amps to eliminate load shed during low-hydro conditions for loss of a line. | Upgrade (6) 1200 Amp disconnects to match rating of the upgraded line (4 hour emergency rating of 1520 Amp). | New, Upgrade | PB-22.03, PB-22.04, PB-22.05, PB-22.06 | Other - See Notes | System Design Upgrade | SCE performs annual patrols and triennial detailed inspections of its transmission circuits, which inspect the structures and lines on those circuits. Last inspection for this circuit was in 2019. Last inspection in Magunden Sub in 2019 | N/A - specific asset age not readily available | Power Flow, Transient, Post Transient, Short Circuit Duty | Option 1: Build two new 220 kV transmission lines from Magunden to Rector. Cost $424-808 M. Option 2: Smart Wires Tower Routers. Cost $300 M. Option 3: Four (4) Phase Shifting Transformers. Cost $120 M. Option 4: Four (4) Thyristor Controlled Series Capacitors (TCSC) - including two (2) Shunt Capacitors. Cost $75 M. Option 5: Distributed Energy Resources (DER) - inadequate | Non-HFRA | See Note 16C | Seismic - Moderate | Brent Gokbudak, MPO-Project Development & Execution | See Note 19B | See Note 20B | See note 21A | 220KV | See Note 23B | 6 separate WOs | 6 separate CWBS | 7866 | See Note 27A | Yes | 2016 | Pre-2017 | Annual Capital Operating Plan Process | 2016 | 2016-2017 TPP to present | N/A | http://www.caiso.com/Documents/Board-Approved_2016-2017TransmissionPlan.pdf | See Col. 37 | 2018 = 167 2019 = 1,315 2020 = 2,754 2021 = 5 2022 = -2 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2019-10-09 | No | 2018-12-31 | 2020-01-31 | Planning and engineering delays | 4429 | 4429 | See Note 53A | 4239.7678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 949.1283 | 2595.7264 | 691.4314 | 5.2233 | -1.7416 | 4239.7678 | 379.1592 | See Note 57A | N/A | See Note 59A | 5.9771e-14 | None | 100% | 0% | Column 5: This project is separate and occurred after the TLRR program reconductored these four circuits with ACCC to help remediate clearance infractions Column 9: To eliminate load shed during low hydro conditions in order to continue to provide safe and reliable electrical service Column 38: Work expected to be exempt from GO 131-D licensing Column 52: Source= Unverified system estimate;Represents PIN level cost
N/A | SP-23 | Eldorado-Pisgah-Lugo TLRR Remediation | 35.798, -115.008 | San Bernardino County, City of Barstow, City of Apple Valley, City of Hesperia, City of Victorville, City of Adelanto, Clark County, Nevada, Boulder City, Nevada | Mitigate transmission line infractions required by GO 95 and NERC Facility Ratings as part of the TLRR Program. The TLRR Program is focused on developing and implementing engineering solutions for each identified discrepancies on its bulk electric system facilities by 2025. | To mitigate the discrepancies on the EPL lines, the proposed scope of work is as follows: The scope will include reconductoring 121 circuit miles with new ACCC conductor, install 12 inter-set structures and replacing existing insulators with shorter ones on 79 structures. | Reconductor | None | Other - See Notes | NERC Compliance - GO 95 | Inspections do not drive the need for TLRR projects. However, SCE performs annual patrols and triennial detailed inspections of its transmission circuits, which inspect the structures and lines on those circuits. The date of last inspection for this circuit was in 2019. | 30+ years | N/A -- Part of TLRR Program | A variety of alternatives were considered including do nothing; entire rebuild (replace lines and structures); removal of lines; inter-set or mid-span structure installation; full reconductor; partial reconductor; tower raising; derating of the lines; and shorter insulator replacement mitigation. | Tier 2 | See Note 16B | High Wind Events, Extreme Temperature Conditions, High Seismic Area, Desert Region | John Keelin, MPO - Project Dev. & Execution | Eldorado-Pisgah-Lugo No.1 & No.2 are each approximately 176 miles in length, for a total of approximately 352 miles. The scope will include reconductoring 163 circuit miles with new ACCC conductor and replacing existing insulators with shorter ones on 32 structures. | There is minimal substation work at Pisgah at one position and Cima with replacing conductor taps. | 220 kV | See Note 22A | See Note 23B | 10 separate Wos-add'l Wos will be created for other elements not previously identified and some will be canceled. | 6 separate CWBS | 7867 | See Note 27A | Yes | 2021 | Pre-2017 | FRM/CRT | No | N/A | N/A | N/A | Not Yet Operational | Not Yet Operational | PEA Completed 2023 | Anticipate MND/FONSI | CPUC/BLM | CPCN | 2023 | Filed and Under Review | 2023 | Planning | See Note 46A | 2026-01-26 | No | Work associated with the TLRR Program is scheduled to be completed by 1/1/2025 as part of compliance obligations. Dates are subject to change following final design, approval of project, and licensing. | 2027-11-03 | Delays associated with developing more comprehensive alternatives (wires and non-wires solutions) | 134728 | 70568 | See Note 53A | 230553.1852 | 2024.066 | 1136.001 | 31976.46 | 62275.692 | 54883.807 | 62329.155 | 214625.181 | 4605.6241 | 3439.6919 | 3442.1983 | 1846.539 | 2593.9508 | 15928.0042 | 4699.0785 | See Note 57A | N/A | See Note 59A | 12472.9126 | None | 100% | 0% | Column 9: Mitigate transmission line ground clearance infractions required by GO 95 and NERC Facility Ratings as part of the TLRR Program Column 38: As of Q2 2021 is in consultation with the CPUC to determine if the project is exempt from GO 131-D filing requirements Column 52: Source= Unverified system estimate;Represents PIN level cost
N/A | SP-24 | Cerritos Channel Tower Relocation | 33.767, -118.227 | Long Beach, Los Angeles County | The Port of Long Beach (POLB) requested SCE to relocate SCE facilities crossing the Cerritos Channel to accommodate a larger class of container ship in a letter from the Port on January 8, 2015. SCE’s relocation is related to the Gerald Desmond Bridge replacement being done by the POLB for the same purpose. Removed the existing 220 kV circuits crossing the Cerritos Channel. Phase 2: Demolition/removal of two, underwater foundations in Cerritos Channel. | Transmission: Harborgen-Long Beach 220kV: Remove Harborgen- Long Beach 220kV line approximately 0.977 Miles of 650 KCM Calson Bronze conductor. Remove abandoned structures and foundations (Foundations are only required to be removed near Pier S - Phase 2). Remove a portion of the Lighthipe-Long Beach 220kV (from Harborgen to Long Beach), reconfigure the Lighthipe-Long Beach to create the Harborgen-Lighthipe 220kV. Substation: Adjust relays at Harborgen and Lighthipe to accommodate the revised line configuration. Remove existing structures and equipment in the Long Beach 220kV switchyard, remove relays and controls from the MEER associated with the equipment in the switchyard being removed. | Removal, reconfiguration | None | Work requested by others | Facility Relocation | SCE performs annual patrols and triennial detailed inspections of its transmission circuits, which inspect the structures and lines on those circuits. Last inspections for the majority of these lines happened in 2019. | > 30 Years | ● Power Flow ● Transient ● Post Transient ● Short Circuit Duty | Relocation | Non-HFRA | See Note 16C | High Wind Events, Flooding, Tsunami, Salt Corrosion (Coastal Areas) | John Keelin, MPO - Project Dev. & Execution | 1 | 2.25 (Long Beach 220 kV yard) | 220 kV | See Note 22A | See Note 23B | 6 separate WOs/ Elements | 6 separate CWBS | 7884 | See Note 27A | Yes | 2016 | Pre-2017 | FRM/CRT | No | N/A | N/A | N/A | See Col. 37 | 2018 = 4,811 2019 = 919 2020 = 6,963 2021 = 2,514 | CEQA Final Certified 2017 | EIR/EA | Port of Long Beach/USACE | PTC A.18-08-002 | 2018 | Approved | 2018 | Construction more than 50% completed | See Note 46A | 2018-11-14 | No | 2019-01-01 | 2026-08-24 | Phase 1: Project was delayed due to more challenging geotechnical conditions than expected, which impacted foundation designs. Phase 2: Project bids/construction delayed due to third party pipelines conflicting with SCE foundations. Waiting for Port of Long Beach discussion with third party utilities. | 151550 | 55217.651 | See Note 53A | 58163.5518 | 99.2755 | 250 | 12860.2035 | 12860.2035 | 6431.5975 | 9921.938 | 42423.218 | 7841.2984 | 1540.0735 | 4216.5719 | 1801.8985 | 340.4916 | 15740.3338 | 1501.5152 | See Note 57A | 100% | See Note 59A | 6.1233e-13 | None | 100% | 0% | Column 21: Project also includes 115kV relocation work which is CPUC-jurisdictional. As the 115KV work is out of scope for this report and not FERC-jurisdictional, it is not included. Column 52: Source= FRM (10/31/2018);Represents total project cost estimate
N/A | SP-25 | Ivanpah-Control TLRR Remediation | Various Locations | San Bernardino County, City of Barstow, City of Apple Valley, City of Hesperia, City of Victorville, City of Adelanto, Clark County, Nevada, Boulder City, Nevada | Mitigate transmission line infractions required by GO 95 and NERC Facility Ratings as part of the TLRR Program. The TLRR Program is focused on developing and implementing engineering solutions for each identified discrepancies on its bulk electric system facilities by 2025 | Proposed scope of work being finalized; See Ivanpah-Control PEA for additional information: (https://www.cpuc.ca.gov/Environment/info/aspen/ivanpah-control/toc-pea.htm); Transmission lines | Modification/Upgrade | None | Other - See Notes | NERC Compliance - GO 95 | SCE performs annual patrols and triennial detailed inspections of its transmission circuits, which inspect the structures and lines on those circuits. Last inspections for the majority of these lines happened in 2019. | Various (2013, 1977, 2010) | N/A -- Part of TLRR Program | A variety of alternatives were considered including do nothing, full rebuild, removing the lines, inter-sets, reconductor, tower raising, derating and other system alternatives. | Tier 2 | See Note 16B | High Wind Events, Extreme Temperature Conditions | John Keelin, MPO - Project Dev. & Execution | 358 | This project does not include any specific substation modifications. However, minor changes associated with mitigating the clearance infractions (e.g. changing relay settings) will be required, but are not yet determined as the scoping work is still in progress. | 115 | See Note 22A | See Note 23B | 14 separate WOs / Elements | 13 separate CWBS | 7904 | See Note 27A | Approval to file PTC | 2019 | Pre-2017 | FRM/CRT | No | N/A | N/A | N/A | See Col. 37 | Not Yet Operational | Expected DEIR 2023 | EIR/EIS | CPUC/BLM | PTC A.19-07-015 | 2019 | Filed and Under Review | 2019 | Planning | See Note 46A | 2027-02-04 | No | Work associated with the TLRR Program is scheduled to be completed by 1/1/2025 as part of compliance obligations. Dates are subject to change following final design, approval of project, and licensing. | 2030-08-02 | The BLM has requested the project to provide the Archeological Evaluation Report (AER) prior to the issuance of the determination of eligibility. There has been a delay in developing the AER due to the significant amount of archeological field work testing and review process. | 213750 | 211429.1837 | See Note 53A | 695728.4763 | 3243.336 | 3100 | 5112.578 | 42439.1766 | 124759.0976 | 472142.4454 | 650796.6336 | 9188.0908 | 8500.2178 | 12780.0269 | 7311.6455 | 7151.8618 | 44931.8427 | 12571.8467 | See Note 57A | N/A | See Note 59A | 43152.64 | None | 0% | 100% | Column 9: Mitigate transmission line ground clearance infractions required by GO 95 and NERC Facility Ratings as part of the TLRR Program Column 52: Source= Unverified system estimate; Represents PIN level cost
N/A | SP-26 | Control-Silver Peak TLRR Remediation | 37.336, -118.481 | San Bernardino County, City of Barstow, City of Apple Valley, City of Hesperia, City of Victorville, City of Adelanto, Clark County, Nevada, Boulder City, Nevada | Mitigate transmission line infractions required by GO 95 and NERC Facility Ratings as part of the TLRR Program. The TLRR Program is focused on developing and implementing engineering solutions for each identified discrepancies on its bulk electric system facilities by 2025 | Rebuild existing sub-transmission circuit, replacing lattice, wood, H-Frames and tubular steel poles with steel poles (light weight steel and tubular steel poles). | Modification/Upgrade | PB-22.60, PB-22.61 | Other - See Notes | NERC Compliance - GO 95 | SCE performs annual patrols and triennial detailed inspections of its transmission circuits, which inspect the structures and lines on those circuits. Last inspections for the majority of these lines happened in 2019. | 70 | N/A -- Part of TLRR Program | Alternatives work is complete | Tier 2, Zone 1 | See Note 16B | High Wind Events, High Fire Risk Area, Extreme Temperature Conditions, Mudslide | John Keelin, MPO - Project Dev. & Execution | 58 | This project does not include any specific substation modifications. However, minor changes associated with mitigating the clearance infractions (e.g. changing relay settings) will be required, but are not yet determined as the scoping work is still in progress. | 55 | See Note 22A | See Note 23B | 7 separate WOs / Elements | 4 separate CWBS | 7906 | See Note 27A | Development Funds Only | 2016 | Pre-2017 | FRM/CRT | No | N/A | N/A | N/A | Not Yet Operational | Not Yet Operational | Expected DEIR 2024 | EIR/EIS | CPUC/BLM | PTC Expected | 2021 | Filed and Under Review | 2021 | Planning | See Note 46A | 2026-04-29 | No | Work associated with the TLRR Program is scheduled to be completed by 1/1/2025 as part of compliance obligations. Dates are subject to change following final design, approval of project, and licensing. | 2029-04-30 | The project incurred delays due to the larger amount of data requests and deficiencies identified by the CPUC, than what was originally anticipated, after SCE submitted the Permit to Construct Application. | 58750 | 58750 | See Note 53A | 253222.3191 | 1555 | 1500 | 37230.545 | 42170.769 | 42364.986 | 110782.226 | 235603.526 | 5203.6611 | 4531.2193 | 2138.5137 | 2508.7146 | 3236.6844 | 17618.7931 | 4997.303 | See Note 57A | N/A | See Note 59A | 16178.2141 | None | 0% | 100% | Column 9: Mitigate transmission line ground clearance infractions required by GO 95 and NERC Facility Ratings as part of the TLRR Program Column 52: Source= PMWIF (v2 Proj Summary); Represents PIN level estimate
N/A | SP-27 | Devers Substation Facility Upgrade | 33.935, -116.578 | North Palm Springs, Riverside County | This project will retrofit the existing maintenance and test facility. This will address current facility conditions and issues, and accommodate accessible kitchen and restroom facilities for male and female employees, add accessible parking stalls, etc. | Facility Upgrade | Upgrade | None | Other - See Notes | Age/Condition | 2019-10-28 | ~55 Years (Built in 1975) | Temporary City Permit for Crews working in Trailers | 1) New Construction ($10.5M) 2) Do Nothing (<$1M immediate capital repair costs, ongoing O&M) | Non-HFRA | See Note 16C | No specific factors outside of very extreme weather and environmental events that could compromise the integrity of the structure. | Randy White, Corporate Security | See Note 19B | Site: 0.254; Building: 0.135 | See note 21A | Though this project does not impact capacity, the substation is 500 kV | See Note 23B | 801432305 | COS-00-RE-AD-SR0004 | 7957 | See Note 27A | Yes | 2018 | 2018 | FRM/CRT | No | N/A | N/A | N/A | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Construction less than 50% completed | See Note 46A | 2019-11-04 | Yes | 2019-03-03 | 2023-06-01 | Additional time required to perform more granular facility design and cost estimation. Vendor had safety issue. New construction contract necessary. | 4300 | 3526 | See Note 53A | 9253.1415 | 802.3865 | 0 | 0 | 0 | 0 | 0 | 802.3865 | 332.4555 | 967.0643 | 1661.1725 | 1249.5176 | 4240.5451 | 8450.755 | 1405.9906 | See Note 57A | N/A | SCE performed a Present Value Revenue Requirement analysis for the proposed and alternative options considered. | 8381.675 | None | 100% | 0% | Column 9: Asset Condition Column 23: SCE utilized Facility Condition Index analysis to evaluate Maintenance and Test facilities, including this facility, to prioritize facility work. In addition, SCE also considered compliance with local jurisdictions and regulations and opportunities for operational improvements. Column 52: Source= FRM (03/27/2018); Represents total project cost approved by FRM
N/A | SP-28 | Rector Substation Facility Upgrade | 36.304, -119.244 | Visalia, Tulare County | This project will construct a new maintenance and test facility. This will satisfy the requirement to remove temporary facilities, address facility conditions and issues, and improve site efficiencies. | Facility New Construction | New | None | Other - See Notes | Age/Condition | 2019-09-11 | N/A - This is a new construction project | Temporary City Permit for Crews working in Trailers | 1) Remodel w/Expansion ($12.6M) 2) Do Nothing (<$1M immediate capital repair costs, ongoing O&M) | Non-HFRA | See Note 16C | No specific factors outside of very extreme weather and environmental events that could compromise the integrity of the structure. | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | Site: 5.79; Building: 0.363 | See note 21A | Though this project does not impact capacity, the substation is 220 kV | See Note 23B | 801432582 | COS-00-RE-AD-SR0006 | 7959 | See Note 27A | Yes | 2018 | 2018 | FRM/CRT | No | N/A | N/A | N/A | See Col. 37 | 2020 = 8,432 2021 = 98 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2019-09-11 | No | 2019-02-24 | 2020-07-29 | Additional value engineering and procurement strategies to seek reduced cost estimates. | 11100 | 6438 | See Note 53A | 8529.6018 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 0 | 441.0123 | 2640.665 | 5349.9579 | 97.9665 | 0 | 8529.6018 | 775.1902 | See Note 57A | N/A | SCE performed a Present Value Revenue Requirement analysis for the proposed and alternative options considered. | -2.9796e-12 | None | 100% | 0% | Column 9: Compliance Column 23: SCE utilized Facility Condition Index analysis to evaluate Maintenance and Test facilities, including this facility, to prioritize facility work. In addition, SCE also considered compliance with local jurisdictions and regulations and opportunities for operational improvements Column 52: Source= FRM (03/27/2018); Represents total project cost approved by FRM. SCE notes that it previously provided a data request response indicating a project cost of $7.7M which represents the FERC portion of costs from SCE's GRC; however, consistent with the updated methodology for the July 2021 SRP, SCE has provided the original approved costs from FRM.
N/A | SP-29 | Northern CRAS to Tehachapi CRAS | Various Locations | Project area spans portions of Los Angeles and Kern Counties; bounded by cities of Palmdale to the south and Tehachapi to the north. | Implement in SCE's Centralized Remedial Action Scheme (CRAS) platform a special protection system to accommodate generation in the Tehachapi Area. Monitors for outages of 500 kV transmission lines linking Whirlwind, Antelope, and Vincent Substations and trips generation at Antelope and Whirlwind Substations. Project is scalable and will evolve as needed to include future generation projects at Highwind, Windhub and other points of interconnection along the Tehachapi transmission corridor. This is a protection/IT project consisting of protective relays, telecom network circuits and terminal equipment, and central processing architecture at GCC and IOC. Protects 500 kV transmission lines from overloads caused by existing and future generation connected to the SCE grid at Antelope, Highwind, Whirlwind, and Windhub Substations, but is scalable to include interconnections at other locations and voltage levels. | Multiple relays for line outage monitoring and generator tripping; telecom circuits and terminal equipment | New | PB-07.01, PB-11.01, PB-11.03, PB-11.07, PB-16.04, PB-16.17, PB-16.18, PB-18.01, PB-18.11, PB-18.12, PB-19.01, PB-19.06, SP-29, SP-38, SP-45, SP-52, SP-53, SP-58, SP-59, SP-60, SP-61, SP-74, SP-75, SP-76, SP-77, SP-78, SP-79, SP-80, SP-81, SP-84, SP-85, SP-94, SP-95, SP-97, SP-107 | Other - See Notes | Special Protection Scheme | N/A - New. Varies, but last inspections performed in between 2017 to 2019. | Various | Load Flow, Dynamic Stability | No alts - modernize RAS telecom infrastructure in compliance with WECC criteria | Non-HFRA | See Note 16C | High Wind Events, Extreme Temperature Conditions, High Seismic Area | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | Whirlwind: 92 Vincent: 55 Antelope: 73 Windhub: 62 | See note 21A | 500 kV, 220KV | See Note 23B | 7 separate WOs | 4 separate CWBS | 8009 | See Note 27A | Yes | 2017 | 2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2020 = 7,722 2021 = 4 2022 = -213 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2019-04-01 | No | 2018-12-31 | 2020-09-23 | Delays due to additional scope and testing facilities required. | 31800 | 31800 | See Note 53A | 7513.0793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2114.8559 | 4049.4167 | 1557.7948 | 4.0164 | -213.0045 | 7513.0793 | 2265.8633 | See Note 57A | 100% | See Note 59A | -4.0642e-12 | None | 100% | 0% | Column 9: Generator Interconnection Column 52: Source= FRM (09/21/2020); Represents total project cost approved by FRM; PIN level estimate from PMWIF (v2 Proj Summary $23.587M
TPP | SP-30 | Lugo Substation Upgrade | 34.367, -117.369 / 34.535, -117.295 | Hesperia, San Bernardino County | Thermal Overloads on Lugo - Victorville 500 kV Transmission Line during N-2 loss of either Eldorado – Lugo 500 kV with Eldorado –Mohave 500 kV (Category C) or Eldorado – Lugo 500 kV with Lugo –Mohave 500 kV. | Lugo Substation: Replace (3) 500kV CBs (CB#762, 862, 962), (6) 500kV disconnects (#761, 763, 861, 863, 961, 963), terminal equipment and line drop at position 6, conductor on CB #862, legs on CB #762, 862, & 962, and 500kV wavetrap. Upgrade SCE's portion of the Lugo-Victorville 500 kV transmission line, by increasing the ground clearance to increase the thermal rating of the line. | Replace / Upgrade | None | Infrastructure Replacement | Age/Condition - Replace Breakers | SCE performs annual patrols and triennial detailed inspections of its transmission circuits, which inspect the structures and lines on those circuits. Last inspections for the majority of these lines happened in 2019. | > 40 Years | Power Flow | See page F-4 of Appendix F 2016-2017TransmissionPlan | Tier 2 | See Note 16C | High Wind Events, Extreme Temperature Conditions, Air Particulate Levels, High Seismic Area, Desert Region | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | See Note 20B | 500 kV | 500kV | See Note 23B | 2 separate WOs | 2 separate CWBS | 8029 | See Note 27A | Yes | 2017 | Pre-2017 | Annual Capital Operating Plan Process | 2017 | 2015-2016 TPP to present | N/A | Page 379 of 2016-2017 TPP | See Col. 37 | 2019 = 1,200 2020 = 21 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Engineering more than 50% Completed | See Note 46A | 2019-01-02 | No | 2018-12-31 | 2027-01-31 | Project coordination with LADWP. | 16079 | 16063.4385 | See Note 53A | 10759.8714 | 400 | 5337 | 587 | 0 | 0 | 0 | 6324 | 270.2339 | 976.3299 | 1236.6447 | 1846.3445 | 106.3184 | 4435.8714 | 514.7061 | See Note 57A | N/A | See Note 59A | 3071.1888 | None | 100% | 0% | Column 9:Address results of Power Flow Analysis - Mitigate identified thermal overloads Column 38: Work expected to be exempt from GO 131-D licensing Column 52: Source= PMWIF (v1 Proj Summary); Represents PIN level estimate; WO level estimate $14.186M
N/A | SP-32 | Substation Protection Upgrades - San Joaquin Region | Various Locations | Bakersfield, Kern County | Magunden 220 kV: Install four (4) new Bus Differential Relay Racks Install a second set of BCTs for Bus Differential Protection on fifteen (15) 220 kV Circuit Breakers. This is to comply with NERC TPL-001-4 to mitigate for the TPL violations and persistent faults identified as part of ATRA 2016. | Relay Protection | New | None | Other - See Notes | NERC CIP Compliance | Various, last inspection performed in 2019 | Magunden Substation: 80-90 years | Dynamic Analysis | None - Addresses protection issues subject to NERC compliance | Non-HFRA | See Note 16C | Multiple Substation Locations | Demetric Brown, MPO - Programs | See Note 19B | Magunden: 15.3 (excluding laydown yard) | See note 21A | 220KV | See Note 23B | 11 separate WOs | 11 separate CWBS | 8077 | See Note 27A | Yes | 2018 | 2018 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2020 = 2,172 2021 = 3,791 2022 = -18 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Engineering more than 50% Completed | See Note 46A | 2020-03-02 | No | Various substations. 8/31/2020 | 2025-09-26 | Varies WOs with multiple in-service dates | 26562 | 25506.5219 | See Note 53A | 40715.3919 | 1106.433 | 1414.9085 | 18009.119 | 0 | 0 | 0 | 20530.4605 | 14.5335 | 1775.6996 | 5275.0302 | 5169.545 | 7950.1231 | 20184.9314 | 3562.3161 | See Note 57A | N/A | See Note 59A | 13935.1319 | None | 100% | 0% | Column 9: To meet SCE reliability criteria and provide operational flexibility Column 38: Work expected to be exempt from GO 131-D licensing Column 51: Made up of several work orders that have various in-service dates. No significant delays in project in-service. Represents in-service for all WOs. Column 52: Source= PMWIF (v1 Proj Summary); Represents PIN level estimate as a summation of 5 separate PWMIFs; WO level estimate $24.507M as aggregation of relevant WOs
GIDAP/ TPP | SP-33 | Arlington Solar Project (TOT781_Q1196) | 33.589, -114.814 | Blythe, Riverside County | Interconnect a 400 MW Solar PV Generating Facility to SCE's Colorado River 500/220kV Substation; terminate the Colorado River-Sun Catcher 220kV Transmission Line in a new 220kV line position at Colorado River Substation; install telecommunications facilities to support line protection and RAS; install RTU at the Generating Facility and expand RTU at Colorado River Substation; add project to the Colorado River Corridor RAS. | ● Two (2) 230 kV circuit breakers ● Four (4) 230 kV disconnect switches ● Two (2) relays for protection ● Two (2) relays and associated equipment to add the project to the West of Colorado River CRAS ● Associated metering, telecom, & RTU | New, upgrade | SP-02, SP-03 | Work Requested by Others | GIDAP (Generation Interconnection) | N/A | N/A - New. Existing since 2013 | ● Power Flow ● Transient ● Post Transient ● Short Circuit Duty | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Non-HFRA | See Note 16C | High Wind Events, Extreme Temperature Conditions | Demetric Brown, MPO - Programs | <1 mile | 77 | 220 kv | 220 kV | See Note 23B | 3 separate WOs | 3 separate CWBS | 8081 | See Note 27A | Yes | 2017 | 2017 | Annual Capital Operating Plan Process | 2017 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, under the CAISO Generation Interconnection Process | See Col. 37 | 2021 = 3,523 2022 = 55 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2020-02-10 | No | 2020-12-01 | 2021-12-02 | Customer late on deliverables | 8137 | 1687.2702 | See Note 53A | 3581.842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.9926 | 721.8609 | 2026.6731 | 744.3637 | 54.9516 | 3581.842 | 737.5637 | See Note 57A | 100% | See Note 59A | -7.7506e-13 | None | 100% | 0% | Column 9: GIDAP (Generator Interconnection) Column 38: Work expected to be exempt from GO 131-D licensing. Column 52: Source= PMWIF (v1 Proj Summary); Represents PIN level estimate
TPP | SP-34 | Harry Allen-Eldorado Termination Project | 35.798084, -115.006503 | Boulder City, Clark County, Nevada | Install terminal equipment to terminate the Harry Allen-Eldorado Transmission Line | Install two (2) 4000A, 63kA, 500 kV circuit breakers Four (4) 4000A, horizontally mounted disconnect switches, 100 MVAR shunt line reactor with one (1) 4000A, 500 kV disconnect switch, and one (1) 3000 A, 500 kV, synchronous circuit breaker and foundation. | New | None | Work requested by others | Substation Reliability | N/A - New | N/A - New | CAISO analysis | N/A | Non-HFRA | See Note 16C | High Wind Events, Air Particulate Levels, Desert Region, Extreme Temperature Conditions | Demetric Brown, MPO - Programs | See Note 19B | Eldorado Sub: 86.7 (SCE does not own Harry Allen Sub) | 500kV | 500kV | See Note 23B | 2 separate Wos | 2 separate CWBS | 8088 | See Note 27A | Yes | 2015 | Pre-2017 | FRM/CRT | 2014 | 2012-2013 TPP to present | N/A | Multiple URL (copy/paste in your web browser): http://www.caiso.com/Documents/BoardApproved2012-2013TransmissionPlan.pdf (project consideration) https://www.caiso.com/Documents/HarryAllen-EldoradoProjectAnalysisReport_AppendixA.pdf (approval) | See Col. 37 | 2020 = 21,530 2021 = 263 2022 = 29 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2019-09-03 | No | 2020-05-01 | 2020-08-13 | N/A | 25300 | 24860.5109 | See Note 53A | 21822.0306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 507.3918 | 7230.182 | 13792.8417 | 262.99 | 28.625 | 21822.0306 | 2150.5702 | See Note 57A | 100% | See Note 59A (SCE portion not subject to Cost-Benefit Analysis) | -2.5182e-11 | None | 100% | 0% | Column 38: Work expected to be exempt from GO 131-D licensing. Column 52: Source= FRM (11/29/2016); Represents total project cost approved by FRM (earlier CRT available for a modified project scope); PIN level estimate from PMWIF $17.6M
GIDAP/ TPP | SP-35 | Sienna Solar Farm Project (TOT761_Q1207) | 34.547, -116.952 | Lucerne Valley, San Bernardino County | Interconnect a 200 MW Solar Photovoltaic Generating Facility to SCE's Calcite 230 kV Substation; terminate the Calcite-Sienna 230 kV gentie line in a new line 230 kV position at Calcite Substation; install telecommunications facilities to support line protection and RAS; install RTU at the Generating Facility; expand the Calcite RAS to include the project; expand the HDPP RAS to include the project. | ● Two (2) 230 kV circuit breakers ● Four (4) 230 kV disconnect switches ● Two (2) relays for protection ● Four (4) relays and associated equipment to add the project to the HDPP RAS ● Associated metering, telecom, & RTU | New, upgrade | SP-01 | Work Requested by Others | GIDAP (Generation Interconnection) | N/A - New | N/A - New | ● Power Flow ● Transient ● Post Transient ● Short Circuit Duty | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Non-HFRA | See Note 16C | High Wind Events, Extreme Temperature Conditions, Air Particulate Levels, Desert Region | Brent Gokbudak, MPO-Project Development & Execution | See Note 19B | ~10 | 230 kV | 220 kV | See Note 23B | 902310803 | CET-ET-CR-WC-809800 | 8098 | See Note 27A | Yes | 2017 | 2017 | LGIA | 2017 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, under the CAISO Generation Interconnection Process | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Planning | See Note 46A | 2026-01-05 | No | 2021-03-04 | 2027-03-30 | Coordination with other customer projects | 10041 | Not readily available | See Note 53A | 1.3323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84163 | 0.49065 | 0 | 1.3323 | 0.53894 | See Note 57A | 100% | See Note 59A | 1.3323 | None | 100% | 0% | Column 9: GIDAP (Generator Interconnection) Column 52: Source= PMWIF (v0 Proj Summary); Represents PIN level estimate; WO level estimate $3.244M Column 52.1: FERC % not yet available in source file; will be updated in future SRP once available
TPP | SP-36 | Moorpark-Pardee Circuit Install | 34.281, -118.903 / 34.440, -118.582 | Los Angeles & Ventura Counties | Install a fourth Moorpark-Pardee 230 kV circuit on existing structures in SCE's transmission right-of-way. | Transmission line (new), Substation (breakers, protection) | New, upgrade | None | Other - See Notes | New T-Line | N/A - New. Last inspections performed at these location between 2017 and 2019. | New | CAISO Local Capacity Technical Studies (load flow, post-transient) | Page 193 of 2017-2018 ISO TP | Tier 3 | See Note 16C | High Wind Events, High Seismic Area, High Fire Risk Area | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | 26 | Pardee: 29.4 Moorpark: 38.8 | 220 kV | 220 kV | See Note 23B | 6 separate WOs | 6 separate CWBS | 8104 | See Note 27A | Yes | 2019 | 2019 | FRM/CRT | 2018 | 2017-2018 TPP to present | N/A | Page 334 of 2017-2018 ISO TP | See Col. 37 | 2020 = 2,023 2021 = 12,348 2022 = 51,640 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2019-08-05 | Yes | 2020-12-31 | 2022-05-18 | Scope Increase | 35200 | 31724.8906 | See Note 53A | 66011.404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199.0189 | 18404.3062 | 28635.0822 | 16922.9533 | 1850.0434 | 66011.404 | 11837.0735 | See Note 57A | N/A | See Note 59A | 2.3239e-11 | None | 100% | 0% | Column 9: CAISO Local Capacity Criteria - Address a generation capacity deficiency that can cause voltage collapse in the Moorpark local capacity subarea. Column 51: Planned in-service date for this project was input to open the Work Order. The project had no significant delays. Column 52: Source= FRM (01/04/2019); Represents total project cost approved by FRM; PIN level estimate from PMWIF $47.104M
GIDAP/ TPP | SP-37 | Red Bluff Substation Transformer Bank Install (TOT486_Q643AE) | 33.672, -115.559 | Desert Center, Riverside County | Install the second AA 500/230 kV transformer bank at Red Bluff Substation. This will also require the need to modify the existing Special Protection System to trip generation under an N-1 of one transformer bank. | Transformer Bank | New, upgrade | SP-37, SP-03 | Work Requested by Others | GIDAP (Generation Interconnection) | N/A - New Asset. Last inspection performed 2019. | N/A - New Asset. Red Bluff Substation constructed in 2013 | ● Power Flow ● Transient ● Post Transient ● Short Circuit Duty | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Non-HFRA | See Note 16C | High Wind Events, Extreme Temperature Conditions | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | 75.7 | 500 kV & 230 kV | 500kV - 220kV, 1120 MVA | See Note 23B | 2 separate WOs | 1 CWBS | 8163 | See Note 27A | Yes | 2015 | Pre-2017 | FRM/CRT | 2014 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, under the CAISO Generation Interconnection Process | See Col.37 | 2022 = 24,145 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2021-02-05 | Yes | 2021-10-08 | 2022-04-25 | Project progress is contingent upon development of generation projects on the Red Bluff 230 kV Bus | 59000 | 59000 | See Note 53A | 24144.8712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.5691 | 127.2172 | 4681.0566 | 16800.9065 | 2525.1218 | 24144.8712 | 3464.2257 | See Note 57A | 100% | See Note 59A | 3.3193e-11 | None | 100% | 0% | Column 9: GIDAP (Generator Interconnection) Column 38: Work expected to be exempt from GO 131-D licensing. Column 52: Source= FRM (03/31/2015); Represents total project cost estimate approved by FRM; PWMIF (v0 Project Summary) PIN level estimate $26.638M Network Upgrades Project scope does not include the material cost of the second 500/220 kV 'AA' transformer bank at Red Bluff Substation and the lack of transformer cost is reflected in both Original Projected Cost (See Col. 51) and Current Projected Cost (Col. 53)
GIDAP | SP-38 | Lone Butte Substation Interconnect (TOT819_Q1324) | 35.035, -118.281 | Mojave, CA | To interconnect the Terra Gen's solar photovoltaic Sagebrush Solar 3 generating facility in Mojave, California with SCE's transmission system. | New/Interconnection | New/Interconnection | None | Work Requested by Others | GIDAP (Generation Interconnection) | N/A | N/A | System Impact Study; Facility Study | N/A | Non-HFRA | See Note 16C | High Wind Events, Extreme Temperature Conditions, High Seismic | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | See Note 20B | 220 kV | 300 MW; 220 kV | See Note 23B | 2 separate WOs | 2 separate CWBS | 8199 | See Note 27A | Yes | 2018 | 2018 | LGIA | 2018 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, under the CAISO Generation Interconnection Process | See Col. 37 | 2021 = 261 2022 = 28 | TBD | TBD | TBD | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2021-05-03 | Yes | 2022-03-01 | 2022-03-01 | Per Customer Requested Expedited Dates | 8095 | 464.2563 | See Note 53A | 414.0704 | 15 | 50 | 60 | 0 | 0 | 0 | 125 | 0 | 29.8775 | 81.2761 | 149.9275 | 27.9893 | 289.0704 | 92.7674 | See Note 57A | 100% | See Note 59A | -8.2252e-14 | None | 100% | 0% | Column 9: GIDAP (Generator Interconnection) Column 52: Source= PMWIF (v0 Proj Summary); Represents PIN level estimate; WO level estimate $3.407M
GIDAP/ TPP | SP-39 | Red Bluff Substation Interconnect (TOT349_Q421) | 33.672, -115.559 | Riverside County, CA | To interconnect the NRG Solar Desert Center's Sloth generating facilities with SCE's Red Bluff 220 kV substation 220 kV switchrack. | New/Interconnection | New /Interconnection | SP-44 | Work Requested by Others | GIDAP (Generation Interconnection) | N/A | N/A | System Impact Study; Facility Study | N/A | Non-HFRA | See Note 16C | High Wind Events, Extreme Temperature Conditions | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | 75.7 | 220 kV | 220 kV | See Note 23B | 902494149 | CET-ET-TP-RN-707300 | 7073 | See Note 27A | Yes | 2017 | 2017 | LGIA | 2008 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, under the CAISO Generation Interconnection Process | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Canceled | See Note 46A | 2023-12-04 | No | 2021-05-01 | Canceled | Better Scope Refinement | 8871 | 6278.0505 | See Note 53A | 613.8741 | 182.172 | 27.727 | 393.944 | 0 | 0 | 0 | 603.843 | 0.64162 | 1.2491 | 3.1261 | 1.6849 | 3.3293 | 10.0311 | 3.5571 | See Note 57A | 100% | See Note 59A | 10.0311 | None | 100% | 0% | Column 9: GIDAP (Generator Interconnection) Column 52: Source= PMWIF (v7 Proj Summary); Represents PIN level estimates; WO level estimate $3.717M
GIDAP/ TPP | SP-40 | WDAT315 - Casa Diablo 4 - Casa Diablo (D) Install interconnection facilities | 37.649, -118.917 | Mammoth Lakes, CA | To interconnect the Mammoth Pacific's generating facilities with SCE's distribution system at Casa Diablo 33kV substation at the 33kV bus. | Interconnection | New /Interconnection | None | Work Requested by Others | GIDAP (Generation Interconnection) | N/A | N/A | System Impact Study; Facility Study | Plant Site Alternative Modified Pipeline Alternative | Tier 2 | See Note 16C | High Wind Events, High Fire Risk Area, Extreme Temperature Conditions, Mudslide | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | 2.4 | 33 kV | 40.7 MW; 115 kV | See Note 23B | 2 separate WOs | 2 separate CWBS | 7227 | See Note 27A | Yes | 2017 | 2017 | LGIA | 2017 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, under the CAISO Generation Interconnection Process | See Col.37 | 2021 = 7,100 2022 = 996 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Pre-Construction | See Note 46A | 2021-01-21 | Yes | 2020-02-01 | 2023-12-22 | Permitting and Weather Conditions | 30177 | 12867.4928 | See Note 53A | 8227.0979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.5567 | 220.466 | 3283.7211 | 3621.6195 | 1034.7347 | 8227.0979 | 1189.0313 | See Note 57A | 100% | See Note 59A | 7226.2427 | None | 0% | 100% | Column 9: GIDAP (Generator Interconnection) Column 52: Source= PMWIF (v0 Proj Summary); PIN level estimate
GIDAP/ TPP | SP-41 | Kramer Substation Interconnect (TOT773_Q1204) | 34.989, -117.543 | Kramer Junction, San Bernardino County | Kramer Substation (RNU): a. Engineer and construct one (1) 220 kV line position, which includes the following equipment: i. Two (2) 220 kV circuit breakers. ii. Three (3) 220 kV group operated disconnect switches. iii. One (1) 220 kV group operated disconnect switch with grounding attachment. iv. Fourteen (14) 220 kV post insulators. b. Protection Relays: G.E. C60 local breaker failure backup relays | Reliability Network Upgrade | New/Interconnection | None | Work Requested by Others | GIDAP (Generation Interconnection) | 05/20/2021 | N/A - New | Bank Capacity, Power Flow, Short Circuit Duty, dynamic stability, SCE Subtransmission Planning Criteria and Guidelines | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Non-HFRA | See Note 16C | Extreme Temperature Conditions, High Wind Events | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | 20.6 | See note 21A | 220 kV | See Note 23B | 902342409 | CET-ET-TP-RN-810701 | 8107 | See Note 27A | Yes | 2017 | 2017 | LGIA | 2017 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, under the CAISO Generation Interconnection Process | Not Yet Operational | Not Yet Operational | TBD | TBD | TBD | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Construction more than 50% completed | See Note 46A | 2022-07-05 | No | 2020-06-01 | 2024-10-31 | Agreement with the Customer | 7313 | 1885.0384 | See Note 53A | 3973.4811 | 437.944 | 40.955 | 0 | 50 | 0 | 0 | 528.899 | 15.2285 | 4.9906 | 44.4493 | 967.999 | 2411.9146 | 3444.5821 | 673.9396 | See Note 57A | 100% | See Note 59A | 3444.5821 | None | 100% | 0% | Column 9: GIDAP (Generator Interconnection) Column 52: Source= PMWIF (v0 Proj Summary); Represents PIN level estimate; WO level estimate $3.175M
GIDAP/ TPP | SP-42 | Devers Substation Reliability Network Upgrade (TOT789_Q1295) | 33.935, -116.578 | Desert Hot Springs, CA | Part of SCE's Reliability Network Upgrades under TOT789, Marvel Project; Devers Sub (RNU) a; engineer and construct one (1) 220 kV line position which includes 2 CBs, 3 disconnect switches, 1 disconnect switch with grounding attachment, and 14 - 220 kV bus support post insulators. | Reliability Network Upgrade | New/Upgrade | None | Work Requested by Others | GIDAP (Generation Interconnection) | N/A | N/A | System Impact Study; Facility Study | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Non-HFRA | See Note 16C | Extreme Temperature Conditions, High Wind Events | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | 98 | 220 kV | 418 MW; 220 kV | See Note 23B | 902748920 | CET-ET-TP-RN-819500 | 8195 | See Note 27A | Yes | 2019 | 2019 | LGIA | 2016 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, under the CAISO Generation Interconnection Process | Not Yet Operational | Not Yet Operational | TBD | TBD | TBD | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Construction more than 50% completed | See Note 46A | 2022-01-03 | Yes | 2022-10-01 | 2023-12-29 | Scope Change | 10916 | 1436.5666 | See Note 53A | 1560.4713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9148 | 199.1457 | 1359.4108 | 1560.4713 | 222.7963 | See Note 57A | 100% | See Note 59A | 1560.4713 | None | 100% | 0% | Column 9: GIDAP (Generator Interconnection) Column 52: Source= PMWIF (v0 Proj Summary); Represents PIN level estimate; WO level estimate $3.592M
GIDAP/ TPP | SP-44 | Red Bluff Substation Power System Control Upgrade (TOT760_Q1200) | 33.672, -115.559 | Desert Center, Riverside County | Power System Control (RNU) - Expand CRAS RTUs at Red Bluff Substation to include points for status and alarms related to the new CRAS relays. Modify the CRAS program to support the additional relays. | Red Bluff Substation (RNU) - 1. Install one (1) dedicated double breaker 220kV line position to terminate the Red Bluff-Sloth 220kV Transmission Line as follows: a. i. Install two (2) 220kV circuit breakers. ii. Install three (3) 220kV horizontal mounted group-operated disconnect switches. iii. Install one (1) 220kV horizontal mounted group operated disconnect switch with grounding attachment. iv. Install fourteen (14) 220kV bus supports post insulators pedestals. v. Install 2 1590 KCMIL ACSR conductors as required. b. Protection Relays i. Install two (2) GE N60 logic processing relays or equivalent successor to send additional tripping signals to the Large Generating Facility. | New, upgrade | None | Work Requested by Others | GIDAP (Generation Interconnection) | N/A - New | N/A - New | ● Power Flow ● Transient ● Post Transient ● Short Circuit Duty | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Non-HFRA | See Note 16C | High Wind Events, Extreme Temperature Conditions | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | 75.7 | See note 21A | See Note 22A | See Note 23B | 2 separate WOs | 2 separate CWBS | 8214 | See Note 27A | Yes | 2018 | 2020 | LGIA | 2015 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, under the CAISO Generation Interconnection Process | Not Yet Operational | Not Yet Operational | TBD | TBD | TBD | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Construction more than 50% completed | See Note 46A | 2023-03-08 | Yes | 2021-10-01 | 2023-12-29 | Scope Change and Material Delays | 8417 | 2182.7438 | See Note 53A | 4267.6278 | 903.689 | 51.797 | 2631.989 | 0 | 0 | 0 | 3587.475 | 0 | 0 | 0 | 6.9836 | 673.1692 | 680.1528 | 80.5453 | See Note 57A | N/A | See Note 59A | 680.1528 | None | 100% | 0% | Column 9: GIDAP (Generator Interconnection) Column 22: Not SCE facility, GIDAP Column 52: Source= PMWIF (v0 Proj Summary); Represents PIN level estimate; WO level estimate $3.620M
GIDAP/ TPP | SP-45 | Clover Energy Storage Plant Interconnect (TOT827_Q1330) | 34.688, -118.300 | Lancaster, Los Angeles County | To interconnect the Clover Energy Storage's generating facilities with SCE's distribution system at Antelope Substation | Antelope Substation- Tehachapi CRAS (RNU) - 1. Antelope Substation a. Install two (2) GE N60 logic processing relays or equivalent successor to send tripping signals to the Large Generating Facility. 2. Telecommunications a. Install channel banks and associated equipment at Antelope 66 kV Substation (including terminal equipment), to support the RAS requirements. | New/Interconnection | None | Work Requested by Others | GIDAP (Generation Interconnection) | 2020-05-18 | N/A - New | System Impact Study; Facility Study | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Non-HFRA | See Note 16C | High Wind Events, Extreme Temperature Conditions | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | See Note 20B | 66 | 280 MVA 230/66 kV | See Note 23B | 3 separate WOs | 3 separate CWBS | 8226 | See Note 27A | Yes | 2019 | 2020 | LGIA | 2016 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, under the CAISO Generation Interconnection Process | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Canceled | See Note 46A | Canceled | No | 2021-08-03 | Canceled | N/A | 4292 | 4292 | See Note 53A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | See Note 57A | N/A | See Note 59A | 0 | None | 0% | 100% | Column 9: GIDAP (Generator Interconnection) Column 42: Project has been cancelled by the customer; trend has been submitted to IWP for project cancellation. Column 52: Source= PMWIF (v0 Proj Summary); Represents PIN level estimate
TPP | SP-46 | Eldorado-Mohave and Eldorado-Moenkopi 500kV Line Position Swap | 35.798, -115.008 | Clark County, Nevada | Change the 500kV line positions at Eldorado substation for the Eldorado – Mohave and Eldorado –Moenkopi 500kV lines. | Transmission line | Removal / New | None | Other - See Notes | System Operations | Various - SCE performs annual patrols and triennial detailed inspections of its transmission circuits, which inspect the structures and lines on those circuits. Last inspections for the majority of these lines happened in 2019. | 30+ years | Bank Capacity, Power Flow, Short Circuit Duty, Dynamic Stability, SCE Subtransmission Planning Criteria and Guidelines | Relocate six (6) miles of the Eldorado-Lugo 500 kV line to obtain a minimum separation of 250 ft from the Eldorado-Mohave 500 kV line so as to remove the two circuits as a credible adjacent transmission contingency. | Non-HFRA | See Note 16C | High Wind Events, Extreme Temperature Conditions | Brent Gokbudak, MPO-Project Development & Execution | Varies based on project | Eldorado 86.7; Mohave 11.5; Moenkopi 19.9 | See note 21A | 500 kV | See Note 23B | 4 separate WOs | 4 separate CWBS | 7547 | See Note 27A | Yes | 2016 | Pre-2017 | Annual Capital Operating Plan Process | 2014 | 2014-15 to 2017-2018 | N/A | http://www.caiso.com/Documents/Board-Approved2014-2015TransmissionPlan.pdf | See Col. 37 | 2018 = 19,680 2019 = 1,078 2020 = -1,135 2021 = 10 2022 = 1 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2017-06-01 | No | 2016-05-01 | 2020-04-24 | Refinement of schedule for this project | 18300 | 18300 | See Note 53A | 19634.2764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19680.4116 | 1078.1194 | -1134.7068 | 183.2933 | -172.8411 | 19634.2764 | 2902.2859 | See Note 57A | N/A | See Note 59A | -9.476e-12 | None | 100% | 0% | Column 9: CAISO Policy Driven Column 52: Source= v1 Project Summary;PIN level estimate
N/A | SP-47 | Walnut Substation Circuit Breaker Replacement | 34.008, -117.950 | Industry, Los Angeles County | Walnut Substation: 1) Convert the Mesa 220 kV Line Position to Double Breaker. 2) Convert the No. 3A and 4A Bank High Side Positions to Double Breaker. 3) Remove the 220 kV North and South Bus Circuit Breakers. 4) Remove the A & B system F35 relays from the Midway-Vincent RAS | See "Project Description" | Replace / New | None | Other - See Notes | Substation Reliability | 2016-09-05 | Various | Bank Capacity, Power Flow, Short Circuit Duty SCE Subtransmission Planning Criteria and Guidelines | No alternatives - Equipping the banks in circuit breakers configuration would ensure compliance with present SCE criteria. | Non-HFRA | See Note 16C | High Seismic | Demetric Brown, MPO - Programs | See Note 19B | 14.3 | See note 21A | 220 and 66 kV | See Note 23B | 900772538 | CET-ET-TP-RL-711900 | 7119 | See Note 27A | Yes | 2012-08-02 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2019 = 7,180 2020 = 69 2021 = -3 2022 = 1 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2016-09-19 | No | 2017-12-31 | 2019-08-27 | Scope changes, testing and outage requirements | 8000 | 3280 | See Note 53A | 7246.5686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5762.4471 | 1417.3737 | 69.1665 | -3.1251 | 0.70648 | 7246.5686 | 1873.2913 | See Note 57A | N/A | See Note 59A | 6.6135e-12 | None | 100% | 0% | Column 9: Protection / Safety / Reliability Column 52: Source= Unverified system estimate
GIDAP/ TPP | SP-48 | North Rosamond Energy Only- Whirlwind 220/66 (T) - Install Interconnection Facilities (TOT497_Q643R) | 34.857, -118.436 | Rosamond, Kern County | SCE will design, procure, construct, own, operate, and maintain the Participating TO’s Interconnection Facilities and the Participating TO’s Reliability Network Upgrades required to interconnect the Project to the CAISO Controlled Grid; | Whirlwind Sub (POS) a. Equip one (1) 220 kV position at Whirlwind Substation to terminate the Rattlesnake-Whirlwind 220kV Transmission Line with the following Network Upgrades (plan of service): -Two (2) 3000A – 63 kA 220 kV circuit breakers -Four (4) 3000A – 80 kA horizontal –mounted group-operated disconnect switches -One (1) grounding switch attachment -2-1590 KCMIL ACSR conductors as required -Two (2) G.E. C60 breaker management relays (breaker failure) b. Power System Controls. Expand the Whirlwind Substation RTU to provide additional points required for the Project’s 220 kV generation tie-line position. | New/Interconnection | None | Work Requested by Others | GIDAP (Generation Interconnection) | N/A | N/A - New | Bank Capacity, Power Flow, Short Circuit Duty SCE Subtransmission Planning Criteria and Guidelines | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Non-HFRA | See Note 16C | High Wind Events, Extreme Temperature Conditions, High Seismic | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | 92 | See note 21A | 220 kV | See Note 23B | 901458993 | CET-ET-TP-RN-775602 | 7756 | See Note 27A | Yes | 2014-12-24 | Pre-2017 | LGIA | 2011 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, under the CAISO Generation Interconnection Process | See Col. 37 | 2018 = 3,375 2019 = 388 2020 = 59 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2017-09-25 | No | 2016-11-01 | 2018-11-08 | Refinement of schedule for this project | 9416 | 2834.5471 | See Note 53A | 3820.9646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3374.8292 | 387.6024 | 58.5329 | -7.2475e-13 | 0 | 3820.9646 | 778.7361 | See Note 57A | 100% | See Note 59A | -3.0682e-13 | None | 100% | 0% | Column 9: GIDAP (Generator Interconnection) Column 52: Source= v0 Project Summary; Represents PIN level cost; WO level estimate $2.620M
TPP | SP-49 | Eagle Mountain Reactor Project | 33.811, -115.454 | Desert Center, Riverside County | Eagle Mountain Substation: Install a 45 MVAR tertiary reactor (effective 34 MVAR @ 12 kV) on the 5A bank at Eagle Mountain substation. Extend Eagle Mountain 230 kV operating bus and install a 45 MVAR shunt reactor at west end of the operating bus. Build a new MEER. | Substation Reactor Installation | New | None | Other - See Notes | Substation Reliability | N/A | N/A - New; Substation >70 years | Bank Capacity, Power Flow, Short Circuit Duty, dynamic stability, SCE Subtransmission Planning Criteria and Guidelines | N/A | Non-HFRA | See Note 16C | High Seismic | Demetric Brown, MPO - Programs | See Note 19B | 11 | See note 21A | 5A bank tertiary reactor 34 MVAR; 220kV bus shunt reactor 45 MVAR | See Note 23B | 901552346 | CET-ET-TP-RL-779000 | 7790 | See Note 27A | Yes | 2015-11-05 | Pre-2017 | Annual Capital Operating Plan Process | 2015 | 2018 | N/A | http://www.caiso.com/Documents/Board-Approved2015-2016TransmissionPlan.pdf | See Col. 37 | 2018 = 7,989 2019 = 33 2020 = 11 | TBD | TBD | TBD | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2017-11-27 | No | 2018-12-31 | 2018-08-28 | N/A | 10079 | 10079 | See Note 53A | 8033.282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7989.2697 | 33.2168 | 10.7955 | 0 | 0 | 8033.282 | 1245.2744 | See Note 57A | N/A | See Note 59A | -8.6889e-12 | None | 100% | 0% | Column 9: Mitigate power quality (voltage) concerns Column 52: Source= Unverified system estimate
N/A | SP-50 | Johanna 220/66 (S)-Install new 280MVA transformer to mitigate A-bank N-1 condition | 33.714, -117.852 | Santa Ana, Orange County | Johanna Substation: -Equip New 220kV position with (1) 220kV Circuit Breaker and (2) 220kV Disconnects -Install a new 220/66 kV -280 MVA bank -Replace no. 2 & 3 capacitor bank switchers (#603 & 601 respectively) with two (2) new disconnect switches with grounding attachment. -Remove no. 2 & 3 capacitor bank ground switches. -Extend 66kV rack by installing a new 8 bay low profile bus, bus support structures, foundation, and bus perimeter fence. -Equip (4) new 66kV position bank with (8) 66kV Circuit Breakers -Install (1) sectionalizing breaker -Replace (19) 66kV Circuit Breakers -Update RTU -EH&S -Relay Coordination Study ($100k) Associated Relay Work -Install new No.1A Transformer Bank Differential ((1) SEL-387, (1) GE-C30, (1) GE-T60, (1) GE-D60) -Install new 220kV No.1A Transformer Bank LBFB ((2) GE-C60) -Install new 66kV Switchrack (section B) LBFB ((9) GE-C60) -Install new 66kV West Bus section B Bus Differential ((1) SEL-587Z) -Replace (1) 12kV CB (#316) | Substation Transformer | New / Replace /Upgrade | None | Capacity Increase | Substation Capacity | 2018-09-08 | N/A - New | Bank Capacity, Power Flow, Short Circuit Duty, dynamic stability, SCE Subtransmission Planning Criteria and Guidelines | Install new 280 MVA transformer bank at Villa Park 200/66 kV Substation and split the 66 kV bus. Extend switchrack one position. Reconfigure 66 kV lines. Add ground banks to two transformers | Non-HFRA | See Note 16C | High Seismic, Salt Corrosion (Coastal Areas) | Demetric Brown, MPO - Programs | See Note 19B | 9.9 | See note 21A | 280 MVA 220kV/66kV | See Note 23B | 901487156 | CET-ET-LG-TS-776700 | 7767 | See Note 27A | Yes | 2015-07-24 | Pre-2017 | Annual Capital Operating Plan Process | No | N/A | N/A | N/A | See Col. 37 | 2020 = 1,291 2021 = 63 2022 = 18 | TBD | TBD | TBD | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2018-10-02 | No | 2018-06-01 | 2020-05-18 | Property negotiations with existing RV parking tenant and extended litigation, and resource and engineering delays. | 22677 | 1085.8485 | See Note 53A | 1372.1075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 606.5548 | 451.8561 | 232.5275 | 62.6783 | 18.4908 | 1372.1075 | 269.9679 | See Note 57A | N/A | See Note 59A | 4.1921e-13 | None | 100% | 0% | Column 9: Load driven project, needed to serve areas Column 52: Source= PMWIF (v0 Project Summary); Represents PIN & WO level cost estimate
GIDAP | SP-51 | Whirlwind Substation (RNU) (TOT778_Q1217) | 34.857, -118.436 | Mojave, CA | Part of SCE's Reliability Network Upgrade under TOT819; Whirlwind Substation (RNU) Tehachapi Centralized RAS (“Tehachapi CRAS”) Install two (2) GE N60 logic processing relays or equivalent successor to send tripping signals to Lone Butte (the Large Generating Facility). | Reliability Network Upgrade | New/Upgrade | None | Work Requested by Others | GIDAP (Generation Interconnection) | N/A | N/A | System Impact Study; Facility Study | N/A | Non-HFRA | See Note 16C | High Wind Events, Extreme Temperature Conditions | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | See Note 20B | 220 kV | 300 MW; 500 and 220 kV | See Note 23B | 902668204 | CET-ET-TP-RN-820100 | 8201 | See Note 27A | Yes | 2018 | 2020 | LGIA | No | N/A | N/A | N/A | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Construction more than 50% completed | See Note 46A | 2023-11-01 | Yes | 2022-03-01 | 2023-12-31 | Refinement of schedule for this project | 1651 | 897.1842 | See Note 53A | 957.4162 | 341.707 | 330 | 244.289 | 0 | 0 | 0 | 915.996 | 0 | 0 | 16.1028 | 2.1767 | 23.1407 | 41.4202 | 15.1606 | See Note 57A | 100% | See Note 59A | 41.4202 | None | 100% | 0% | Column 9: GIDAP (Generator Interconnection) Column 52: Source= PMWIF (v0 Proj Summary); Represents PIN level estimate; WO level estimate $1.149M
GIDAP | SP-52 | Rabbitbrush Solar RNU (TOT777_Q1215 ) | 34.873369, -118.370058 | Rosamond, Kern County | To interconnect Rabbitbrush Solar's 150 MW solar photovoltaic generating station to SCE's transmission system; Tehachapi CRAS (relays, channel banks), Whirlwind AA Bank RAS (relays, channel banks), Power System Control (Point addition at SCE sub to support Tehachapi CRAS), Power System Control (Point addition at SCE sub to support Whirlwind CRAS), Power System Control (Point additions to existing RTU at Whirlwind Sub) | Reliability Network Upgrade | New | SP-29 | Work Requested by Others | GIDAP (Generation Interconnection) | N/A | N/A new | Power Flow, Transient, Post Transient, Short Circuit Duty | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Non-HFRA | See Note 16C | No significant environmental factors | Demetric Brown, MPO - Programs | See Note 19B | 92 | See note 21A | See Note 22A | See Note 23B | 3 separate WOs | 3 separate CWBS | 8204 | See Note 27A | Yes | 2019 | 2019 | LGIA | 2015 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | See Col. 37 | 2022 = 665 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2022-10-03 | Yes | 2021-12-31 | 2022-11-17 | Scope Refinement | 1483 | 802.7169 | See Note 53A | 664.6635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.2968 | 424.7543 | 223.6124 | 664.6635 | 172.3201 | See Note 57A | 100% | See Note 59A | -1.962e-13 | None | 100% | 0% | Column 9: GIDAP (Generator Interconnection) Column 52: Source= PMWIF (v0 Proj Summary); Represents PIN level estimate
GIDAP | SP-53 | Willy 9 RNU (TOT793_Q1319) | 34.84, -118.325 | Rosamond, Kern County | To interconnect Chaparral Solar's 250 MW Willy 9 solar photovoltaic generating station to SCE's transmission system; Tehachapi CRAS (f.k.a. Northern Area RAS) generator addition, Whirlwind AA Bank RAS generator addition, Implement Whirlwind AA Bank CRAS, Power System Control (point addition at SCE sub to support Tehachapi CRAS and Whirlwind CRAS) | Reliability Network Upgrade | New | SP-29 | Work Requested by Others | GIDAP (Generation Interconnection) | N/A | N/A new | Power Flow, Transient, Post Transient, Short Circuit Duty | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Non-HFRA | See Note 16C | No significant environmental factors | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | 92 | See note 21A | See Note 22A | See Note 23B | 3 separate WOs | 3 separate CWBS | 8223 | See Note 27A | Yes | 2018 | 2019 | LGIA | 2016 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Construction more than 50% completed | See Note 46A | 2023-02-15 | No | 2021-07-31 | 2024-03-14 | Customer submitted MMA to push out dates. | 1483 | 860.2871 | See Note 53A | 926.6906 | 572.192 | 230.61 | 0 | 0 | 0 | 0 | 802.802 | 0 | 0 | 14.0196 | 6.259 | 103.6101 | 123.8886 | 37.1907 | See Note 57A | 100% | See Note 59A | 123.8886 | None | 100% | 0% | Column 9: GIDAP (Generator Interconnection) Column 52: Source= PMWIF (v0 Proj Summary); Represents PIN level estimate
GIDAP | SP-54 | Daggett Solar 1 RNU (TOT812_Q1312) | 34.873, -116.896 | Daggett, San Bernardino County | To interconnect Daggett Solar Power 1's 144 MW solar photovoltaic/battery storage generating station to SCE's transmission system; Plan of Service - Substation, Plan of Service - Environmental Services | Reliability Network Upgrade | New | None | Work Requested by Others | GIDAP (Generation Interconnection) | N/A new | N/A new | Power Flow, Transient, Post Transient, Short Circuit Duty | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Non-HFRA | See Note 16C | Extreme Temperature Conditions | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | 4.6 | See note 21A | See Note 22A | See Note 23B | 4 separate WOs | 4 separate CWBS | 8239 | See Note 27A | Yes | 2018 | 2018 | LGIA | 2016 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | Not Yet Operational | Not Yet Operational | TBD | TBD | TBD | TBD | TBD | TBD | N/A | Engineering more than 50% completed | See Note 46A | 2024-06-17 | No | 2021-09-15 | 2025-01-09 | Customer requested project on hold and coordination with other projects | 7959 | Not readily available | See Note 53A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | See Note 57A | 100% | See Note 59A | 0 | None | 100% | 0% | Column 9: GIDAP (Generator Interconnection) Column 52: Source= PMWIF (v1 Proj Summary); Represents PIN level estimate Column 52.1: FERC % not yet available in source file; will be updated in future SRP once available
GIDAP | SP-55 | Quartzite Solar 8 RNU (TOT749_Q1198) | 33.589816, -114.787323 | Blythe, Riverside County | To interconnect Desert Quartzite's 150 MW Quartzite Solar 8 solar photovoltaic and battery storage generating station to SCE's transmission system; Add generator to Colorado River Corridor centralized RAS (N60 relays & programming), Equip 220 kV CB & ½ (2-CB) line position at Colorado River Substation, Ground Grid Study, Relay coordination study & adjust setting for cRAS inclusion, Power System Control: Point additions for Colorado River Corridor centralized RAS, Environmental Services: Activities related to 220 kV line position at Colorado River Substation. | Reliability Network Upgrade | New | None | Work Requested by Others | GIDAP (Generation Interconnection) | N/A | N/A new | Power Flow, Transient, Post Transient, Short Circuit Duty | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Non-HFRA | See Note 16C | Extreme Temperature Conditions, High Seismic | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | 77 | See note 21A | See Note 22A | See Note 23B | 902598927 | CET-ET-CR-WC-820701 | 8207 | See Note 27A | Yes | 2018 | 2020 | LGIA | 2011 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Construction less than 50% completed | See Note 46A | 2023-08-28 | No | 2022-01-15 | 2024-06-14 | Material Delays | 9660 | 5942.3299 | See Note 53A | 3514.6975 | 620.041 | 1003.48 | 1796.816 | 0 | 0 | 0 | 3420.337 | 0 | 0 | 0 | 33.8719 | 60.4886 | 94.3605 | 34.4059 | See Note 57A | 100% | See Note 59A | 94.3605 | None | 100% | 0% | Column 9: GIDAP (Generator Interconnection) Column 52: Source= PMWIF (v1 Proj Summary); Represents PIN level estimate; WO level estimate $506k
GIDAP | SP-56 | Athos Power Plant RNU (TOT849_Q1405) | 33.746099, -115.360852 | Desert Center, Riverside County | To interconnect Athos Power Plant's 450 MW solar photovoltaic/battery storage generating station to SCE's transmission system; New Red Bluff 220 kV Substation, West of Colorado River CRAS Inland/Devers extension, West of Colorado River CRAS expansion | Reliability Network Upgrade | New | PB-40 | Work Requested by Others | GIDAP (Generation Interconnection) | N/A | N/A new | Power Flow, Transient, Post Transient, Short Circuit Duty | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Non-HFRA | See Note 16C | Extreme Temperature Conditions, High Seismic | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | 75.7 | See note 21A | See Note 22A | See Note 23B | 8 separate WOs | 8 separate CWBS | 8220 | See Note 27A | Yes | 2018 | 2018 | LGIA | 2017 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | See Col.37 | 2021 = 4,018 2022 = 51 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Construction more than 50% completed | See Note 46A | 2021-01-19 | Yes | 2021-07-31 | 2023-12-29 | Coordination with Other Projects for CRAS QA Test | 11186 | 1521.5517 | See Note 53A | 14630.961 | 596.918 | 50 | 50 | 0 | 0 | 0 | 696.918 | 0 | 618.2591 | 3071.4582 | 6468.6455 | 3775.6802 | 13934.043 | 3445.1887 | See Note 57A | 100% | See Note 59A | 9776.8734 | None | 100% | 0% | Column 9: GIDAP (Generator Interconnection) Column 52: Source= PMWIF (v3 Proj Summary); Represents PIN level estimate
GIDAP | SP-57 | High 5 Solar RNU (TOT847_Q1414) | 34.630879, -117.373721 | San Bernardino, San Bernardino County | To interconnect High 5 Solar's 100 MW solar photovoltaic generating station to SCE's transmission system; New HDPP RAS, North of Lugo CRAS | Reliability Network Upgrade | New | None | Work Requested by Others | GIDAP (Generation Interconnection) | N/A new | N/A new | Power Flow, Transient, Post Transient, Short Circuit Duty | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Non-HFRA | See Note 16C | Extreme Temperature Conditions | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | 33.3 | See note 21A | See Note 22A | See Note 23B | 902732437 | CET-ET-TP-RN-822700 | 8227 | See Note 27A | Yes | 2019 | 2018 | LGIA | 2017 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | See Col.37 | 2021 = 601 2022 = -19 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2021-04-02 | No | 2021-05-01 | 2021-06-19 | Outage Constraints | 3806 | 859 | See Note 53A | 582.0263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.8822 | 247.4127 | 262.3316 | -18.6003 | 582.0263 | 168.5557 | See Note 57A | 100% | See Note 59A | 8.6051e-13 | None | 100% | 0% | Col 52.1 was updated per Dec 2021 Data Request responses. Column 9: GIDAP (Generator Interconnection) Column 52: Source= PMWIF (v0 Proj Summary); Represents PIN level estimate; WO level estimate $859k
GIDAP | SP-58 | Golden Fields Solar RNU (TOT754_Q1212) | 34.844786, -118.391535 | Rosamond, Kern County | To interconnect Raven Solar Development Company's 100 MW Golden Fields solar photovoltaic generating station to SCE's transmission system; Add Large Generating Facility to Tehachapi CRAS, Whirlwind AA Bank RAS, Equip 220 kV circuit breaker & ½ (2 circuit breaker) line position | Reliability Network Upgrade | New | SP-29 | Work Requested by Others | GIDAP (Generation Interconnection) | N/A | N/A new | Power Flow, Transient, Post Transient, Short Circuit Duty | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Non-HFRA | See Note 16C | High Wind Events, Extreme Temperature Conditions | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | 92 | See note 21A | See Note 22A | See Note 23B | 903099017 | CET-ET-TP-RN-828500 | 8285 | See Note 27A | Yes | 2019 | 2020 | LGIA | 2015 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | Not Yet Operational | Not Yet Operational | TBD | TBD | TBD | TBD | TBD | TBD | N/A | Engineering more than 50% completed | See Note 46A | 2024-11-25 | No | 2022-04-01 | 2024-12-24 | POCO location recently defined/extended major material times Change of Customer COD | 12339 | 4436 | See Note 53A | 3645.7231 | 189.012 | 1554.078 | 610 | 1275 | 0 | 0 | 3628.09 | 0 | 0 | 0 | 0 | 17.6331 | 17.6331 | 8.2029 | See Note 57A | 100% | See Note 59A | 17.6331 | None | 100% | 0% | Col 52.1 was updated per Dec 2021 Data Request responses. Column 9: GIDAP (Generator Interconnection) Column 52: Source= PMWIF (v0 Proj Summary); Represents PIN level estimate; WO level estimate $4.436M
GIDAP | SP-59 | Solar Star 3 RNU (TOT795_Q1322) | 34.857, -118.436 | Rosamond, Kern County | To interconnect Solar Star 3's 24 MW solar photovoltaic/energy storage generating station to SCE's transmission system; At Substation (Tehachapi CRAS (f.k.a. Northern Area RAS) - generator addition), at Substation (Whirlwind AA Bank RAS - generator addition), at Substation (implement Whirlwind AA Bank CRAS ‐ monitoring infrastructure), Power System Control (Point addition at SCE sub to support Tehachapi CRAS), Power System Control (Point addition at SCE sub to support Whirlwind CRAS) | Reliability Network Upgrade | New | SP-29 | Work Requested by Others | GIDAP (Generation Interconnection) | N/A | N/A new | Power Flow, Transient, Post Transient, Short Circuit Duty | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Non-HFRA | See Note 16C | High Wind Events, Extreme Temperature Conditions | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | 92 | See note 21A | See Note 22A | See Note 23B | 902924856 | CET-RP-CR-WC-827000 | 8270 | See Note 27A | Yes | 2019 | 2020 | LGIA | 2016 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | Not Yet Operational | Not Yet Operational | TBD | TBD | TBD | TBD | TBD | TBD | N/A | Engineering more than 50% completed | See Note 46A | 2024-10-11 | No | 2023-02-01 | 2024-11-07 | OD Change per LGIA | 1739 | Not readily available | See Note 53A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | See Note 57A | 100% | See Note 59A | 0 | None | 100% | 0% | Column 9: GIDAP (Generator Interconnection) Column 52: Source= PMWIF (v0 Proj Summary); Represents PIN level estimate; WO level estimate $1.198M Column 52.1: FERC % not yet available in source file; will be updated in future SRP once available
GIDAP | SP-60 | Solar Star 4 RNU (TOT821_Q1323) | 34.857, -118.436 | Rosamond, Kern County | To interconnect Solar Star 4's 26.54 MW solar photovoltaic/energy storage generating station to SCE's transmission system; Substation: Tehachapi CRAS (f.k.a. Northern Area RAS) - generator addition; Substation: Whirlwind AA Bank RAS - generator addition; Power System Control: Point addition at SCE sub to support Tehachapi CRAS; Power System Control: Point addition at SCE sub to support Whirlwind CRAS | Reliability Network Upgrade | New | SP-29 | Work Requested by Others | GIDAP (Generation Interconnection) | N/A | N/A new | Power Flow, Transient, Post Transient, Short Circuit Duty | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Non-HFRA | See Note 16C | High Wind Events, Extreme Temperature Conditions | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | 92 | See note 21A | See Note 22A | See Note 23B | 902924965 | CET-RP-CR-WC-826900 | 8269 | See Note 27A | Yes | 2019 | 2020 | LGIA | 2016 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | Not Yet Operational | Not Yet Operational | TBD | TBD | TBD | TBD | TBD | TBD | N/A | Engineering more than 50% completed | See Note 46A | 2024-02-09 | No | 2023-02-01 | 2024-03-07 | OD Change per LGIA | 1739 | Not readily available | See Note 53A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | See Note 57A | 100% | See Note 59A | 0 | None | 100% | 0% | Column 9: GIDAP (Generator Interconnection) Column 52: Source= PMWIF (v1 Proj Summary); Represents PIN level estimate; WO level estimate $1.198M Column 52.1: FERC % not yet available in source file; will be updated in future SRP once available
GIDAP | SP-61 | Bellefield Solar Farm RNU (TOT892_Q1510) | 35.012635, -118.077893 | Mojave, Kern County | To interconnect 50LW 8ME's 500 MW Bellefield Solar Farm solar photovoltaic/energy storage generating station to SCE's transmission system; New 220 kV switchrack @ Windhub Substation, environmental services, Tehachapi centralized RAS – generation addition, Windhub AA Bank centralized RAS - generator addition, Windhub AA Bank centralized RAS - monitoring infrastructure | Reliability Network Upgrade | New | SP-29 | Work Requested by Others | GIDAP (Generation Interconnection) | N/A | N/A new | Power Flow, Transient, Post Transient, Short Circuit Duty | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Non-HFRA | See Note 16C | High Wind Events, Extreme Temperature Conditions | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | 14 | 59.2 | 220 KV | See Note 22A | See Note 23B | 4 separate WOs | 4 separate CWBS | 8298 | See Note 27A | Yes | 2020 | 2019 | LGIA | 2018 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Construction less than 50% completed | See Note 46A | 2023-03-27 | No | 2022-10-15 | 2024-07-02 | Customer Point-of-Interconnection design delay | 9192 | 4163 | See Note 53A | 6149.0077 | 1887.523 | 1146.946 | 1148.661 | 0 | 0 | 0 | 4183.13 | 0 | 0 | 9.8642 | 684.2061 | 1271.8073 | 1965.8777 | 251.5491 | See Note 57A | 100% | See Note 59A | 1965.8777 | None | 100% | 0% | Col 52.1 was updated per Dec 2021 Data Request responses Column 9: GIDAP (Generator Interconnection) Column 52: Source= PMWIF (v0 Proj Summary); Represents PIN level estimate
GIDAP | SP-62 | Daggett Solar 3 RNU (TOT810_Q1314) | 34.8623, -116.8912 | Daggett, San Bernardino County | To interconnect Daggett Solar Power 3's 300 MW solar photovoltaic/energy storage generating station to SCE's transmission system; Add Project to North of Lugo Centralized RAS – Install two N60 Relays | Reliability Network Upgrade | New | None | Work Requested by Others | GIDAP (Generation Interconnection) | N/A new | N/A new | Power Flow, Transient, Post Transient, Short Circuit Duty | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Non-HFRA | See Note 16C | Extreme Temperature Conditions | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | 3.3 | 4.6 | 220 kV | See Note 22A | See Note 23B | 903103547 | CET-ET-TP-RN-824100 | 8241 | See Note 27A | Yes | 2019 | 2020 | LGIA | 2016 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | See Col.37 | 2022 = 0 | TBD | TBD | TBD | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2022-03-28 | Yes | 2022-09-15 | 2022-12-15 | Customer Delays and Material Delays | 12979 | 3.9801 | See Note 53A | 0.11623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11623 | 0.11623 | 0.01478 | See Note 57A | 100% | See Note 59A | 0.11623 | None | 100% | 0% | Column 9: GIDAP (Generator Interconnection) Column 52: Source= PMWIF (v0 Proj Summary); PIN level estimate
GIDAP | SP-63 | WOCR CRAS Inland Devers Extension | 33.784, -113.603 | Salome, La Paz County, Arizona | To interconnect Atlas Solar project's 3,200 MW solar photovoltaic and battery storage generating station to SCE's transmission system as part of an Affected Participating Transmission Owner Upgrade Facilities Agreement; Colorado River Substation telecommunications, West of Colorado River CRAS Inland/Devers extension – generator addition, West of Colorado River CRAS Inland/Devers Extension –Monitoring infrastructure, West of Colorado River CRAS expansion – generation addition, Ground Grid Study. | Reliability Network Upgrade | New | None | Work Requested by Others | GIDAP (Generation Interconnection) | N/A | N/A new | Power Flow, Transient, Post Transient, Short Circuit Duty | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Out of State | See Note 16C | Extreme Temperature Conditions | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | See Note 20B | See note 21A | See Note 22A | See Note 23B | 4 separate Wos | 4 separate CWBS | 8284 | See Note 27A | Yes | 2020 | 2019 | LGIA | 2017 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Construction more than 50% completed | See Note 46A | 2021-09-27 | No | 2022-12-30 | 2025-02-24 | Coordination with other non-SCE projects with the Interconnecting PTO and IC. | 19771 | 19083.7505 | See Note 53A | 2921.0071 | 707.879 | 750 | 0 | 0 | 0 | 0 | 1457.879 | 0 | 68.0062 | 251.5038 | 157.0674 | 986.5506 | 1463.1281 | 402.2844 | See Note 57A | 100% | See Note 59A | 1463.129 | None | 100% | 0% | Column 2: Previously called "Atlas Solar RNU (TOT870AFS_Q1402)" Column 9: GIDAP (Generator Interconnection) Column 52: Source= PMWIF (v2 Proj Summary); Represents PIN level estimate; WO level estimate $1.402M
GIDAP | SP-64 | Baldy Mesa RNU (TOT851_Q1413) | 34.499103, -117.417355 | Adelanto, San Bernardino County | To interconnect sPower Development Company's Baldy Mesa 100 MW generating facility to SCE's 115 kV system; North of Lugo CRAS - generation addition North of Lugo CRAS - monitoring infrastructure, Short -Circuit Duty Mitigation | Reliability Network Upgrade | New | None | Work Requested by Others | GIDAP (Generation Interconnection) | N/A | N/A new | Power Flow, Transient, Post Transient, Short Circuit Duty | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Non-HFRA | See Note 16C | Extreme Temperature Conditions, High Wind Events, Air particulate levels | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | 0.1 | See note 21A | See Note 22A | See Note 23B | 5 separate WOs | 5 separate CWBS | 8246 | See Note 27A | Yes | 2020 | 2018 | LGIA | 2017 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | ADVICE 4665-E | 2021-12-10 | Exempt: Not subject to GO 131-D licensing | 2021 | Pre-Construction | See Note 46A | 2022-04-04 | Yes | 2021-08-02 | 2023-12-08 | Additional Phases | 5797 | 548.804 | See Note 53A | 584.1422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.8443 | 94.846 | 131.7373 | 345.7146 | 584.1422 | 135.2794 | See Note 57A | 100% | See Note 59A | 584.1422 | None | 100% | 0% | Column 9: GIDAP (Generator Interconnection) Column 52: Source= PMWIF (v0 Proj Summary);PIN level estimate
GIDAP | SP-65 | Daggett Solar 2 RNU (TOT811_Q1313) | 34.862251. -116.856503 | Daggett, San Bernardino County | To interconnect Daggett Solar Power's Daggett Solar 2 energy storage-battery/solar PV generating facility to SCE' Coolwater 220kV substation; RNU include Mojave Desert RAS and Short-Circuit Duty Mitigation. | Reliability Network Upgrade | New | None | Work Requested by Others | GIDAP (Generation Interconnection) | N/A new | N/A new | Power Flow, Transient, Post Transient, Short Circuit Duty | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Non-HFRA | See Note 16C | Extreme Temperature Conditions | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | 4.6 | See note 21A | See Note 22A | See Note 23B | 2 separate WOs | 2 separate CWBS | 8240 | See Note 27A | Yes | 2019 | Not Available | LGIA | 2016 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | See Col. 37 | 2023 = 0 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2022-11-15 | Yes | 2023-04-15 | 2023-04-18 | N/A | 504 | Not readily available | See Note 53A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | See Note 57A | 100% | See Note 59A | 0 | None | 100% | 0% | Column 9: GIDAP (Generator Interconnection) Column 52: Source= PMWIF (v1 Proj Summary); Represents PIN level estimate Column 52.1: FERC % not yet available in source file; will be updated in future SRP once available
TPP | SP-66 | TRTP 6 Environmental Restoration, Oak Tree Mitigation, Escrow Close-Out | 34.487, -118.119/ 34.159, -117.943 | Acton/ Duarte, Los Angeles County & Angeles National Forest | Replacement of impacted trees and habitat resources impacted during construction of the TRTP as set forth in the Habitat Restoration Plan (ANF 2014) and the Habitat Mitigation and Monitoring Plan (ICF, 2014) prepared as required under mitigation measures Bio-1a,1b and 1c of the EIR and EIS. | Environmental | Restoration | None | Other - See Notes | Environmental | N/A | NA | Performed all required analysis per permit | Robust alternative analysis conducted and included in the Environmental Impact Report (EIR) and Environmental Impact Statement (EIS) | Tier 3 | See Note 16C | High Wind Events, High Fire Area, Extreme Temperature Conditions | Brent Gokbudak, MPO-Project Development & Execution | See Note 19B | See Note 20B | See Note 21A | See Note 22A | See Note 23B | 903216225 | CET-ET-TP-RN-524301 | 5243 | See Note 27A | Yes | 2014 | 2021 | Other- See Notes | No | N/A | N/A | N/A | Not Yet Operational | Not Yet Operational | Final Certified | EIR/EIS | CPUC/ US Forest Service | N/A- See Notes | N/A- See Notes | Approved | 2014 | Engineering more than 50% completed | See Note 46A | 2024-04-05 | No | 2025-12-31 | 2028-12-31 | Change is due to a decision Jan 2022 by the USFS to require 5 years monitoring of plants installed in 2022 in place of the 10 year requirement to monitor trees planted in 2020. | 39867 | 38113.4924 | See Note 53A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.93706 | 1909.5467 | -1910.4837 | 0 | 0 | See Note 57A | N/A | See Note 59A | 2.7099e-13 | Return on Equity (ROE) Adder, Abandoned Plant & CWIP Incentives (121 FERC ¶ 61,168) | 100% | 0% | Column 1: Environmental capital restoration/ remediation required as part of project licensure; therefore several fields are not applicable to this type of work Column 3: Start and end point of segment Column 9: Habitat Restoration Column 19 & 21: Project is related to environmental restoration, not directly related to the Transmission line project Column 31: Habitat Restoration Plan Column 41: Condition of CPUC Licensing process, no separate approval required Column 52: Source= PMWIF (v8 Proj Summary);SCE believes the project was PMWIF'd at a lower cost estimate; however, PMWIF is not readily available, so SCE provides a later estimate that it is able to verify with documentation Column 53: The maximum and reasonable prudent cost established in the Certificate of Public Convenience and Necessity pursuant to California Public Utilities Code Section 1005.5 (a) for this project, includes, but is not limited to: (1) $746 million (2008$) as noted in D.09-09-033 dated September 24, 2009 and issued on September 28, 2009, which amended D.07-03-012 and D.07-03-045 (For Segments 1-3); and (2) $1,522.92 million, excluding AFUDC which is estimated at $261.82 million for a total estimated project cost of $1,784.74 Million (2009$) as noted in CPUC Decision 09-12-044 dated December 17, 2009, and issued on December 24, 2009 (Segments 4-11); (3) the addition of $32.95 million (2013$), including Contracting Termination Charges, as noted in CPUC Decision D13-02-035 dated July 28, 2013 and issued on March 6, 2013 (for studies related to the feasibility of undergrounding Segment 8A); (4) the addition of $224 million (2013$) as noted in the CPUC Decision D13-07-018 dated July 11, 2013 and issued on July 16, 2013 (undergrounding of Segment 8A); and (5) the addition of $23 million (2013$) as noted in CPUC Decision D14-01-005 dated January 16, 2014 and issued on January 14, 2014 (the inclusion of voltage control equipment for UG5), as well as any adjustments to these amounts made in any of the Petitions for Modification filed in A.07-06-031 and any related dockets associated with the project. Further, as referenced above, these amounts are in different year nominal dollars and would need to be placed in current year dollars to determine the actual cost for the project
TPP | SP-67 | TRTP 7 Environmental Restoration, Oak Tree Mitigation, Escrow Close-Out | 34.159, -117.943/ 34.037, -118.11 | Duarte/ Montebello, Los Angeles County | Replacement of impacted trees and habitat resources impacted during construction of the TRTP as set forth in the Habitat Mitigation and Monitoring Plan (ICF, 2014) prepared as required under mitigation measures Bio-1a,1b and 1c of the EIR. | Environmental | Restoration | SP-68 | Other - See Notes | Environmental | N/A | NA | Performed all required analysis per permit | Robust alternative analysis conducted and included in the Environmental Impact Report (EIR) | Tier 3/ Non-HFRA | See Note 16C | High Wind Events, High Fire Area, Extreme Temperature Conditions | Brent Gokbudak, MPO-Project Development & Execution | See Note 19B | See Note 20B | See Note 21A | See Note 22A | See Note 23B | 903216563 | CET-ET-TP-RN-643801 | 6438 | See Note 27A | Yes | 2014 | 2021 | Other- See Notes | No | N/A | N/A | N/A | Not Yet Operational | Not Yet Operational | Final Certified | EIR | CPUC | N/A- See Notes | N/A- See Notes | Approved | 2014 | Construction more than 50% completed | See Note 46A | 2015 | No | 2024-12-31 | 2024-12-31 | N/A | 130798 | 123532.009 | See Note 53A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 472.1957 | -472.1957 | 0 | -7.276e-15 | See Note 57A | N/A | See Note 59A | 7.5659e-14 | Return on Equity (ROE) Adder, Abandoned Plant & CWIP Incentives (121 FERC ¶ 61,168) | 100% | 0% | Column 1: Environmental capital restoration/ remediation required as part of project licensure; therefore several fields are not applicable to this type of work Column 3: Start and end point of segment Column 9: Habitat Restoration Column 19 & 21: Project is related to environmental restoration, not directly related to the Transmission line project Column 31: Habitat Restoration Plan Column 41: Condition of CPUC Licensing process, no separate approval required Column 52: Source= PMWIF (v4 Proj Summary);SCE believes the project was PMWIF'd at a lower cost estimate of approximately $76.7M; however, PMWIF is not readily available, so SCE provides a later estimate that it is able to verify with documentation Column 53: The maximum and reasonable prudent cost established in the Certificate of Public Convenience and Necessity pursuant to California Public Utilities Code Section 1005.5 (a) for this project, includes, but is not limited to: (1) $746 million (2008$) as noted in D.09-09-033 dated September 24, 2009 and issued on September 28, 2009, which amended D.07-03-012 and D.07-03-045 (For Segments 1-3); and (2) $1,522.92 million, excluding AFUDC which is estimated at $261.82 million for a total estimated project cost of $1,784.74 Million (2009$) as noted in CPUC Decision 09-12-044 dated December 17, 2009, and issued on December 24, 2009 (Segments 4-11); (3) the addition of $32.95 million (2013$), including Contracting Termination Charges, as noted in CPUC Decision D13-02-035 dated July 28, 2013 and issued on March 6, 2013 (for studies related to the feasibility of undergrounding Segment 8A); (4) the addition of $224 million (2013$) as noted in the CPUC Decision D13-07-018 dated July 11, 2013 and issued on July 16, 2013 (undergrounding of Segment 8A); and (5) the addition of $23 million (2013$) as noted in CPUC Decision D14-01-005 dated January 16, 2014 and issued on January 14, 2014 (the inclusion of voltage control equipment for UG5), as well as any adjustments to these amounts made in any of the Petitions for Modification filed in A.07-06-031 and any related dockets associated with the project. Further, as referenced above, these amounts are in different year nominal dollars and would need to be placed in current year dollars to determine the actual cost for the project
TPP | SP-68 | TRTP 8 Environmental Restoration, Oak Tree Mitigation, Escrow Close-Out | 34.036, -118.076/ 34.008, -117.566 | Montebello, Los Angeles County & Chino Hills, San Bernardino County | Replacement of impacted trees and habitat resources impacted during construction of the TRTP as set forth in the Habitat Mitigation and Monitoring Plan (ICF, 2014) prepared as required under mitigation measures Bio-1a,1b and 1c of the EIR. | Environmental | Restoration | SP-67 | Other - See Notes | Environmental | N/A | NA | Performed all required analysis per permit | Robust alternative analysis conducted and included in the Environmental Impact Report (EIR) | Non-HFRA/Non-HFRA | See Note 16C | High Wind Events, High Fire Area, Extreme Temperature Conditions | Brent Gokbudak, MPO-Project Development & Execution | See Note 19B | See Note 20B | See Note 21A | See Note 22A | See Note 23B | 903216565 | CET-ET-TP-RN-643902 | 6439 | See Note 27A | Yes | 2014 | 2021 | Other- See Notes | No | N/A | N/A | N/A | Not Yet Operational | Not Yet Operational | Final Certified | EIR | CPUC | N/A- See Notes | N/A- See Notes | Approved | 2014 | Engineering more than 50% completed | See Note 46A | 2024-04-05 | No | 2024-12-31 | 2025-12-31 | Change is due to a decision Jan 2022 by the USFS to require 5 years monitoring of plants installed in 2022 in place of the 10 year requirement to monitor trees planted in 2020. | 400053 | 399925.5451 | See Note 53A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216.7077 | -216.7077 | 0 | -1.4552e-14 | See Note 57A | N/A | See Note 59A | 4.8786e-14 | Return on Equity (ROE) Adder, Abandoned Plant & CWIP Incentives (121 FERC ¶ 61,168) | 100% | 0% | Column 1: Environmental capital restoration/ remediation required as part of project licensure; therefore several fields are not applicable to this type of work Column 3: Start and end point of segment Column 9: Habitat Restoration Column 19 & 21: Project is related to environmental restoration, not directly related to the Transmission line project Column 31: Habitat Restoration Plan Column 41: Condition of CPUC Licensing process, no separate approval required Column 52: Source= PMWIF (v7 Proj Summary) Column 53: The maximum and reasonable prudent cost established in the Certificate of Public Convenience and Necessity pursuant to California Public Utilities Code Section 1005.5 (a) for this project, includes, but is not limited to: (1) $746 million (2008$) as noted in D.09-09-033 dated September 24, 2009 and issued on September 28, 2009, which amended D.07-03-012 and D.07-03-045 (For Segments 1-3); and (2) $1,522.92 million, excluding AFUDC which is estimated at $261.82 million for a total estimated project cost of $1,784.74 Million (2009$) as noted in CPUC Decision 09-12-044 dated December 17, 2009, and issued on December 24, 2009 (Segments 4-11); (3) the addition of $32.95 million (2013$), including Contracting Termination Charges, as noted in CPUC Decision D13-02-035 dated July 28, 2013 and issued on March 6, 2013 (for studies related to the feasibility of undergrounding Segment 8A); (4) the addition of $224 million (2013$) as noted in the CPUC Decision D13-07-018 dated July 11, 2013 and issued on July 16, 2013 (undergrounding of Segment 8A); and (5) the addition of $23 million (2013$) as noted in CPUC Decision D14-01-005 dated January 16, 2014 and issued on January 14, 2014 (the inclusion of voltage control equipment for UG5), as well as any adjustments to these amounts made in any of the Petitions for Modification filed in A.07-06-031 and any related dockets associated with the project. Further, as referenced above, these amounts are in different year nominal dollars and would need to be placed in current year dollars to determine the actual cost for the project
TPP | SP-69 | TRTP Seg 8A CHUG | 33.97, -117.774/ 33.987, -117.714 | Chino Hills, San Bernardino County | Replacement of impacted trees and habitat resources impacted during construction of the TRTP as set forth in the Habitat Mitigation and Monitoring Plan (ICF, 2014) prepared as required under mitigation measures Bio-1a,1b and 1c of the EIR. | Environmental | Restoration | None | Other - See Notes | Environmental | N/A | NA | Performed all required analysis per permit | Robust alternative analysis conducted and included in the Environmental Impact Report (EIR) | Tier 3/ Non-HFRA | See Note 16C | High Seismic | Brent Gokbudak, MPO-Project Development & Execution | See Note 19B | See Note 20B | See Note 21A | 500kV | See Note 23B | 4 separate WOs | 2 separate CWBS | 7553 | See Note 27A | Yes | 2014 | 2021 | Other- See Notes | No | N/A | N/A | N/A | Not Yet Operational | Not Yet Operational | Final Certified | EIR | CPUC | N/A- See Notes | N/A- See Notes | Approved | 2014 | Construction (50%) | See Note 46A | 2016 | No | 2025-12-31 | 2027-12-29 | The Initial In-service date did not account for the additional remediation activities needed for the CHUG | 82471 | 82145.1749 | See Note 53A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 227.4169 | -227.4169 | 0 | 0 | See Note 57A | N/A | See Note 59A | 0 | Return on Equity (ROE) Adder, Abandoned Plant & CWIP Incentives (121 FERC ¶ 61,168) | 100% | 0% | Column 1: Environmental capital restoration/ remediation required as part of project licensure; therefore several fields are not applicable to this type of work Column 3: Start and end point for segment Column 9: Habitat Restoration Column 19 & 21: Project is related to environmental restoration, not directly related to the Transmission line project Column 31: Habitat Restoration Plan Column 41: Condition of CPUC Licensing process, no separate approval required Column 53: The maximum and reasonable prudent cost established in the Certificate of Public Convenience and Necessity pursuant to California Public Utilities Code Section 1005.5 (a) for this project, includes, but is not limited to: (1) $746 million (2008$) as noted in D.09-09-033 dated September 24, 2009 and issued on September 28, 2009, which amended D.07-03-012 and D.07-03-045 (For Segments 1-3); and (2) $1,522.92 million, excluding AFUDC which is estimated at $261.82 million for a total estimated project cost of $1,784.74 Million (2009$) as noted in CPUC Decision 09-12-044 dated December 17, 2009, and issued on December 24, 2009 (Segments 4-11); (3) the addition of $32.95 million (2013$), including Contracting Termination Charges, as noted in CPUC Decision D13-02-035 dated July 28, 2013 and issued on March 6, 2013 (for studies related to the feasibility of undergrounding Segment 8A); (4) the addition of $224 million (2013$) as noted in the CPUC Decision D13-07-018 dated July 11, 2013 and issued on July 16, 2013 (undergrounding of Segment 8A); and (5) the addition of $23 million (2013$) as noted in CPUC Decision D14-01-005 dated January 16, 2014 and issued on January 14, 2014 (the inclusion of voltage control equipment for UG5), as well as any adjustments to these amounts made in any of the Petitions for Modification filed in A.07-06-031 and any related dockets associated with the project. Further, as referenced above, these amounts are in different year nominal dollars and would need to be placed in current year dollars to determine the actual cost for the project Column 52: Source= PMWIF (v6 Proj Summary); Represents PIN level estimate
GIDAP | SP-70 | Techren Solar RNU (TOT809_Q1339) | 35.798084, -115.006503 | Boulder City, Clark County, Nevada | To interconnect Techren Solar LLC's Techren Solar 300 MW Energy Storage-Battery/Solar PV generating facility to SCE's transmission system; RNU includes: 1) SCE-owned Eldorado 220kV substation 2) Add generator to Ivanpah RAS 3) Add generator to Lugo-Victorville RAS | Reliability Network Upgrade | New | SP-72 | Work Requested by Others | GIDAP (Generation Interconnection) | N/A | N/A - New | Power Flow, Transient, Post Transient, Short Circuit Duty | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Out of State | See Note 16C | High Wind Events, Extreme Temperature Conditions | Brent Gokbudak, MPO-Project Development & Execution | See Note 19B | Eldorado Sub: 86.7 (SCE does not own Harry Allen Sub) | See note 21A | See Note 22A | See Note 23B | 902460358 | CET-ET-TP-RN-817100 | 8171 | See Note 27A | Yes | 2018 | 2021 | LGIA | 2016 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Pre-construction | See Note 46A | 2024-01-08 | No | 2021-03-13 | 2024-07-23 | Customer requested project on hold (resumed in 2021) and delays/coordination of other projects in the area (ELM and other compliance/reliability projects) | 8571 | 1674.7392 | See Note 53A | 3648.1006 | 1787 | 477 | 333 | 0 | 0 | 0 | 2597 | 2.6832 | 0.07206 | 0 | 136.8179 | 911.5273 | 1051.1006 | 186.8099 | See Note 57A | 100% | See Note 59A | 1051.1006 | None | 100% | 0% | Column 9: GIDAP (Generator Interconnection) Column 52 Source= PMWIF (v1 Proj Summary); Represents PIN level estimate
N/A | SP-71 | El Nido/El Segundo CRAS RGOOSE Conversion | Various Locations | Hawthorne/ Ladera Heights/ Torrance, Los Angeles County | Upgrade the existing El Nido/El Segundo Centralized Remedial Action Scheme to accommodate IEC 61850 90-5 telecommunications protocol. | Replace power supply, CPU module, frame and front cover of 20 CRAS relays at four SCE substations. | New | SP-71 | Other - See Notes | Special Protection Scheme | N/A | N/A | No alts - modernize RAS telecom infrastructure in compliance with WECC criteria | No alts - modernize RAS telecom infrastructure in compliance with WECC criteria | Non-HFRA/Tier 2 | See Note 16C | No significant environmental factors | Demetric Brown, MPO - Programs | See Note 19B | This project occurs at various sites. | See Note 21A | 220kV | See Note 23B | 4 separate WOs | 4 separate CWBS | 8278 | See Note 27A | Yes | 2020 | 2019 | Annual Capital Operating Plan Process | No | N/a | N/a | N/a | See Col. 37 | 2022 = 765 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2021-08-30 | Yes | 2021-12-31 | 2022-03-06 | N/A | 7303 | 7303 | See Note 53A | 764.5351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.6037 | 429.758 | 320.1733 | 764.5351 | 255.7798 | See Note 57A | N/A | See Note 59A | 2.326e-13 | None | 100% | 0% | Column 9: Generator Interconnection Column 4: El Nido, El Segundo, La Cienega, and La Fresa substations Column 52: Source= PMWIF (v1 Proj Summary); Represents PIN level estimate
N/A | SP-72 | Lugo-Victorville Centralized RAS | Various Locations | Project area spans western Nevada and eastern California; bounded by cities of Bullhead City to the northeast, Boulder City to the southeast, and Mountain Pass to the west. | Implement in SCE's Centralized Remedial Action Scheme (CRAS) platform a special protection system to accommodate generation in the eastern Mojave Desert near the CA/NV border. Monitors for outages of 500 kV transmission lines linking Eldorado, Lugo, and Mohave Substations and trips generation at Ivanpah, Merchant, Primm, and Valley (VEA) Substations. Project is scalable and will evolve as needed to include future generation projects at other points of interconnection in the area. This is a protection/IT project consisting of protective relays, telecom network circuits and terminal equipment, and central processing architecture at GCC and IOC. Protects 500 kV transmission lines from overloads caused by existing and future generation projects in the area. | Multiple relays for line outage monitoring and generator tripping; telecom circuits and terminal equipment | New | SP-70, SP-72, SP-78, SP-96, SP-112, SP-114, SP-115 | Other - See Notes | Special Protection Scheme | N/A | N/A | Load Flow, Dynamic Stability | N/A - Project uses latest SCE standard CRAS platform to implement standard mitigation for generation interconnections; transmission alternative is known to be orders of magnitude higher in cost, much faster to implement, and not subject to extensive siting, environmental, and licensing requirements of transmission expansion. | Spans multiple zones | See Note 16C | Extreme Temperature Conditions | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | This project occurs at various sites. | See Note 21A | 500 kV, 220KV | See Note 23B | 7 separate WOs/ Elements | 3 separate CWBS | 8345 | See Note 27A | Yes | 2020 | 2021 | Annual Capital Operating Plan Process | No | N/a | N/a | N/a | Not Yet Operational | Not Yet Operational | TBD | TBD | CDFW/BLM | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Engineering less than 50% completed | See Note 46A | 2025-01-02 | No | 2024-06-30 | 2025-03-13 | Project On Hold and OD Deferral | 40582 | 20950.2584 | See Note 53A | 13996.8627 | 400 | 2683 | 5854 | 4743 | 0 | 0 | 13680 | 0 | 0 | 0 | 155.9389 | 160.9238 | 316.8627 | 132.0726 | See Note 57A | N/A | See Note 59A | 315.7792 | None | 100% | 0% | Column 9: Generator Interconnection Column 52: Source= PMWIF (v0 Proj Summary); Represents PIN level estimate
N/A | SP-73 | North of Lugo Centralized RAS (NoL CRAS)11225 | Various Locations | Project area is in the northwest Mojave Desert; bounded by cities of Hesperia to the south, Inyokern to the north, US 395 to the west, and Newberry Springs to the east. | Implement in SCE's Centralized Remedial Action Scheme (CRAS) platform a special protection system to accommodate generation in the northern Mojave Desert Area. Monitors for outages of 500/230 kV transformer banks, 500 kV, 230 kV, and 115 kV transmission lines linking multiple SCE Substations and trips generation at numerous points of interconnection in the area. Project is scalable and will evolve as needed to include future generation projects in the region. This is a protection/IT project consisting of protective relays, telecom network circuits and terminal equipment, and central processing architecture at GCC and IOC. Protects SCE facilities from overloads and dynamic instability caused by existing and future generation connected to the SCE grid. | Multiple relays for line and transformer outage monitoring and generator tripping; telecom circuits and terminal equipment | New | SP-01, SP-35, SP-40, SP-41, SP-45, SP48, SP-51, SP-54, SP-57, SP-62, SP-64, SP-65, SP-73, SP-82, SP-86, SP-93, SP-95, SP-116 | Other - See Notes | Special Protection Scheme | N/A | N/A | Load Flow, Dynamic Stability | N/A - Project uses latest SCE standard CRAS platform to implement standard mitigation for generation interconnections; transmission alternative is known to be orders of magnitude higher in cost, much faster to implement, and not subject to extensive siting, environmental, and licensing requirements of transmission expansion. | Spans multiple zones | See Note 16C | Extreme Temperature Conditions | Brent Gokbudak, MPO-Project Development & Execution | See Note 19B | This project occurs at various sites. | See Note 21A | 500 kV, 220 kV, 115 kV | See Note 23B | 14 separate WOs/ Elements | 9 separate CWBS | 8350 | See Note 27A | Yes | 2020 | 2021 | Annual Capital Operating Plan Process | No | N/a | N/a | N/a | Not Yet Operational | Not Yet Operational | TBD | TBD | TBD | TBD | TBD | TBD | N/A | Engineering more than 50% completed | See Note 46A | 2025-10-03 | No | 2024-06-30 | 2027-03-10 | Coordination of work with other projects in the area | 44746 | 29205.2175 | See Note 53A | 20593.8382 | 346 | 390 | 390 | 7108 | 7127 | 4913.85 | 20274.85 | 0 | 0 | 0 | 99.1699 | 219.8182 | 318.9882 | 126.5499 | See Note 57A | N/A | See Note 59A | 318.9882 | None | 100% | 0% | Column 9: Generator Interconnection Column 52: Source= PMWIF (v0 Proj Summary); Represents PIN level estimate
GIDAP | SP-74 | Whirlwind Substation Expansion: AV Solar 1 / Solar Ranch RNU (TOT345_Q412) | 34.761854, -118.316498 | Lancaster, Los Angeles County | To interconnect Solar Ranch 1's AV Solar 250 MW PV generating facility to SCE's Whirlwind sub; RNU includes: 1. Whirlwind Substation: The Participating TO shall: Equip one 220 kV position at Whirlwind Substation to terminate the generation tie-line. Install the following equipment at the 220 kV Switchyard: a. Two 3000A – 63kA circuit breakers b. Four 3000A – 80kA horizontal-mounted group-operated disconnect switches c. One grounding switch attachment (for lines grounding) d. Eighteen bus supports with associated steel pedestals 2. Other Reliability Network Upgrades: The Participating TO shall: a. Install a Whirlwind AA-bank N-1 SPS b. Install a Whirlwind 220 kV bus extension c. Install short-circuit duty (“SCD”) mitigation: Replace seven circuit breakers and upgrade four circuit breakers to achieve 63 kA rating on overstressed Vincent 500 kV circuit breakers. d. Power System Controls: Add points at Whirlwind Substation and upgrade existing RTU. | Reliability Network Upgrade | New/Upgrade | None | Work Requested by Others | GIDAP (Generation Interconnection) | N/A | N/A new | Power Flow, Transient, Post Transient, Short Circuit Duty | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Non-HFRA | See Note 16C | High Wind Events, Extreme Temperature Conditions | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | 92 | See note 21A | See Note 22A | See Note 23B | 4 separate WOs | 4 separate CWBS | 7054 | See Note 27A | Yes | 2010 | Pre-2017 | LGIA | 2006 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | See Col. 37 | 2012 = 2,706 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2011-01-20 | No | 2012-09-01 | 2012-11-03 | Not readily available | 8608 | 1434.7333 | See Note 53A | 2705.5986 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 2705.5986 | 0 | 0 | 0 | 0 | 2705.5986 | 214.7904 | See Note 57A | 100% | See Note 59A | 2.0304e-12 | Abandoned Plant & CWIP Incentives (134 FERC ¶ 61,181) | 100% | 0% | Column 9: GIDAP (Generator Interconnection) Column 52: Source= PMWIF (v7 Proj Summary); Represents PIN level estimate
GIDAP | SP-75 | Antelope Valley Solar PV 2 RNU (TOT340_Q407) | 34.862419, -118.428386 | Rosamond, Kern County | To interconnect Solar Start California's Antelope Valley Solar PV1 310MW PV generating facility to SCE's Whirlwind substation; RNU includes: 1. Whirlwind Substation: The Participating TO shall: Equip one 220 kV position at Whirlwind Substation to terminate the Generation-Tie-line. Install the following equipment at the 220 kV Switchyard: a. Two 4000A – 63kA circuit breakers b. Four 4000A – 80kA horizontal-mounted group-operated disconnect switches c. One grounding switch attachment (for lines grounding) d. Eighteen bus supports with associated steel RNU in pedestals e. Power System Controls: Expand existing Whirlwind RTU to install additional points required for the AVSP1-Whirlwind 220 kV Generation-Tie Line position. 2. Other Reliability Network Upgrades: The Participating TO shall: a. Install a Whirlwind 220 kV bus extension b. Install a Whirlwind AA-bank N-1 SPS when both the Whirlwind No.3 & No.4 AA-Banks are placed into service and sufficient resources exist to warrant need for the SPS c. Install short-circuit duty (“SCD”) mitigation at Whirlwind | Reliability Network Upgrade | New/Upgrade | None | Work Requested by Others | GIDAP (Generation Interconnection) | N/A | N/A new | Power Flow, Transient, Post Transient, Short Circuit Duty | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Non-HFRA | See Note 16C | High Wind Events, Extreme Temperature Conditions | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | 92 | See note 21A | See Note 22A | See Note 23B | 4 separate WOs | 4 separate CWBS | 7068 | See Note 27A | Yes | 2011 | Pre-2017 | LGIA | 2009 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | See Col. 37 | 2013 = 1,863 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2011-12-31 | No | 2014-01-01 | 2013-09-19 | Project On Hold | 5606 | 2459 | See Note 53A | 1862.5018 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 1862.5018 | 0 | 0 | 0 | 0 | 1862.5018 | 215.569 | See Note 57A | 100% | See Note 59A | 3.5081e-12 | None | 100% | 0% | Col 52.1 was updated per Dec 2021 Data Request responses. Column 9: GIDAP (Generator Interconnection) Column 52: Source= PMWIF (v0 Proj Summary);PIN level estimate
GIDAP | SP-76 | Antelope Valley Solar PV 2 RNU (TOT341_Q408) | 34.74739, -118.369249 | Rosamond, Kern County | To interconnect Solar Star California's Antelope Valley Solar PV 2 276 MW generating facility to SCE's Whirlwind sub system.; RNU includes: Equip one 220kV position at Whirlwind sub to terminate at Generation-Tie-Line; a. Two 3000A – 63kA circuit breakers b. Four 3000A – 80kA horizontal-mounted group-operated disconnect switches c. One grounding switch attachment (for lines grounding) d. Eighteen bus supports with associated steel pedestals e. Power System Controls: Expand existing Whirlwind RTU to install additional points required for the AVSP 2-Whirlwind 220 kV Generation-Tie Line position. Other RNUs: a. Install a Whirlwind 220 kV bus extension b. Install a Whirlwind AA-bank N-1 SPS when both the Whirlwind No.3 & No.4 AA-Banks are placed into service and sufficient resources exist to warrant need for the SPS c. Install short-circuit duty (“SCD”) mitigation at Whirlwind: d. Replace seven circuit breakers and upgrade four circuit breakers to achieve 63 kA rating on overstressed Vincent 500 kV circuit breakers when duty capabilities of these breakers are identified to be exceeded. | Reliability Network Upgrade | New/Upgrade | None | Work Requested by Others | GIDAP (Generation Interconnection) | N/A | N/A new | Power Flow, Transient, Post Transient, Short Circuit Duty | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Non-HFRA | See Note 16C | High Wind Events, Extreme Temperature Conditions | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | 92 | See note 21A | See Note 22A | See Note 23B | 4 separate WOs | 4 separate CWBS | 7069 | See Note 27A | Yes | 2011 | Pre-2017 | LGIA | 2015 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | See Col. 37 | 2013 = 1,718 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2012-01-05 | No | 2014-01-01 | 2013-09-19 | N/A | 5328 | 2380 | See Note 53A | 1717.934 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 1717.934 | 0 | 0 | 0 | 0 | 1717.934 | 179.8118 | See Note 57A | 100% | See Note 59A | 8.5874e-13 | None | 100% | 0% | Col 52.1 was updated per Dec 2021 Data Request responses. Column 9: GIDAP (Generator Interconnection) Column 52: Source= PMWIF (v0 Proj Summary);PIN level estimate
GIDAP | SP-77 | Soleil Solar Project (Formerly Catalina Solar Project) RNU (TOT455_Q602) | 34.951085 -118.242136 | Rosamond, Kern County | To interconnect Catalina Solar's Soleil Solar 18 MW PV generating facility to SCE's Whirlwind sub 220 kv bus; RNU includes: Expand Northern Area 500 SPS a. Antelope Substation SPS Central Processing Location (i) Install three N60 relays for each SPS A and SPS B (total of six relays) for line monitoring, logic processing and sending of generator tripping signals (ii) Install one SEL-2407 satellite synchronized clock b. Vincent Substation (i) Install two N60 relays for each SPS A and SPS B (total of four relays) for line monitoring (ii) Install one SEL-2407 satellite synchronized clock c. Whirlwind Substation (i) Install two N60 relays for each SPS A and SPS B (total of four relays) for line monitoring (ii) Install one SEL-2407 satellite synchronized clock d. Windhub Substation (i) Install one N60 relay for each SPS A and SPS B (total of two relays) for line monitoring (ii) Install one SEL-2407 satellite synchronized clock e. Telecommunications (i) Telecomm Channels - Use existing infrastructure to provide two diversely routed telecommunication channels. (ii) Equipment - Install all required light-wave, channel and related terminal equipment at the Antelope, Vincent, Whirlwind, and Windhub Substations and the Alhambra Communications Site to provide the required interface between the existing channels and the SPS relays. f. Power System Control Expand existing RTU’s at Antelope Substation to support the SPS. Expand Whirlwind Special Protection System; Wave Trap Replacements; and implementation of Short-Circuit Duty Mitigation. | Reliability Network Upgrade | New/Upgrade | None | Work Requested by Others | GIDAP (Generation Interconnection) | N/A | N/A new | Power Flow, Transient, Post Transient, Short Circuit Duty | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Non-HFRA | See Note 16C | No significant environmental factors | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | 92 | See note 21A | See Note 22A | See Note 23B | 2 separate WOs | 2 separate CWBS | 7245 | See Note 27A | Yes | 2011 | Pre-2017 | LGIA | 2014 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | See Col. 37 | 2019 = 0 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2017-02-08 | No | 2012-10-01 | 2019-03-13 | Not readily available | 119 | Not readily available | See Note 53A | 0 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 0 | 0 | 0 | 0 | 0 | 0 | 0 | See Note 57A | 100% | See Note 59A | 0 | None | 100% | 0% | Column 9: GIDAP (Generator Interconnection) Column 52: Source= PMWIF (v1 Proj Summary); Represents PIN level estimate Column 52.1: FERC % not yet available in source file; will be updated in future SRP once available
GIDAP | SP-78 | North Rosamond Solar RNU (TOT497_Q643R) | 34.863, -118.377 | Rosamond, Kern County | To interconnect North Rosamond Solar PV generating facility to SCE's Whirlwind sub 230 kV bus; RNU includes: Short Circuit duty upgrades to CBs at Vincent Substation; Expand Northern area 500 kV RAS; Expand Whirlwind RAS; 1. Plan of Service Reliability Network Upgrades. a. Whirlwind Substation. Equip one (1) 220 kV position at Whirlwind Substation to terminate the Rattlesnake-Whirlwind 220kV Transmission Line with the following Network Upgrades (plan of service): • Two (2) 3000A – 63 kA 220 kV circuit breakers • Four (4) 3000A – 80 kA horizontal –mounted group-operated disconnect switches • One (1) grounding switch attachment • 2-1590 KCMIL ACSR conductors as required • Two (2) G.E. C60 breaker management relays (breaker failure) b. Power System Controls. Expand the Whirlwind Substation RTU to provide additional points required for the Rattlesnake-Whirlwind 220kV Transmission Line position. c. Corporate Environmental Services Perform all required environmental activities to support the plan of service Participating TO’s Reliability Network Upgrades. | Reliability Network Upgrade | New/Upgrade | SP-72 | Work Requested by Others | GIDAP (Generation Interconnection) | N/A | N/A new | Power Flow, Transient, Post Transient, Short Circuit Duty | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Non-HFRA | See Note 16C | High Wind Events, Extreme Temperature Conditions | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | 92 | See note 21A | See Note 22A | See Note 23B | 4 separate WOs | 4 separate CWBS | 7756 | See Note 27A | Yes | 2014 | Pre-2017 | LGIA | 2014 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | See Col. 37 | 2018 = 3,375 2019 = 388 2020 = 59 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2017-10-23 | No | 2016-11-01 | 2018-11-14 | Change of Customer COD | 9416 | 2834.5471 | See Note 53A | 3820.9646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3374.8292 | 387.6024 | 58.5329 | 0 | 0 | 3820.9646 | 778.7361 | See Note 57A | 100% | See Note 59A | -3.0682e-13 | None | 100% | 0% | Column 9: GIDAP (Generator Interconnection) Column 52: Source= PMWIF (v0 Proj Summary);PIN level estimate
GIDAP | SP-79 | Willow Springs 2 RNU (TOT494_Q643AJ) | 34.86576, -118.21547 | Rosamond, Kern County | To interconnect Willow Springs Solar 2 PV generating facility to SCE's Whirlwind 220 kV line; RNU includes: a. Whirlwind Substation. Equip one (1) 220 kV position at Whirlwind Substation to terminate the Desert Flower-Whirlwind 220kV Transmission Line with the following Network Upgrades (plan of service): • Two (2) 3000A – 63 kA 220 kV circuit breakers • Four (4) 3000A – 80 kA horizontal–mounted group-operated disconnect switches • One (1) grounding switch attachment • 2-1590 KCMIL ACSR conductors as required • Two (2) G.E. C60 breaker management relays (breaker failure) b. Power System Controls. Expand the Whirlwind Substation RTU to provide additional points required for the Project’s 220 kV generation tie-line position. Expanse the Whirlwind AA bank SPS and the Northern Ara SPS; Install new 500 kV MVAR capacitor bank on the existing 500 kV bus; Add new points to RTU to support the additional of the capacitor bank; and Upgrade transmission network circuit breakers (pro-rata share of upgrade based on project contribution to short circuit duty at each location). | Reliability Network Upgrade | New/Upgrade | None | Work Requested by Others | GIDAP (Generation Interconnection) | N/A | N/A new | Power Flow, Transient, Post Transient, Short Circuit Duty | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Non-HFRA | See Note 16C | High Wind Events, Extreme Temperature Conditions | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | 92 | See note 21A | See Note 22A | See Note 23B | 4 separate WOs | 4 separate CWBS | 7775 | See Note 27A | Yes | 2015 | 2017 | LGIA | 2016 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | See Col. 37 | 2017 = 36 2018 = 48 2019 = 38 2020 = 15 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2018-10-01 | No | 2017-12-31 | 2019-01-31 | Not readily available | 10808 | 2516 | See Note 53A | 138.3808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.6355 | 38.4154 | 15.3299 | 0 | 0 | 138.3808 | 26.6208 | See Note 57A | 100% | See Note 59A | 5.3115e-14 | None | 100% | 0% | Col 52.1 was updated per Dec 2021 Data Request responses Column 9: GIDAP (Generator Interconnection) Column 52: Source= PMWIF (v0 Proj Summary);PIN level estimate
GIDAP | SP-80 | Gaskell West RNU (TOT727_Q1074) | 34.83282, -118.519275 | Rosamond, Kern County | To interconnect RE Gaskell West generating facility to SCE's Whirlwind 220 kv bus; RNU includes: shared RNU between the Gaskell West Project, TOT573 Project, and TOT672 project; Expand Whirlwind AA-Bank SPS and Northern Area SPS by installing G.E. N60 logic processing relays or equivalent successor to send additional tripping signals to the generation projects, and expanding existing RTU at Whirlwind sub to include points for status and alarms related to the new SPS relays and modify the programs of the planned north area SPS. | Reliability Network Upgrade | New/Upgrade | None | Work Requested by Others | GIDAP (Generation Interconnection) | N/A | N/A new | Power Flow, Transient, Post Transient, Short Circuit Duty | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Non-HFRA | See Note 16C | No significant environmental factors | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | 92 | See note 21A | See Note 22A | See Note 23B | 2 separate WOs | 2 separate CWBS | 7911 | See Note 27A | Yes | 2019 | Pre-2017 | LGIA | 2014 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | See Col. 37 | 2022 = 56 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2018-04-17 | No | 2018-05-28 | 2020-10-19 | Additional Phases | 523 | Not readily available | See Note 53A | 56.2622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.30962 | 55.9526 | 56.2622 | 14.5135 | See Note 57A | 100% | See Note 59A | 56.2622 | None | 100% | 0% | Column 9: GIDAP (Generator Interconnection) Column 52: Source= PMWIF (v0 Proj Summary); Represents PIN level estimate Column 52.1: FERC % not yet available in source file; will be updated in future SRP once available
GIDAP | SP-81 | Rosamond West Solar RNU (TOT411_Q506) | 34.86576, -118.21547 | Rosamond, Kern County | To interconnect Solar Star California's 300 MW Rosamond West Solar generating facility to SCE's Whirlwind 220 kV bus; RNU includes: equip one 220kV position at Whirlwind sub to terminate the Teddy-Whirlwind 220kV Transmission Line; Expand existing Whirlwind RTU to install additional points required for the Teddy-Whirlwind 220kV Transmission Line position; perform required environment activities associated with the equipping of the 220 kV position at Whirlwind sub; Expanse Northern Area 500kV SPS; and Expand Whirlwind SPS. | Reliability Network Upgrade | New/Upgrade | None | Work Requested by Others | GIDAP (Generation Interconnection) | N/A | N/A new | Power Flow, Transient, Post Transient, Short Circuit Duty | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Non-HFRA | See Note 16C | High Wind Events, Extreme Temperature Conditions | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | 92 | See note 21A | See Note 22A | See Note 23B | 4 separate WOs | 4 separate CWBS | 7733 | See Note 27A | Yes | 2014 | Pre-2017 | LGIA | 2009 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | See Col. 37 | 2020 = 2,860 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2019-12-27 | No | 2016-11-01 | 2020-09-01 | Additional Phases | 6149 | 4096.7924 | See Note 53A | 2860.0621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2511.8995 | 348.1626 | 0 | 0 | 0 | 2860.0621 | 874.195 | See Note 57A | 100% | See Note 59A | 4.929e-13 | None | 100% | 0% | Column 9: GIDAP (Generator Interconnection) Column 52: Source= PMWIF (v1 Proj Summary); Represents PIN level estimate
GIDAP | SP-82 | Stage Coach Solar RNU (TOT640_Q897) | 34.5467, -116.9483 | Lucerne Valley, San Bernardino County | To interconnect Aurora Solar LLA's proposed 200 MW Stage Coach Solar generating facility to SCE's Calcite 220kV substation; RNU includes: Calcite sub: install all necessary equipment including 220kV position at Calcite sub to terminate at Calcite-Sorrel 220kV line with the following NU: 63kA 220 kV CBs, 80 kA horizontal-mounted group operated disconnect switches, grounding switch attachment, 1590 KCMIL aluminum-conductor-steel reinforced (ACSR) conductors, C60 breaker management relays, and 220kV bus supports with associated steel pedestals; Power System Controls to expand Calcite sub RTU to provide additional points required for the Calcite-Sorrel 220kV line position; Real Properties, Transmission Project Licensing, and Corporate Environmental services; Calcite SPS; and High Desert Power Plant SPS . | Reliability Network Upgrade | New/Upgrade | None | Work Requested by Others | GIDAP (Generation Interconnection) | N/A new | N/A new | Power Flow, Transient, Post Transient, Short Circuit Duty | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Tier 2 | See Note 16C | Extreme Temperature Conditions | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | 10 | See note 21A | See Note 22A | See Note 23B | 8 separate WOs/ Elements | 1 separate CWBS | 7902 | See Note 27A | Yes | 2016 | 2021 | LGIA | 2012 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | Not Yet Operational | Not Yet Operational | Expected EIR 2024 | EIR | State Lands Commission | PTC Expected | Not yet filed 2023 | N/A | N/A | Planning | See Note 46A | 2025-01-06 | No | 2023-09-01 | 2026-06-30 | Customer requested project on hold | 8084 | 3113 | See Note 53A | 2635.4785 | 10 | 25.196 | 2588.427 | 0 | 0 | 0 | 2623.623 | 0 | 0 | 0 | 8.19 | 3.6655 | 11.8555 | 5.8598 | See Note 57A | 100% | See Note 59A | 11.8555 | None | 100% | 0% | Col 52.1 was updated per Dec 2021 Data Request responses. Column 9: GIDAP (Generator Interconnection) Column 52: Source= PMWIF (v4 Proj Summary); Represents PIN level estimate
GIDAP | SP-83 | Rexford Solar Farm RNU (TOT896_Q1516) | 35.841276, -119.071222 | Ducor, Tulare County | To interconnect 20SD 8ME's Rexford Solar Farm generating facility to SCE's Vestal 220/66kV system; RNU includes: utilize one 220kV line position, install two 220 kV transmission line positions required for the line relocations, extend the 220kV bus required for the line relocations, remove one 220kV line position required for the line relocations, and conduct grid study; add points to the existing RTU at Vestal sub; Real Properties; Environmental activities, permits, and licensing. General RNU includes: Big Creek/San Joaquin RAS - Generating Addition; Power System Controls; and install corporate security approved cabinets/cameras/other security measures to monitor and protect SCE assets per compliance standards at Rector substation. | Reliability Network Upgrade | New/Upgrade | None | Work Requested by Others | GIDAP (Generation Interconnection) | N/A | N/A new | Power Flow, Transient, Post Transient, Short Circuit Duty | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Non-HFRA | See Note 16C | No significant environmental factors | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | 12.7 | See note 21A | See Note 22A | See Note 23B | 7 separate WOs | 7 separate CWBS | 8320 | See Note 27A | Yes | 2020 | 2021 | LGIA | 2018 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Construction less than 50% completed | See Note 46A | 2023-07-17 | No | 2022-10-15 | 2024-03-29 | Scope Change | 21509 | Not readily available | See Note 53A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | See Note 57A | 100% | See Note 59A | 0 | None | 100% | 0% | Column 9: GIDAP (Generator Interconnection) Column 52: Source= PMWIF (v1 Proj Summary); Represents PIN level estimate Column 52.1: FERC % not yet available in source file; will be updated in future SRP once available
GIDAP | SP-84 | Rosamond South East RNU (TOT753_Q1211) | 34.844786, -118.391535 | Rosamond, Kern County | To interconnect SunPower Corp's Rosamond South East generating facility to SCE's Whirlwind 220 kV sub at the 220 kV switchrack; RNU includes: Utilize 220kV line position which terminated the Teddy-Whirlwind gen-tie and utilize the existing 2 local breaker failure backup relays in support of the Teddy-Whirlwind 220 kV line; Power system controls; expand Whirlwind AA-Bank RAS; expand Tehachapi CRAS. | Reliability Network Upgrade | New/Upgrade | None | Work Requested by Others | GIDAP (Generation Interconnection) | 2023-10-09 | N/A new | Power Flow, Transient, Post Transient, Short Circuit Duty | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Non-HFRA | See Note 16C | No significant environmental factors | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | 92 | See note 21A | See Note 22A | See Note 23B | 903183397 | CET-ET-CR-WC-832200 | 8322 | See Note 27A | Yes | 2017 | 2021 | LGIA | 2015 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | TBD | TBD | TBD | N/A | Canceled | See Note 46A | 2024-04-23 | No | 2022-04-30 | Canceled | Customer Request | Not readily available | Not readily available | See Note 53A | 44.2226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.2226 | 44.2226 | 8.9743 | See Note 57A | 100% | See Note 59A | -266.1114 | None | 100% | 0% | Column 9: GIDAP (Generator Interconnection)
GIDAP | SP-85 | Sanborn Solar 2 RNU (TOT876_Q1581) | 34.941445, -118.107572 | Mojave, Kern County | To interconnect Terra-Gen Dev Company's Sanborn Solar 2 generating facility to SCE's Windhub 220 kV bus; RNU includes: Install one 22kV line position at Windhub sub including 2 CBs 1 group operated switch with grounding attachment; disconnect switches, and 14 bus support post insulators; Real Properties, environmental activities, permits, and licensing; general reliability Network upgrades which include: 1) Tehachapi cRAS - generator addition, 2) Windhub AA bank cRAS - monitoring infrastructure, 3) Windhub AA bank cRAS - generator addition, and 4) Short-Circuit Duty Mitigation. | Reliability Network Upgrade | New/Upgrade | None | Work Requested by Others | GIDAP (Generation Interconnection) | N/A | N/A new | Power Flow, Transient, Post Transient, Short Circuit Duty | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Non-HFRA | See Note 16C | High Wind Events, Extreme Temperature Conditions | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | 59.2 | See note 21A | See Note 22A | See Note 23B | 3 separate WOs | 3 separate CWBS | 8338 | See Note 27A | Yes | 2020 | 2021 | LGIA | 2018 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | See Col.37 | 2022 = 478 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2022-05-23 | Yes | 2022-08-01 | 2022-07-20 | N/A | 9121 | Not readily available | See Note 53A | 478.4212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.2173 | 436.2039 | 478.4212 | 70.2427 | See Note 57A | 100% | See Note 59A | 469.0535 | None | 100% | 0% | Column 9: GIDAP (Generator Interconnection) Column 52: Source= PMWIF (v1 Proj Summary); Represents PIN level estimate Column 52.1: FERC % not yet available in source file; will be updated in future SRP once available
GIDAP | SP-86 | Baldy Mesa 2 RNU (TOT882_Q1519) | 34.609137, -117.453663 | Adelanto, San Bernardino County | To interconnect Spower Development Company's Baldy Mesa 2 generating facility to SCE's Roadway 115kV substation at the 115kV bus; RNU includes: Mojave Desert RAS expansion; North of Lugo centralized RAS - generation addition; Roadway 115kV operating/transfer bus upgrade; short-circuit Duty (SCD) mitigation; real properties. | Reliability Network Upgrade | New/Upgrade | None | Work Requested by Others | GIDAP (Generation Interconnection) | N/A | N/A new | Power Flow, Transient, Post Transient, Short Circuit Duty | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Non-HFRA | See Note 16C | Extreme Temperature Conditions, High Wind Events, Air particulate levels | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | 1.9 | See note 21A | See Note 22A | See Note 23B | 6 separate WOs/ Elements | 5 separate CWBS | 8344 | See Note 27A | Yes | 2020 | 2021 | LGIA | 2018 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | Not Yet Operational | Not Yet Operational | TBD | TBD | TBD | TBD | TBD | TBD | N/A | Pre-Construction | See Note 46A | 2022-06-10 | No | 2022-10-15 | 2024-01-18 | Coordination with Other Work | 2878 | Not readily available | See Note 53A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | See Note 57A | 100% | See Note 59A | 0 | None | 100% | 0% | Column 9: GIDAP (Generator Interconnection) Column 52: Source= PMWIF (v0 Proj Summary); Represents PIN level estimate Column 52.1: FERC % not yet available in source file; will be updated in future SRP once available
TPP | SP-87 | Path 42 Upgrade | Various Locations | Riverside County & San Bernardino County | Install relays, meters and logic controllers as necessary associated with IID's new proposed SPS. Upgrade the following transmission lines post Devers-Coachella Valley Loop-in Project: Devers-Mirage #1 230kV T/L, Devers-Mirage #2 230kV T/L, SCE-owned portion of Mirage-Ramon #1 230kV T/L and SCE-owned portion of Mirage - Coachella Valley 230 kV T/L. | Substation Relay Installation | Replace/Upgrade | None | Capacity Increase | Substation Reliability | N/A | N/A | Bank Capacity, Power Flow, Short Circuit Duty, dynamic stability, SCE Subtransmission Planning Criteria and Guidelines | Project alternatives are discussed in Decision 16-18-017 chapter 6 | Non-HFRA | See Note 16C | High Wind Events, High Fire Area, Extreme Temperature Conditions, High Seismic | Demetric Brown, MPO - Programs | 15 | See Note 20B | 220kV | 220 kV | See Note 23B | 6 separate WOs | 6 separate CWBS | 6415 | See Note 27A | Yes | 2010 | Pre-2017 | FRM/CRT | 2011 | 2011 to present | N/A | ONLY 2012-2013 TPP available online http://www.caiso.com/Documents/BoardApproved2012-2013TransmissionPlan.pdf | See Col. 37 | 2014 = 6,168 2015 = 28,993 2016 = 1,378 2017 = -54 2018 = 2 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | Not Available | No | 2013-12-31 | 2016-10-20 | Customer (IID) caused delay due to uncompleted relay upgrades at their substation | 51448 | 51448 | See Note 53A | 36487.5135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36487.5135 | 0 | 0 | 0 | 0 | 36487.5135 | 6179.3427 | See Note 57A | N/A | See Note 59A | -4.1436e-11 | None | 100% | 0% | Column 52: Source= PMWIF (v6 Proj Summary); Represents PIN level estimate
TPP | SP-88 | Pardee-Sylmar No. 1 and No. 2 230 kV Lines Rating Increase | 34.4410, -118.5816 34.314, -118.493 | Los Angeles County | Upgrade CB's and terminal equipment at Pardee (SCE) and Sylmar (LADWP); Raise four towers for the Pardee-Sylmar No. 1 and No. 2 230 kV lines to match the emergency rating of the conductor (4360 Amps) | Substation; CBs 4172, 5172, 6172 and 4192, 5192, 6192 | Replace/Upgrade | None | Capacity Increase | System Design Upgrade | 2020-05-04 | 52 years | Bank Capacity, Power Flow, Short Circuit Duty, dynamic stability, SCE Subtransmission Planning Criteria and Guidelines | A new Pardee-Sylmar 230 kV Line: • Cost-ineffective: Requires Licensing and more expensive • Additional scope: Includes equipping a position at Pardee and Sylmar Substations • Coordination and Approval from LADWP | Tier 3/ Non-HFRA | See Note 16C | Minimal besides catastrophic environmental events that would impact physical security measures | Demetric Brown, MPO - Programs | See Note 19B | See Note 20B | See note 21A | 220kV | See Note 23B | 4 separate WOs/ Elements | 3 separate CWBS | 8294 | See Note 27A | Yes | 2020 | 2021 | Annual Capital Operating Plan Process | 2020 | 2020 to present | N/A | http://www.caiso.com/Documents/ISOBoardApproved-2019-2020TransmissionPlan.pdf | See Col.37 | 2023 = 2,669 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Construction less than 50% completed | See Note 46A | 2022-09-01 | No | 2023-06-01 | 2024-10-04 | Scope Change | 26269 | Not readily available | See Note 53A | 19034.5369 | 3817.323 | 1090 | 2000 | 5955.777 | 0 | 0 | 12863.1 | 0 | 0 | 17.711 | 249.5139 | 5904.212 | 6171.4369 | 665.9612 | See Note 57A | N/A | See Note 59A | 5731.432 | None | 100% | 0% | Column 52: Source= PMWIF (v1 Proj Summary); Represents PIN level estimate Column 52.1: FERC % not yet available in source file; will be updated in future SRP once available
GIDAP | SP-89 | Genesis McCoy Solar Project RNU (TOT223_Q193) | 33.6113, -114.6815 | Blythe, Riverside County | Genesis McCoy Solar Project is to interconnect NextEra Desert Center Blythe's generating facility to SCE's transmission system; 1. Terminate the Colorado River-Genesis McCoy 220kV Transmission Line (initially the RNU includes: Colorado River-Genesis 220kV Transmission Line) at Colorado River Substation; 2. Loop the Colorado River-Devers No.2 500kV Transmission Line into Red Bluff Substation; 3. Colorado River Substation Expansion – No. 1 AA-Bank: Expand the substation, presently configured as a 500kV switchyard, to a 1120MVA 500/220kV substation by installing one 1120MVA, 500/220kV transformer bank with corresponding 500kV and 220kV bank positions and installing a new 220kV switchyard; 4. Upgrade the Mira Loma-Vista No.2 220kV transmission Line drops at Vista Substation; 5. New SPS to trip up to 1,400 MW of generation under the Devers-Red Bluff No. 1 and No. 2 double contingency; 6. New SPS to trip up to 500 MW of generation connected to Colorado River Substation under either No. 1 AA or No. 2 AA transformer bank single contingency. | Reliability Network Upgrade | New/Upgrade | None | Work Requested by Others | GIDAP (Generation Interconnection) | N/A | N/A new | Power Flow, Transient, Post Transient, Short Circuit Duty | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Non-HFRA | See Note 16C | Extreme Temperature Conditions, High Seismic | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | 77 | See note 21A | See Note 22A | See Note 23B | 3 separate WOs | 3 separate CWBS | 7049 | See Note 27A | Yes | 2011 | Pre-2017 | LGIA | 2007 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | See Col. 37 | 2013 = 1,104 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | Not Available | No | 2013-11-08 | 2013-09-13 | N/A | 6055 | Not readily available | See Note 53A | 1191.3561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1191.3561 | 0 | 0 | 0 | 0 | 1191.3561 | 227.1711 | See Note 57A | 100% | See Note 59A | 1.6439e-12 | None | 100% | 0% | Column 9: GIDAP (Generator Interconnection) Column 52: Source= PMWIF (v1 Proj Summary); Represents PIN level estimate Column 52.1: FERC % not yet available in source file; will be updated in future SRP once available
GIDAP | SP-90 | Almasol Generating Station Project RNU (TOT 321_Q365) | 33.809041, -115.366577 | Desert Center, Riverside County | To interconnect Palen Solar II's Almasol generating station to SCE's transmission system; RNU includes: Terminate the Gen Tie-line at Red Bluff sub; loop the Colorado River-Devers No. 2 500 kV line into Red Bluff; expand the Colorado River sub; upgrade the Mira Loma-Vista No. 2 220kV line at Vista sub; new SPS to trip generation under simultaneous outage of the Devers-Red Bluff No. 1 and No. 2 500 kV lines; New SPS to trip generation connects to Colorado River sub under wither No. 1 or No. 2 AA transformer bank single contingency. | Reliability Network Upgrade | New/Upgrade/removal | None | Work Requested by Others | GIDAP (Generation Interconnection) | N/A | N/A new | Power Flow, Transient, Post Transient, Short Circuit Duty | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Non-HFRA | See Note 16C | Extreme Temperature Conditions, High Seismic | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | 75.7 | See note 21A | See Note 22A | See Note 23B | 900346247 | CET-ET-TP-RN-705900 | 7059 | See Note 27A | Yes | 2010 | Pre-2017 | LGIA | 2008 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | See Col. 37 | 2020 = 2,513 2021 = 372 2022 = 4 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2019-10-07 | No | 2013-10-01 | 2020-12-30 | Customer Request, Project Name and OD Change Per LGIA, Customer Coordination Issues | Not readily available | Not readily available | See Note 53A | 2889.1507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1403.931 | 591.634 | 517.768 | 372.2651 | 3.5526 | 2889.1507 | 854.5086 | See Note 57A | 100% | See Note 59A | 1.6343e-12 | None | 100% | 0% | Column 9: GIDAP (Generator Interconnection)
GIDAP | SP-91 | Alamitos Energy Center RNU (TOT840) | 33.7651, -118.2245 | Long Beach, Los Angeles County | The interconnection agreement involves the retirement of the customer's existing units 1-6 at its generating station located in Long Beach, and the interconnection of 3 new generation blocks; RNU includes: Install one (1) 220 kV line position (position 15); install one (1) 220 kV line position (position 4); install one (1) 220Kv line position (position 8); protection relays; environmental activities, permits, and licensing; RTU points at Alamitos sub. | Reliability Network Upgrade | New/Upgrade/removal | None | Work Requested by Others | GIDAP (Generation Interconnection) | N/A | N/A new | Power Flow, Transient, Post Transient, Short Circuit Duty | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Non-HFRA | See Note 16C | Salt Corrosion (Coastal Areas), Flooding, High Seismic | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | 22.5 | See note 21A | See Note 22A | See Note 23B | 902354956 | CET-ET-CR-WS-803904 | 8039 | See Note 27A | Yes | 2017 | 2017 | LGIA | 2012 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | See Col. 37 | 2020 = 1,737 2021 = 5 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2020-01-06 | No | 2020-04-01 | 2020-11-07 | Customer Outage Constraints | 6325 | Not readily available | See Note 53A | See Note | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | See Note | 0 | See Note 57A | 100% | See Note 59A | 0 | None | 100% | 0% | Column 9: GIDAP (Generator Interconnection) Column 52: Source= PMWIF (v1 Proj Summary)- Phase 2; Represents PIN level estimate for Phase 2 of project; WO level estimate is $3.112M Column 52.1: FERC % not yet available in source file; will be updated in future SRP once available Project was determined to be 100% customer-funded.
GIDAP | SP-92 | Sandstorm Wind Power Reliability Network Upgrades (RNU) (TOT185_Q138) | 33.91732, -116.73445 | San Bernardino, San Bernardino County | To interconnect Cabazon Wind Energy's 150 MW Sandstorm Wind Power generating station to SCE's transmission system; New loop-in Glimmer substation facility, including: Glimmer-Sandstorm 220 kV Transmission Line, environmental services, line protection, licensing, Power System Controls/RTU, telecom, Real Properties support. | Reliability Network Upgrade | New | None | Work Requested by Others | GIDAP (Generation Interconnection) | N/A | N/A new | Power Flow, Transient, Post Transient, Short Circuit Duty | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Tier 2 | See Note 16C | Desert Region, Extreme Temperature Conditions | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | See Note 20B | See note 21A | 220 kV | See Note 23B | 6 separate WOs / Elements | 4 separate CWBS | 7777 | See Note 27A | Yes | 2014 | Not available | LGIA | 2006 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | TBD | TBD | TBD | N/A | On Hold | See Note 46A | 2024-06-18 | No | 2020-08-31 | 2025-04-04 | LGIA Negotiations | 41776 | 41776 | See Note 53A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | See Note 57A | 100% | See Note 59A | -22.647 | None | 100% | 0% | Column 9: GIDAP (Generator Interconnection) Column 52: Source= PMWIF (v4 Proj Summary); Represents PIN level estimate
GIDAP | SP-93 | Ord Mountain Reliability Network Upgrades (RNU) (TOT438_Q552) | 34.547943, -116.944771 | San Bernardino, San Bernardino County | To interconnect Nextera Energy Resources' 60 MW Ord Mountain solar photovoltaic generating station to SCE's transmission system; New Calcite Substation 220 kV switchrack position, SPS, power system control, Real properties licensing, and environmental services. | Reliability Network Upgrade | New | SP-01 | Work Requested by Others | GIDAP (Generation Interconnection) | N/A new | N/A new | Power Flow, Transient, Post Transient, Short Circuit Duty | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Non-HFRA | See Note 16C | Extreme Temperature Conditions | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | 7 | See note 21A | See Note 22A | See Note 23B | 2 separate WOs | 2 separate CWBS | 7903 | See Note 27A | Yes | 2016 | 2019 | LGIA | 2009 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | TBD | TBD | TBD | N/A | Canceled | See Note 46A | Canceled | No | 2020-08-01 | Canceled | Project On Hold. No Information Found | 8659 | 89.4341 | See Note 53A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | See Note 57A | 100% | See Note 59A | 0 | None | 100% | 0% | Column 9: GIDAP (Generator Interconnection) Column 52: Source= PMWIF (v0 Proj Summary);PIN level estimate
GIDAP | SP-94 | Antelope 2 Solar RNU (TOT762_Q1208) | 34.74739, -118.369249 | Lancaster, Los Angeles County | To interconnect Antelope 2 Solar's 650 MW solar photovoltaic generating station and battery energy storage system to SCE's transmission system; Short circuit mitigation, modify previously proposed Northern Area 500 kV SPS, plan of service (substation), environmental, add to Tehachapi RAS | Reliability Network Upgrade | New | SP-29 | Work Requested by Others | GIDAP (Generation Interconnection) | N/A | N/A new | Power Flow, Transient, Post Transient, Short Circuit Duty | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Non-HFRA | See Note 16C | No significant environmental factors | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | 73 | See note 21A | See Note 22A | See Note 23B | 2 separate WOs | 2 separate CWBS | 8078 | See Note 27A | Yes | 2017 | 2017 | LGIA | 2015 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | See Col. 37 | 2022 = 732 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2022-02-22 | Yes | 2019-10-31 | 2022-12-15 | Scope Change | 1232 | 1232 | See Note 53A | 732.0541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.832 | 20.1518 | 14.8362 | 265.0777 | 397.1564 | 732.0541 | 176.5701 | See Note 57A | 100% | See Note 59A | 729.4034 | None | 100% | 0% | Column 9: GIDAP (Generator Interconnection) Column 52: Source= PMWIF (v1 Proj Summary); Represents PIN level estimate
GIDAP | SP-95 | Willow Springs Solar 3 RNU (TOT726_Q1076) | 34.84444, -118.313888 | Rosamond, Kern County | To interconnect Willow Springs Solar's 50 MW 3 solar photovoltaic generating station to SCE's transmission system; Modify the programs to add the Large Generating Facility to the Tehachapi CRAS, expand the Whirlwind Substation AA Bank RAS (install logic processing relays, required channel banks), expand the Tehachapi CRAS (install logic processing relays, required channel banks) | Reliability Network Upgrade | New | SP-29 | Work Requested by Others | GIDAP (Generation Interconnection) | N/A | N/A new | Power Flow, Transient, Post Transient, Short Circuit Duty | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Non-HFRA | See Note 16C | High Wind Events, Extreme Temperature Conditions | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | 92 | See note 21A | See Note 22A | See Note 23B | 902326568 | CET-ET-TP-RN-810000 | 8100 | See Note 27A | Yes | 2017 | 2020 | LGIA | 2014 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Pre-construction | See Note 46A | 2023-12-04 | No | 2020-12-31 | 2024-01-02 | Scope Change | 12534 | 64.4116 | See Note 53A | 717.3504 | 340.323 | 180.254 | 185.163 | 0 | 0 | 0 | 705.74 | 0 | 0 | 5.5211 | 0 | 6.0893 | 11.6104 | 3.1506 | See Note 57A | 100% | See Note 59A | 0 | None | 100% | 0% | Column 9: GIDAP (Generator Interconnection) Column 52: Source= PMWIF (v1 Proj Summary); Represents PIN level estimate; WO level estimate $3.543M
GIDAP | SP-96 | Ares Nevada RNU (TOT728AFS_Q1064) | 36.142777, -115.85 | Pahrump, Nye County, Nevada | To interconnect Ares Nevada project's 44 MW gravity power storage rail system generating station to SCE's transmission system as part of an Affected Participating Transmission Owner Upgrade Facilities Agreement; Expand Lugo-Victorville RAS (install Relays at Eldorado Substation), Expand Ivanpah Area RAS (install relays at Eldorado Substation), Expand Ivanpah Area RAS (RTU reprogram, RAS modify, test, and add point addition), Telecom scope to support Lugo-Victorville RAS and Ivanpah Area RAS. | Reliability Network Upgrade | New | SP-72 | Work Requested by Others | GIDAP (Generation Interconnection) | N/A | N/A new | Power Flow, Transient, Post Transient, Short Circuit Duty | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Out of State | See Note 16C | High Wind Events, Extreme Temperature Conditions | Brent Gokbudak, MPO-Project Development & Execution | See Note 19B | 86.7 | See note 21A | See Note 22A | See Note 23B | 902266605 | CET-ET-CR-WS-809500 | 8095 | See Note 27A | Yes | 2018 | 2020 | LGIA | 2014 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Canceled | See Note 46A | 2022-07-15 | No | 2020-03-11 | Canceled | Change of Customer COD | 893 | Not readily available | See Note 53A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | See Note 57A | 100% | See Note 59A | 0 | None | 100% | 0% | Column 9: GIDAP (Generator Interconnection) Column 52: Source= PMWIF (v0 Proj Summary); Represents PIN level estimate Column 52.1: FERC % not yet available in source file; will be updated in future SRP once available
GIDAP | SP-97 | Tropico Solar RNU (TOT823_Q1329) | 34.98717 -118.29228 | Mojave, Kern County | To interconnect Renewables Development's 110 MW EDF Tropico Solar photovoltaic generating station to SCE's transmission system; Substation and Telecommunications: Tehachapi CRAS - generator addition; Substation and Telecommunications: Whirlwind AA Bank RAS - generator addition; Power System Control: Point addition at Whirlwind Substation to support Whirlwind CRAS; Power System Control: .Point addition at Whirlwind Substation to support Tehachapi CRAS | Reliability Network Upgrade | New | SP-29 | Work Requested by Others | GIDAP (Generation Interconnection) | N/A | N/A new | Power Flow, Transient, Post Transient, Short Circuit Duty | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Non-HFRA | See Note 16C | High Wind Events, Extreme Temperature Conditions | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | 92 | See note 21A | See Note 22A | See Note 23B | 2 separate WOs | 2 separate CWBS | 8205 | See Note 27A | Yes | 2018 | 2018 | LGIA | 2016 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | See Col.37 | 2022 = 732 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2021-09-22 | Yes | 2021-06-01 | 2022-08-01 | Scope Change | 1133 | 1133 | See Note 53A | 732.3035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9038 | 8.3466 | 217.6493 | 505.4038 | 732.3035 | 258.8284 | See Note 57A | 100% | See Note 59A | 10.8708 | None | 100% | 0% | Column 9: GIDAP (Generator Interconnection) Column 52: Source= PMWIF (v0 Proj Summary); Represents PIN level estimate
N/A | SP-98 | Chino 220/66 kV: Split the existing Chino 220/66 kV System into two 220/66 kV Systems. Install SA-2 | 33.999, -117.680 | Chino, San Bernardino County | Split existing Chino System into two systems and add a fourth 280 MVA transformer and 2-28MVAR Capacitors. New Switchracks to be constructed. | Install Transformer, Capacitor New Switchrack | New, Replacement | None | Capacity | Substation Capacity | N/A - New | N/A - New Equipment | Bank Capacity, Power Flow, Short Circuit Duty SCE Subtransmission Planning Criteria and Guidelines | N/A | Non-HFRA | See Note 16C | Extreme Temperature Conditions | Demetric Brown, MPO - Programs | See Note 19B | See Note 20B | See Note 21A | 220 kV | See Note 23B | 901191112 | CET-ET-LG-TS-538303 | 5383 | See Note 27A | Yes | 2012 | Pre-2017 | See Note 31A | No | N/A | N/A | N/A | See Col. 37 | 2020 = 3,494 2021 = 28 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2016-06-16 | No | 2020-06-01 | 2020-09-08 | N/A | 13635 | 4772.25 | See Note 53A | 3522.5122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1632.0432 | 1077.0844 | 784.5664 | 28.3302 | 0.48793 | 3522.5122 | 1069.367 | See Note 57A | N/A | See Note 59A | -6.7822e-12 | None | 100% | 0% | Column 52: Source=V.23 Project Summary Work Order Level Costs
N/A | SP-99 | Vestal: Equip 230 KV A-Bank positions (no.1 and 2) with circuit breakers circuit breaker configuration. | 35.8408, -119.086 | Richgrove, Tulare County | Install 4 bank breakers to correct bank on circuit breaker configuration. The objective of this project is to improve operational flexibility and system reliability by reconfiguring the connection of the 220 kV switchrack for the existing Nos. lA and 2A transformer banks from bank-on-bus to double bus-double breaker arrangement. | Circuit Breakers | New | None | Capacity | Substation Capacity | N/A - New | N/A - New Equipment | Bank Capacity, Power Flow, Short Circuit Duty SCE Subtransmission Planning Criteria and Guidelines. I would recommend to check with the sponsor. This work order is just for the bank on breakers project. However, two transformers were replaced under the same PIN number, but with the different orders. The orders are listed in K. | N/A | Non-HFRA | See Note 16C | Seismic- Moderate Flooding Particulate | Demetric Brown, MPO - Programs | See Note 19B | 10.3 | See Note 21A | 220 kV | See Note 23B | 900312889 | CET-ET-LG-TS-626302 | 6263 | See Note 27A | Yes | 2013 | Pre-2017 | See Note 31A | No | N/A | N/A | N/A | See Col. 37 | 2017 = 13,753 2018 = 95 2020 = -16 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2014-02-20 | No | 2015-06-01 | 2017-08-31 | Coordination with Other Work, Outage Constraints, and As Built Changes | 4735 | 4403.55 | See Note 53A | 13831.2387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13847.6243 | -0.32255 | -16.0631 | 0 | 0 | 13831.2387 | 4417.3357 | See Note 57A | N/A | See Note 59A | 3.7469e-12 | None | 100% | 0% | Column 52: Source= PMWIF (V.9 Project Summary) Work Order Level Costs
TPP | SP-100 | Tehachapi Renewable Transmission Project (TRTP) - Segment 10 System Upgrades: New Whirlwind-Windhub 500kV Transmission Line | 34.858, -118.437 / 35.035, -118.281 | Kern County, Los Angeles County, San Bernardino County | Construct new Whirlwind-Windhub 500 kV Transmission Line | Transmission Line | New | None | Capacity | New T-Line | N/A - New | N/A - New Equipment | ● Power Flow ● Transient ● Post Transient ● Short Circuit Duty | Alternatives considered included in CPCN filing | Non-HFRA | See Note 16C | Extreme Temperature Conditions, High Wind Events | Brent Gokbudak, MPO-Project Development & Execution | 17 | See Note 20B | 500 kV | See Note 22A | See Note 23B | 3 Separate WOs | 3 separate CWBS | 6441 | See Note 27A | Yes | 2006 | Pre-2017 | FRM/CRT | 2007 | 2007-2016 | N/A | CAISO 2007 (not available online, but can be provided upon request) | See Col. 37 | 2012 = 85,750 2015 = 71 2017 = 1,393 | Final Certified | EIR/EIS | CPUC/ US Forest Service | CPCN | 2007 | Approved | 2009 | Operational | See Note 46A | 2010-09-01 | No | 2011-10-31 | 2015-12-10 | Not readily available | 108410 | 108410 | See Note 53A | 87213.843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87214.0649 | -0.22197 | 0 | 0 | 0 | 87213.843 | 3883.6329 | See Note 57A | N/A | See Note 59A | -3.0859e-10 | Return on Equity (ROE) Adder, Abandoned Plant & CWIP Incentives (121 FERC ¶ 61,168) | 100% | 0% | Column 52: Source=CPCN Column 53: The maximum and reasonable prudent cost established in the Certificate of Public Convenience and Necessity pursuant to California Public Utilities Code Section 1005.5 (a) for this project, includes, but is not limited to: (1) $746 million (2008$) as noted in D.09-09-033 dated September 24, 2009 and issued on September 28, 2009, which amended D.07-03-012 and D.07-03-045 (For Segments 1-3); and (2) $1,522.92 million, excluding AFUDC which is estimated at $261.82 million for a total estimated project cost of $1,784.74 Million (2009$) as noted in CPUC Decision 09-12-044 dated December 17, 2009, and issued on December 24, 2009 (Segments 4-11); (3) the addition of $32.95 million (2013$), including Contracting Termination Charges, as noted in CPUC Decision D13-02-035 dated July 28, 2013 and issued on March 6, 2013 (for studies related to the feasibility of undergrounding Segment 8A); (4) the addition of $224 million (2013$) as noted in the CPUC Decision D13-07-018 dated July 11, 2013 and issued on July 16, 2013 (undergrounding of Segment 8A); and (5) the addition of $23 million (2013$) as noted in CPUC Decision D14-01-005 dated January 16, 2014 and issued on January 14, 2014 (the inclusion of voltage control equipment for UG5), as well as any adjustments to these amounts made in any of the Petitions for Modification filed in A.07-06-031 and any related dockets associated with the project. Further, as referenced above, these amounts are in different year nominal dollars and would need to be placed in current year dollars to determine the actual cost for the project
TPP | SP-101 | Tehachapi Renewable Transmission Project (TRTP) - Segment 11 System Upgrades: New Mesa-Vincent T/L (Via Gould) 500/230 kV | 34.036, -118.112 / 34.486, -118.119 | Los Angeles County | Construct new Mesa-Vincent 500/230 kV Transmission Line | Transmission Line | New | None | Capacity | New T-Line | N/A - New | N/A - New Equipment | ● Power Flow ● Transient ● Post Transient ● Short Circuit Duty | Alternatives considered included in CPCN filing | Tier 2/Tier 3 | See Note 16C | Extreme Temperature Conditions | Brent Gokbudak, MPO-Project Development & Execution | 38 | See Note 20B | 500 kV | See Note 22A | See Note 23B | 6 Separate WOs | 4 separate CWBS | 6442 | See Note 27A | Yes | 2006 | Pre-2017 | FRM/CRT | 2007 | 2007-2016 | N/A | CAISO 2007 (not available online, but can be provided upon request) | See Col. 37 | 2014 = 4,239 2015 = 262,849 2017 = 6,878 2018 = 875 2019 = 1,300 2020 = 183 2021 =1,516 2022 = -1,502 | Final Certified | EIR/EIS | CPUC/ US Forest Service | CPCN | 2007 | Approved | 2009 | Operational | See Note 46A | 2011-06-01 | No | 2013-11-29 | 2015-04-29 | Not readily available | 111826 | 111826 | See Note 53A | 276335.9488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 274838.0726 | 1300.1499 | 183.3752 | 1515.9035 | -1501.5524 | 276335.9488 | 17337.926 | See Note 57A | N/A | See Note 59A | 1.9436e-10 | Return on Equity (ROE) Adder, Abandoned Plant & CWIP Incentives (121 FERC ¶ 61,168) | 100% | 0% | Column 52: Source=CPCN Column 53: The maximum and reasonable prudent cost established in the Certificate of Public Convenience and Necessity pursuant to California Public Utilities Code Section 1005.5 (a) for this project, includes, but is not limited to: (1) $746 million (2008$) as noted in D.09-09-033 dated September 24, 2009 and issued on September 28, 2009, which amended D.07-03-012 and D.07-03-045 (For Segments 1-3); and (2) $1,522.92 million, excluding AFUDC which is estimated at $261.82 million for a total estimated project cost of $1,784.74 Million (2009$) as noted in CPUC Decision 09-12-044 dated December 17, 2009, and issued on December 24, 2009 (Segments 4-11); (3) the addition of $32.95 million (2013$), including Contracting Termination Charges, as noted in CPUC Decision D13-02-035 dated July 28, 2013 and issued on March 6, 2013 (for studies related to the feasibility of undergrounding Segment 8A); (4) the addition of $224 million (2013$) as noted in the CPUC Decision D13-07-018 dated July 11, 2013 and issued on July 16, 2013 (undergrounding of Segment 8A); and (5) the addition of $23 million (2013$) as noted in CPUC Decision D14-01-005 dated January 16, 2014 and issued on January 14, 2014 (the inclusion of voltage control equipment for UG5), as well as any adjustments to these amounts made in any of the Petitions for Modification filed in A.07-06-031 and any related dockets associated with the project. Further, as referenced above, these amounts are in different year nominal dollars and would need to be placed in current year dollars to determine the actual cost for the project
TPP | SP-102 | Eldorado-Ivanpah Transmission Project (EITP) | 35.797, -115.009 / 35.5443, -115.4690 | San Bernardino County, Clark County, NV | Construct new 220/115 kV Substation, replace portion of circuit and upgrade to double circuit to connect Eldorado Substation, Install new telecommunications and distribution lines | Underground conductor, underground fiber optic cable, Substation, towers, | New, replacement, upgrade | None | Capacity | New T-Line | N/A - New | N/A - New Equipment | Bank Capacity, Power Flow, Short Circuit Duty SCE Subtransmission Planning Criteria and Guidelines | N/A | Non-HFRA | See Note 16C | Project is complete. High Wind Event, Extreme Temperature Conditions, Mudslide, Mountainous Desert Region | Brent Gokbudak, MPO-Project Development & Execution | 34.4 | See Note 20B | 220 kV | See Note 22A | See Note 23B | 10 separate WOs | 10 separate CWBS | 6551 | See Note 27A | Yes | 2011 | Pre-2017 | FRM/CRT | 2011 | 2011-2013 | N/A | CAISO 2011-2012 TPP | See Col. 37 | 2013 = 332,410 2019 = 1,506 | Final Certified | EIR/EIS | CPUC/ BLM | CPCN | 2009 | Approved | 2010 | Operational | See Note 46A | 2013-07-31 | No | 2013-07-31 | 2013-08-29 | N/A | 380650 | 380650 | See Note 53A | 333916.735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 332410.43 | 1506.305 | 0 | 0 | 0 | 333916.735 | 24549.2543 | See Note 57A | N/A | See Note 59A | 6.0172e-11 | Abandoned Plant & CWIP Incentives (129 FERC ¶ 61,246) | 100% | 0% | Column 52: Source= PMWIF (V.0 Project Summary)
N/A | SP-103 | Devers-Bank on Circuit Breaker Project | 33.935, -116.578 | North Palm Springs, Riverside County | Upgrade bank-on-bus configuration to banks in circuit breaker configuration | Circuit Breakers | New, Replacement | None | Infrastructure Replacement, Infrastructure Enhancement | System Design Upgrade | N/A - New | N/A - New Equipment | Bank Capacity, Power Flow, Short Circuit Duty SCE Subtransmission Planning Criteria and Guidelines | N/A | Non-HFRA | See Note 16C | High Seismic, Extreme Temperature Conditions, High Wind Events | Demetric Brown, MPO - Programs | See Note 19B | 98 | See Note 21A | 220 kV | See Note 23B | 900305114 | CET-ET-TP-RL-711200 | 7112 | See Note 27A | Yes | 2010 | Pre-2017 | See Note 31A | No | N/A | N/A | N/A | See Col. 37 | 2017 = 6,575 2018 = 249 2019 = 25 2020 = 1 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2016-08-01 | No | 2012-12-31 | 2017-12-29 | Coordination with Other Work, As Built Issues, Engineering Priorities, and Outage Constraints | 5000 | 5000 | See Note 53A | 6849.6743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6824.1031 | 24.9817 | 0.58958 | 0 | 0 | 6849.6743 | 4189.3751 | See Note 57A | N/A | See Note 59A | -1.331e-11 | None | 100% | 0% | Column 52: Source= PMWIF (V.0 Project Summary)
N/A | SP-104 | El Nido-Bank on Circuit Breaker Project | 33.896016, -118.372576 | Hawthorne, Los Angeles County | Upgrade bank-on-bus configuration to banks in circuit breaker configuration | Circuit Breakers | New, Replacement | None | Infrastructure Replacement, Infrastructure Enhancement | System Design Upgrade | N/A - New | N/A - New Equipment | Bank Capacity, Power Flow, Short Circuit Duty SCE Subtransmission Planning Criteria and Guidelines | N/A | Non-HFRA | See Note 16C | N/A | Demetric Brown, MPO - Programs | See Note 19B | 13.6 | See Note 21A | 220 kV | See Note 23B | 901241164 | CET-ET-LG-TS-711300 | 7113 | See Note 27A | Yes | 2010 | Pre-2017 | See Note 31A | No | N/A | N/A | N/A | See Col. 37 | 2018 = 8,526 2019 = 15 2020 = 4 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2017-05-15 | No | 2016-12-31 | 2018-06-25 | Coordination with Other Work with Bundling, and Scope Change (MEER) | 5000 | 2746.5 | See Note 53A | 8545.4451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8525.7848 | 15.3882 | 4.0202 | 0.25193 | 0 | 8545.4451 | 1696.534 | See Note 57A | N/A | See Note 59A | -4.7548e-13 | None | 100% | 0% | Column 52: Source= PMWIF (V.5 Project Summary)
TPP | SP-105 | Bailey Sub Upgrades to 66kV Switchrack | 34.776491, -118.774429 | Gorman, Los Angeles County | Construct new MEER, convert existing switchrack to double-breaker configuration | MEER, Circuit Breaker | New, Upgrade | None | Infrastructure Replacement, Infrastructure Enhancement | System Design Upgrade | N/A - New | N/A - New Equipment | Bank Capacity, Power Flow, Short Circuit Duty SCE Subtransmission Planning Criteria and Guidelines | N/A | Tier 2 | See Note 16C | High Wind Events, Flooding, High Fire Area, Extreme Temperature Conditions, Air Particulate Levels | Brent Gokbudak, MPO-Project Development & Execution | See Note 19B | 8.9 | See Note 21A | 220/66kV | See Note 23B | 2 separate WOs | 2 separate CWBS | 7451 | See Note 27A | Yes | 2013 | Pre-2017 | See Note 31A | No | N/A | N/A | N/A | See Col. 37 | 2017 = 12,877 2019 = 10 2020 = -9 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2014-09-15 | No | 2015-12-31 | 2017-02-08 | Coordination with Other Work | 7558.51 | 5366.5421 | See Note 53A | 12878.0854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12877.2709 | 9.5234 | -8.7088 | 0 | 0 | 12878.0854 | 2974.4564 | See Note 57A | N/A | See Note 59A | 76.0048 | None | 0% | 100% | Column 52: Source= PMWIF (V.1 Project Summary)
TPP | SP-106 | Victor Loop-In Project | 34.505936, -117.387680 | Victorville, San Bernardino County | Loop Kramer-Lugo 230 kV No. 1 and 2 into Victor substation to eliminate system instability due to outage of Victor-Lugo 230 kV No. 1 and No. 2 | Circuit Breakers, Disconnects, Protection Equipment | New | None | Reliability, Infrastructure Enhancement | System Design Upgrade | N/A - New | N/A - New Equipment | Bank Capacity, Power Flow, Short Circuit Duty SCE Subtransmission Planning Criteria and Guidelines | Modify Existing HDPP RAS to drop load at Victor and change arming points of generation tripping. Considered in the study but not in project Proposal. | Non-HFRA | See Note 16C | High Wind Events | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | 33.3 | 230 kV | See Note 22A | See Note 23B | 5 Separate WOs | 4 separate CWBS | 7645 | See Note 27A | Yes | 2014 | Pre-2017 | See Note 31A | 2014 | 2014-Present | N/A | CAISO 2013-2014 TPP | See Col. 37 | 2017 = 15,507 2018 = 964 2019 = -175 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2016-02-01 | No | 2015-06-01 | 2018-05-29 | Outage Constraints, Coordination with Other Work | 20940.449 | 20940.449 | See Note 53A | 16294.6818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16470.9796 | -176.0123 | -0.28546 | 0 | 0 | 16294.6818 | 4675.6799 | See Note 57A | N/A | See Note 59A | 4.9965e-12 | None | 100% | 0% | Column 52: Source= PMWIF (V.1 Project Summary)
TPP | SP-107 | Whirlwind Substation Expansion: Whirlwind 3rd 500/220 kV (AA) Bank | 34.857, -118.436 | Rosamond, Kern County | Install third 500/230 kV transformer bank at Whirlwind Substation and expansion of the Whirlwind AA Bank N-1 SPS | Transformer Bank, Circuit Breakers, Disconnects, SPS/RAS | New, Modify | None | Capacity Increase | GIDAP (Generation Interconnection) | N/A - New | N/A - New Equipment | ● Power Flow ● Transient ● Post Transient ● Short Circuit Duty | N/A | Non-HFRA | See Note 16C | High Wind Events | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | 92 | See Note 21A | 500 kV | See Note 23B | 901307713 | CET-ET-TP-RN-765000 | 7650 | See Note 27A | Yes | 2014 | Pre-2017 | FRM/CRT | 2012 | 2012-Present | N/A | CAISO 2012-2013 | See Col. 37 | 2017 = 32,971 2018 = 13 2019 = 19 2020 = -2 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2016-06-06 | No | 2016-12-31 | 2017-04-28 | N/A | 14978.364 | 14978.364 | See Note 53A | 33000.9845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32984.1048 | 18.5244 | -1.6447 | 0 | 0 | 33000.9845 | 2384.5548 | See Note 57A | N/A | See Note 59A | 1.9643e-11 | Abandoned Plant & CWIP Incentives (134 FERC ¶ 61,181) | 100% | 0% | Column 52: Source= V.0 Project Summary
TPP | SP-108 | Santiago Synchronous Condenser | 33.665128, -117.767521 | Irvine, Orange County | Install one 225 MVAR Synchronous Condenser at Santiago Substation to alleviate dynamic reactive support | Circuit breakers, Capacitor Bank, Synchronous Condenser | New | None | Reliability | GIDAP (Generation Interconnection) | N/A - New | N/A - New Equipment | ● Power Flow ● Transient ● Post Transient ● Short Circuit Duty | Reinforce existing switchrack, Reconfigure 3-66kV subtrans lines | Non-HFRA | See Note 16C | High Seismic | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | 18.1 | See Note 21A | 230 kV | See Note 23B | 2 Separate WOs | 2 separate CWBS | 7680 | See Note 27A | Yes | 2014 | Pre-2017 | FRM/CRT | 2014 | 2014-Present | N/A | CAISO 2014-2015 TPP | See Col. 37 | 2017 = 58,528 2019 = 854 2020 = 96 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2015-12-15 | No | 2017-12-31 | 2017-12-08 | N/A | 62586.488 | 60083.0285 | See Note 53A | 59199.0541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58258.1009 | 844.8626 | 96.0906 | 0 | 0 | 59199.0541 | 7791.8591 | See Note 57A | N/A | See Note 59A | 8.2025e-11 | None | 100% | 0% | Column 52: Source= PMWIF (V.1 Project Summary)
TPP | SP-109 | Kramer High Voltage Mitigation - Tertiary Reactors | 34.989582, -117.542405 | Kramer, San Bernardino County | Install two 45 MVAR tertiary bank reactors and a 45 MVAR 230 kV bus shunt reactor at Kramer Substation to mitigate high voltage | Bank Reactors, Bus Shunt Reactor | New | None | Reliability | System Design Upgrade | N/A - New | N/A - New Equipment | Bank Capacity, Power Flow, Short Circuit Duty SCE Subtransmission Planning Criteria and Guidelines | Install Two 45 MVAR 220 kV bus shunt reactors. Considered in the study but not in project Proposal | Non-HFRA | See Note 16C | High Wind Events | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | 20.6 | 220 kV | 115 kV | See Note 23B | 2 Separate WOs | 2 separate CWBS | 7806 | See Note 27A | Yes | 2015 | Pre-2017 | See Note 31A | 2015 | 2015-2018 | N/A | CAISO 2015-2016 TPP | See Col. 37 | 2016 = 5,412 2017 = 3,863 2018 = 53 2019 = 14 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2016-03-14 | No | 2016-06-01 | 2017-11-02 | Delays in permitting | 3324.654 | 3324.654 | See Note 53A | 9340.6774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9327.1743 | 13.5031 | 0 | 0 | 0 | 9340.6774 | 1440.8859 | See Note 57A | N/A | See Note 59A | -2.615e-12 | None | 0% | 100% | Column 52: Source= PMWIF (V.0 Project Summary)
N/A | SP-110 | Bailey 220/66 KV - Install a 28.8 MVAR Cap | 34.776491, -118.774429 | Gorman, Los Angeles County | Install 28.8 MVAR Cap to mitigate deficit | Capacitor | New | None | Reliability | Substation Reliability | N/A - New | N/A - New Equipment | Bank Capacity, Power Flow, Short Circuit Duty SCE Subtransmission Planning Criteria and Guidelines | N/A | Tier 2 | See Note 16C | High Wind Events, Flooding, High Fire Area, Extreme Temperature Conditions, Air Particulate Levels | Demetric Brown, MPO - Programs | See Note 19B | 8.9 | 220 kV | 220/66kV | See Note 23B | 901618623 | CET-ET-LG-TS-783400 | 7834 | See Note 27A | Yes | 2015 | Pre-2017 | See Note 31A | No | N/A | N/A | N/A | See Col. 37 | 2018 = 1,433 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2016-03-14 | No | 2018-06-01 | 2018-06-28 | N/A | 1202.941 | 1202.941 | See Note 53A | 1434.022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1433.4358 | 0.43934 | 0.14683 | 0 | 0 | 1434.022 | 345.0608 | See Note 57A | N/A | See Note 59A | 2.2806e-13 | None | 0% | 100% | Column 52: Source= PMWIF (V.0 Project Summary) Work Order Level Costs
N/A | SP-111 | Control-Silver Peak 55 kV Reliability Project | 37.336, -118.481 / 37.754, -117.632 | Inyo County | Scope of the project involves installing remote fault indicators and converting 5 switches to remote transmission switches on the two Control-Silver Peak 55kV lines to expedite locating faults and enabling remote switching | Remote Fault Indicators, Switches | New | None | Reliability | Substation Reliability | N/A - New | N/A - New Equipment | Bank Capacity, Power Flow, Short Circuit Duty SCE Subtransmission Planning Criteria and Guidelines | N/A | Tier 2/Out of State | See Note 16C | High Wind Events, Flooding, High Fire Area, Extreme Temperature Conditions, Air Particulate Levels | John Keelin, MPO - Project Dev. & Execution | See Note 19B | See Note 20B | 55 kV | See Note 22A | See Note 23B | 2 Separate WOs | 2 separate CWBS | 8019 | See Note 27A | Yes | 2017 | Pre-2017 | See Note 31A | 2017 | 2017-2019 | N/A | CAISO 2017-2018 TPP | See Col. 37 | 2023 = 1,772 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2019-11-04 | Yes | 2018-10-01 | 2023-03-16 | Delays in Permitting, Weather Conditions, Government Lands Clearance, and Outage Constraints | 2054.621 | 2054.621 | See Note 53A | 1771.952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 388.0941 | 225.6792 | 726.1452 | 186.783 | 245.2505 | 1771.952 | 611.452 | See Note 57A | N/A | See Note 59A | 1450.3745 | None | 0% | 100% | Column 52: Source= PMWIF (V.1 Project Summary)
TPP | SP-112 | Eldorado - Sloan Canyon 220kV Interconnection | 35.792, -115.009 | Clark County, Nevada | Interconnect Bob Switch to SCE-owned 220 kV Switchyard | See Project Description | New | None | Work requested by others | GIDAP (Generation Interconnection) | N/A - New | N/A - New Equipment | ● Power Flow ● Transient ● Post Transient ● Short Circuit Duty | N/A | Out of State | See Note 16C | Extreme Temperature Conditions | Brent Gokbudak, MPO-Project Development & Execution | See Note 19B | See Note 20B | 220 kV | 500 kV, 220 kV | See Note 23B | 2 Separate WOs | 2 separate CWBS | 8090 | See Note 27A | Yes | 2017 | 2017 | See Note 31A | 2019 | 2018-2019 TPP to Present | N/A | CAISO 2018-2019 | See Col. 37 | 2019 = 5,717 2020 = 260 2021 = 18 2022 = 7 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2019-03-04 | No | 2019-07-30 | 2019-12-10 | N/A | 5792 | 5792 | See Note 53A | 6108.6404 | 84 | 22 | 0 | 0 | 0 | 0 | 106 | 602.5036 | 5114.3486 | 260.3561 | 18.4078 | 7.0243 | 6002.6404 | 1050.0058 | See Note 57A | 100% | See Note 59A | 4.1445e-12 | None | 100% | 0% | Column 52: Source= PMWIF (V.2 Project Summary) Work Order Level Costs
GIDAP | SP-113 | Mountainview Generating Station Pmax Increase 38 MW (TOT842_Q1407) | 34.081188, -117.242108 | Redlands, San Bernardino County | To interconnect the Mountainview Generating Station Pmax Increase of an additional 38 MW of combined-cycle thermal generators; Conduct relay study and make adjustments; West of Colorado River CRAS/Monitoring Infrastructure - new relays, telecommunication, programing, real properties, environmental, permits, licensing and security. | Reliability Network Upgrades | New | PB-40 | GIDAP (Generator Interconnection) | GIDAP (Generation Interconnection) | N/A - New | N/A - New Equipment | Power Flow, Transient, Post Transient, Short Circuit Duty | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered | Non-HFRA | See Note 16C | None | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | See Note 20B | See Note 21A | See Note 22A | See Note 23B | 7 separate WOs | 7 separate CWBS | 8238 | See Note 27A | Yes | 2019 | 2021 | LGIA | 2017 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Construction more than 50% completed | See Note 46A | 2021-09-27 | Yes | 2021-12-31 | 2023-12-29 | Coordination with Other Projects for CRAS QA Test | 1038.669 | 1038.669 | See Note 53A | 481.5784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1205 | 111.974 | 274.6172 | 93.8667 | 481.5784 | 90.6259 | See Note 57A | 100% | See Note 59A | 480.8089 | None | 100% | 0% | Column 52: Source= PMWIF (V.0 Project Summary)
GIDAP | SP-114 | Yellow Pine 2, LLC (TOT796_Q1341) | 34.081188, -117.242108 | Pahrump, Nye County | To interconnect the Yellow Pine 2 256.5 MW solar photovoltaic and battery energy storage system (BESS); construct new switching station (Trout Canyon); Expand and Modify Lugo-Victorville RAS - telecommunication facilities, relays and programming; Expand and Modify Ivanpah Area RAS - telecommunication facilities, relays and programming. | Reliability Network Upgrades | New | SP-72 | GIDAP (Generator Interconnection) | GIDAP (Generation Interconnection) | N/A - New | N/A - New Equipment | Power Flow, Transient, Post Transient, Short Circuit Duty | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered | Non-HFRA | See Note 16C | Extreme Temperature Conditions | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | 86.7 | See note 21A | 500 kV, 220 kV | See Note 23B | 2 separate WOs | 2 separate CWBS | 8358 | Yes | Yes | 2021 | 2021 | LGIA | 2016 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Pre-construction | See Note 46A | 2023-02-13 | No | 2023-02-27 | 2024-03-18 | Scope Change | 943 | 943 | See Note 53A | 1264.1143 | 40 | 166 | 387 | 354 | 0 | 0 | 947 | 0 | 0 | 0 | 38.925 | 278.1893 | 317.1143 | 50.8641 | See Note 57A | 100% | See Note 59A | 317.1143 | None | 100% | 0% | Column 52: Source= PMWIF (V.0 Project Summary) Work Order Level Costs
GIDAP | SP-115 | ARIDA SOLAR FARM TOT880 (Q1522) | 35.798, -115.007 | Laughlin, Clark County | To interconnect the Arida Solar Farm Project 370 MW solar photovoltaic and battery energy storage system (BESS); Install new 500 kV position Mohave, gen-tie line, telecommunication, relays, security, real properties and environmental, permits and licensing; Lugo-Victorville RAS and CRAS - telecommunication facilities, relays and programming. | Reliability Network Upgrades | New | SP-72 | GIDAP (Generator Interconnection) | GIDAP (Generation Interconnection) | N/A - New | N/A - New Equipment | Power Flow, Transient, Post Transient, Short Circuit Duty | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered | Out of State | See Note 16C | Extreme Temperature Conditions | Brent Gokbudak, MPO-Project Development & Execution | See Note 19B | 11.5 | See note 21A | 500 kV | See Note 23B | 4 separate WOs | 4 separate CWBS | 8326 | See Note 27A | Yes | 2020 | 2021 | LGIA | 2018 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Engineering more than 50% completed | See Note 46A | 2024-09-03 | No | 2024-08-01 | 2025-05-01 | Change of Customer COD | 29482.037 | 29482.037 | See Note 53A | 8061.7596 | 778 | 318 | 3355 | 2007 | 0 | 0 | 6458 | 0 | 0 | 19.9863 | 28.6211 | 1555.1523 | 1603.7596 | 147.8393 | See Note 57A | 100% | See Note 59A | 1603.7596 | None | 100% | 0% | Column 52: Source= PMWIF (V.1 Project Summary) Work order for Bend-Mohave 500 kV Gen Tie-Line removed December 2022
GIDAP | SP-116 | Glenfeliz Solar Farm (TOT909_Q1631) | 35.0561, -118.1767 | Mojave, Kern County | To interconnect the Glenfeliz Solar Farm Project 500 MW solar photovoltaic and battery energy storage system (BESS); Utilize existing 220 kV facilities from TOT892; Windhub Substation - Perform relay coordination study and adjustments, telecommunications, security and real properties; Tehachapi CRAS - relays, programming, telecommunication and security; Windhub AA Bank CRAS. | Reliability Network Upgrades | New | SP-29 & SP-61 | GIDAP (Generator Interconnection) | GIDAP (Generation Interconnection) | N/A - New | N/A - New Equipment | Power Flow, Transient, Post Transient, Short Circuit Duty | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered | Non-HFRA | See Note 16C | High Wind Events, Extreme Temperature Conditions | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | 59.2 | See note 21A | See Note 22A | See Note 23B | 5 separate WOs | 5 separate CWBS | 8355 | See Note 27A | Yes | 2021 | 2021 | LGIA | 2019 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Engineering less than 50% completed | See Note 46A | 2023-08-15 | No | 2024-03-01 | 2025-03-15 | Change of Customer COD | 4541.608 | 4541.608 | See Note 53A | 2679.0646 | 429.315 | 1028.435 | 135 | 687 | 0 | 0 | 2279.75 | 0 | 0 | 0 | 20.11 | 379.2047 | 399.3146 | 60.8019 | See Note 57A | 100% | See Note 59A | 399.3146 | None | 100% | 0% | Column 52: Source= PMWIF (V.0 Project Summary)
GIDAP | SP-117 | Sanborn Hybrid 3 - TOT915_Q1632 | 35.034918;-118.280829 | Mojave, Kern County | To interconnect the Sanborn Hybrid 3 Project 1,400 MW solar photovoltaic and battery energy storage system (BESS); Install a new 500 kV position Windhub Substation, gen-tie line, telecommunication, relays, security, metering, real properties, and environmental, permits and licensing; Tehachapi Centralized RAS - telecommunication facilities, relays, programming and security. | Reliability Network Upgrades | New | SP-19 | Work Requested by Others | N/A | 2022-05-03 | N/A - Installing New Assets | Power Flow, Transient, Post Transient, Short Circuit Duty and ground grid evaluation | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Not applicable - No HFRA | See Note 16C | High Wind Events | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | 0.4 miles | 59.2 | See Note 21A | 500/220kV | See Note 23B | 5 separate WOs | CET-ET-CR-WC-834204 | 8342 | See Note 27A | Yes | 2021 | 2021 | LGIA | 2019 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Engineering less than 50% completed | See Note 46A | 2025-01-02 | No | 2025-04-15 | 2025-04-24 | N/A | 15833 | 15833 | See Note 53A | 14083.3198 | 274.725 | 3715.669 | 5154.695 | 4930.66 | 0 | 0 | 14075.749 | 0 | 0 | 0 | 0 | 7.5709 | 7.5709 | 2.9809 | See Note 57A | 100% | See Note 59A | 7.5709 | None | 100% | 0% | Column 52: Source = PMWIF (V.1 Project Summary)
GIDAP | SP-118 | Humidor Storage - TOT959- Q1629 | 34.486169;-118.118391 | Palmdale, Los Angeles County | To interconnect the Humidor Storage 1 300 MW battery energy storage system (BESS); Install a new 220 kV position Vincent Substation, gen-tie line, telecommunication, relays, security, metering, real properties, and environmental, permits and licensing. | Reliability Network Upgrades | New | SP-29 | Work Requested by Others | N/A | 2022-05-12 | N/A - Installing New Assets | Power Flow, Transient, Post Transient, Short Circuit Duty and ground grid evaluation | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | HFTD Tier 3 | See Note 16C | High Wind Events | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | 5 miles | 46 | See Note 21A | 500kV, 220kV | See Note 23B | 903516981 | CET-ET-CR-WC-839401 | 8394 | See Note 27A | Yes | 2021 | 2021 | LGIA | 2019 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Engineering more than 50% completed | See Note 46A | 2025-02-10 | No | 2023-10-15 | 2025-03-10 | Scope Change | 2909 | 2909 | See Note 53A | 2487.547 | 368.492 | 1057.243 | 352.414 | 639.352 | 0 | 0 | 2417.501 | 0 | 0 | 0 | 0 | 70.046 | 70.046 | 21.4775 | See Note 57A | 100% | See Note 59A | 70.046 | None | 100% | 0% | Column 52: Source = PMWIF (V.0 Project Summary)
GIDAP | SP-119 | Bonanza Solar - TOT931_Q1649 | 35.797879;-115.007526 | Amargosa Valley, Nye County, Nevada | To interconnect the Bonanza Solar Project 300 MW solar photovoltaic and 150 MW battery energy storage system (BESS); Lugo-Victorville CRAS - telecommunication facilities, relays, programming, real properties and security. | Reliability Network Upgrades | New | SP-29 | Work Requested by Others | N/A | 2022-05-03 | N/A - Installing New Assets | Power Flow, Transient, Post Transient, Short Circuit Duty and ground grid evaluation | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Not applicable - No HFRA | See Note 16C | "High Wind Events Extreme Temperature Conditions (Heat) " | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | 86.7 | 220 kV | 500kV/220kV | See Note 23B | 903606178 | CET-ET-CR-WC-842600 | 8426 | See Note 27A | Yes | 2021 | 2021 | LGIA | 2019 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Planning | See Note 46A | 2025-01-06 | No | 2025-06-01 | 2025-02-03 | N/A | 1106.308 | 1106.308 | See Note 53A | 906.265 | 23 | 241 | 321 | 317 | 0 | 0 | 902 | 0 | 0 | 0 | 0 | 4.265 | 4.265 | 0.30504 | See Note 57A | 100% | See Note 59A | 4.265 | None | 100% | 0% | Column 52: Source = PMWIF (V.0 Project Summary)
N/A | SP-120 | Digital 395 Project: North-of-Kramer Area Telecom Network and RAS Upgrades | 37.334943;-118.481952 | Bishop, Inyo County | This project upgrades the existing to add redundant RAS systems and fiber paths, per WECC RAS Reliability criteria. The Bishop RAS monitors the status of two 115 kV lines terminating at Control Substation and trips SCE Bishop Creek Hydroelectric and NVE Oxbow generating units for loss of one or more monitored lines. | Install 8 relays, various fiber optic circuits, two ethernet switches, and associated telecom terminal equipment as needed to upgrade the Bishop RAS to compliance with WECC reliability criteria; program and test RAS functionality. | New, Replacement, Upgrade | None | Other - See Notes | Generation Interconnection, Special Protection Scheme | 2021-09-02 | ~40 years | N/A | N/A | HFTD Tier 2 | See Note 16C | Extreme Temperature Conditions | Demetric Brown, MPO - Programs | See Note 19B | 4.95 | See Note 21A | 115kV/55kV | See Note 23B | 2 separate WOs | 2 separate CWBS | 7727 | See Note 27A | Yes | 2014 | Pre-2018 | Grid Planning Committee (now Asset Strategy & Technical Review Committee) | No | N/A | N/A | N/A | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Construction more than 50% completed | See Note 46A | 2021-09-27 | Yes | 2016-12-31 | 2023-12-29 | Coordination of work and delay in receiving permit from outside entities | 1080 | 928.8 | See Note 53A | 1313.2264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.2386 | 239.755 | 212.3653 | 561.7887 | 256.0787 | 1313.2264 | 298.2627 | See Note 57A | N/A | See Note 59A | 1312.0689 | None | 0% | 100% | Column 52: Source = PMWIF (V.1 Project Summary)
GIDAP | SP-121 | Crimson - TOT764_Q1192 | 33.5807073;-114.8170621 | Blythe, Riverside County | To interconnect the RE Crimson Project 350 MW solar photovoltaic and battery energy storage system (BESS); Install a new 220 kV position Colorado River Substation, gen-tie line, telecommunication, relays, security, metering, real properties, and environmental, permits and licensing; West of Colorado River CRAS - telecommunication facilities, relays, programming, real properties and environmental, permits and licensing. | Reliability Network Upgrades | New | PB-40 and SP-113 | Work Requested by Others | N/A | 2021-04-06 | N/A - Installing New Assets | Power Flow, Transient, Post Transient, Short Circuit Duty and ground grid evaluation | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Not applicable - No HFRA | See Note 16C | Extreme Temperature Conditions | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | 77 | See Note 21A | 500kV/220kV | See Note 23B | 902660304 | CET-ET-TP-RN-821601 | 8216 | See Note 27A | Yes | 2018 | 2018 | LGIA | 2015 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | See Col.37 | 2022 = 2,240 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2021-04-19 | Yes | 2021-04-01 | 2022-05-04 | Coordination with Other Work | 664 | 664 | See Note 53A | 2239.9401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.2159 | 334.1913 | 985.7893 | 825.7437 | 2239.9401 | 307.7136 | See Note 57A | 100% | See Note 59A | 1.9295e-12 | None | 100% | 0% | Column 52: Source = PMWIF (V.0 Project Summary)
GIDAP | SP-122 | Commerce Energy Storage - TOT927_Q1611 | 33.976179;-118.147937 | Commerce, Los Angeles County | To interconnect the Commerce Energy Storage 250 MW battery energy storage system (BESS); Install a new 220 kV position Laguna Bell Substation, gen-tie line, telecommunication, relays, security, metering, real properties, and environmental, permits and licensing. | Reliability Network Upgrades | New | N/A | Work Requested by Others | N/A | 2022-05-20 | N/A - Installing New Assets | Power Flow, Transient, Post Transient, Short Circuit Duty and ground grid evaluation | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Not applicable - No HFRA | See Note 16C | High Wind Events | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | 25.2 | See Note 21A | 220kV/66kV/12kV | See Note 23B | 903627525 | CET-ET-TP-RN-841802 | 8418 | See Note 27A | Yes | 2022 | 2021 | LGIA | 2019 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Engineering more than 50% completed | See Note 46A | 2024-06-26 | No | 2024-03-01 | 2025-03-01 | POCO location recently defined/extended major material times Change of Customer COD | 2845 | 2845 | See Note 53A | 2362.7845 | 459.222 | 621.438 | 450 | 805 | 0 | 0 | 2335.66 | 0 | 0 | 0 | 0 | 27.1245 | 27.1245 | 12.6649 | See Note 57A | 100% | See Note 59A | 27.1245 | None | 100% | 0% | Column 52: Source = PMWIF (V.0 Project Summary)
0: N/A; Project Description 1: SP-123; Project Description 2: Antelope 230kV Circuit Breaker Replacement; Project Description 3: 34.688, -118.300; Project Description 4: Lancaster, Los Angeles County; Project Description 5: Replace circuit breakers 4072 and 6032 to achieve 63 kA rating.; Project Description 6: Please see Notes; Project Description 7: Please see Notes; Project Description (Cont.) 24: Please see Notes; Project Description (Cont.) 25: Please see Notes; Project Description (Cont.) 26: Please see Notes; Project Status 45: Canceled; Project Status 50: Canceled; Costs 52: Canceled; Costs 52.1: Canceled; Costs 54: Canceled | [16 empty] | Project has been canceled
TPP | SP-124 | Laguna Bell-Mesa No. 1 230 kV Line Rating Increase Project | 33.976,-118.148 / 34.035,-118.112 | Commerce; Monterey Park, Los Angeles County | Reconductor Laguna Bell-Mesa 230 kV No. 1 Line to Aluminum Conductor Composite Core Forth Worth, or equivalent High Temperature Low Sag conductor. Upgrade the Laguna Bell-Mesa No. 1 230 kV Line terminal equipment in Position 11 at Laguna Bell Substation to achieve rating increase to 3250/4760 Amps SN/SE. | Transmission Line | Reconductor | None | Capacity Increase | Reconductor | 2022-06-23 | Various | Power Flow, Short Circuit Duty, dynamic stability, SCE Transmission Planning Criteria and Guidelines | N/A | Non-HFRA | No | No significant environmental factors | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | 5 | See Note 20B | 230 kV | See Note 22A | See Note 23B | 2 separate WOs | 2 separate CWBS | 8448 | See Note 27A | Yes | 2022 | 2022 | See Note 31A | 2019 | 2019-2021 | N/A | CAISO 2019-2020 TPP | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Engineering more than 50% completed | See Note 46A | 2023-05-08 | No | 2023-12-31 | 2024-05-28 | N/A | 14590 | 14590 | See Note 53A | 10077.7833 | 7296.034 | 2614.038 | 0 | 0 | 0 | 0 | 9910.072 | 0 | 0 | 0 | 0 | 167.7113 | 167.7113 | 62.4497 | See Note 57A | N/A | See Note 59A | 151.7448 | None | 100% | 0% | Column 52: Source = Verified PMWIF (Project Summary v.0)
0: N/A; Project Description 1: SP-125; Project Description 2: Vincent 500kV Circuit Breaker Replacement; Project Description 3: 34.486, -118.118; Project Description 4: Palmdale, Los Angeles County; Project Description 5: Replace circuit breakers; Project Description 6: Please see Notes; Project Description 7: Please see Notes; Project Description (Cont.) 24: Please see Notes; Project Description (Cont.) 25: Please see Notes; Project Description (Cont.) 26: Please see Notes; Project Status 45: Canceled; Project Status 50: Canceled; Costs 52: Canceled; Costs 52.1: Canceled; Costs 54: Canceled | [16 empty] | Project has been canceled
GIDAP | SP-126 | TOT910 (Q1642) Oberon | 33.672, -115.559 | Desert Center, Riverside County | To interconnect the Oberon Project 500 MW solar photovoltaic and battery energy storage system (BESS); Install a new 500 kV position Red Bluff Substation, gen-tie line, telecommunication, relays, security, metering, real properties, and environmental, permits and licensing; West of Colorado River CRAS - telecommunication facilities, relays, programming, real properties and environmental, permits and licensing. | Transmission line; Substation - breakers, disconnects, bus, tower, relays and communication. | New | SP-44 | Work Requested by Others | N/A | N/A - New | N/A - New Equipment | Power Flow, Transient, Post Transient, Short Circuit Duty, Relay Coordination and ground grid evaluation. | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Non-HFRA | NA | High Wind Events, Extreme Temperature Conditions | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | 75.7 | 500 kV & 230 kV | 500kV - 220kV, 1120 MVA | See Note 23B | 2 separate WOs | 2 separate CWBS | 8308 | See Note 27A | Yes | 2021 | 2022 | LGIA | 2019 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Construction more than 50% completed | See Note 46A | 2022-08-01 | Yes | 2023-12-15 | 2023-12-29 | Changed per Customer request in March 2021. | 877 | 877 | See Note 53A | 5199.2246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.92734 | 187.1933 | 5011.104 | 5199.2246 | 688.0212 | See Note 57A | 100% | See Note 59A | 337.9961 | None | 100% | 0% | Column 52: Source = Verified PMWIF (Project Summary v.0)
GIDAP | SP-127 | Kestrel Storage Project (TOT907/Q1616) | 34.008, -117.950 | Industry, Los Angeles County | To interconnect the Kestrel Storage Project 200 MW battery energy storage system (BESS); Install a new 220 kV position Walnut Substation, gen-tie line, telecommunication, relays, security, metering, real properties, and environmental, permits and licensing; Relocate the existing Mesa-Walnut 220 KV line to a new bus position - all this work is within the Walnut Substation - telecommunication facilities, programming, and environmental; Conduct a ground grid study at Lewis 220 kV Substation and Walnut 220 kV Substation. | Transmission line; Substation - breakers, disconnects, bus, tower, relays and communication. | New | N/A | Work Requested by Others | N/A | N/A - New | N/A - New Equipment | Power Flow, Transient, Post Transient, Short Circuit Duty, Relay Coordination and ground grid evaluation. | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Non-HFRA | No | High Wind Events, Extreme Temperature Conditions High Seismic | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | 14.3 | See note 21A | 220 and 66 kV | See Note 23B | 4 separate WOs | 4 separate CWBS | 8393 | See Note 27A | Yes | 2021 | 2022 | LGIA | 2019 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Engineering less than 50% completed | See Note 46A | 2024-07-15 | No | 2023-10-01 | 2024-11-04 | Change of Customer COD | 5349 | 5349 | See Note 53A | 6221.5966 | 1050 | 1600 | 2194 | 473 | 0 | 0 | 5317 | 0 | 0 | 0 | 0 | 904.5966 | 904.5966 | 93.3898 | See Note 57A | 100% | See Note 59A | 904.5966 | None | 100% | 0% | Column 52: Source = Verified PMWIF (Project Summary v.1)
GIDAP | SP-128 | Hinson 220/66 kV - TOT906 (Q1608) Avocet Energy Storage 200 MW Project Interconnection | 33.818,-118.222 | Long Beach, Los Angeles County | To interconnect the Avocet Storage Project 200 MW battery energy storage system (BESS); Install a new 220 kV position Hinson Substation, gen-tie line, telecommunication, relays, security, metering, real properties, and environmental, permits and licensing; Conduct a ground grid study at Lewis 220 kV Substation and Redondo 220 kV Substation. | Transmission line; Substation - breakers, disconnects, bus, tower, relays and communication. | New | N/A | Work Requested by Others | N/A | N/A - New | N/A - New Equipment | Power Flow, Transient, Post Transient, Short Circuit Duty, Relay Coordination and ground grid evaluation. | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Non HFRA | See Note 16C | No Significant Environmental Factors | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | 12.2 | See Note 21A | 220kV/66kV | See Note 23B | 2 Separate WOs | CET-ET-CR-WC-833600 | 8389 | See Note 27A | Yes | 2021 | 2022 | LGIA | 2019 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Engineering more than 50% completed | See Note 46A | 2024-07-11 | No | 2024-01-15 | 2024-12-31 | Customer Delays and Vendor Drawings | 3878 | 3878 | See Note 53A | 2917.5698 | 2025 | 242.709 | 620 | 0 | 0 | 0 | 2887.709 | 0 | 0 | 0 | 1.8143 | 28.0465 | 29.8608 | 8.1383 | See Note 57A | 100% | See Note 59A | 29.8608 | None | 100% | 0% | Column 52: Source = Verified PMWIF (Project Summary v.0)
GIDAP | SP-129 | Cyclone Solar (TOT806 / Q1327) | 34.857, -118.436 | Rosamond, Kern County | To interconnect the Cyclone Solar Project 57 MW solar photovoltaic and battery energy storage system (BESS); Sharing existing 220 kV position and gen-tie line Whirlwind Substation, telecommunication, relay coordination, security, metering, and real properties; Whirlwind AA Bank CRAS and Tehachapi CRAS - telecommunication facilities, relays, and programming. | Substation - relays and communication. | New | SP-58 and SP-84 | Work Requested by Others | N/A | N/A - New | N/A - New Equipment | Power Flow, Transient, Post Transient, Short Circuit Duty and Relay Coordination. | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Non-HFRA | No | No Significant Environmental Factors High Wind Events, Extreme Temperature Conditions, High Seismic | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | 92 | See Note 21A | 500/220kV | See Note 23B | 2 separate WOs | 2 separate CWBS | 8411 | See Note 27A | Yes | 2021 | 2022 | LGIA | 2016 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Pre-Construction | See Note 46A | 2024-05-06 | No | 2024-10-30 | 2025-01-02 | N/A | 1118 | 1118 | See Note 53A | 956.1206 | 152.515 | 458.182 | 332.605 | 0 | 0 | 0 | 943.302 | 0 | 0 | 0 | 0 | 12.8186 | 12.8186 | 5.8211 | See Note 57A | 100% | See Note 59A | 12.8186 | None | 100% | 0% | Column 52: Source = Verified PMWIF (Project Summary v.0)
GIDAP | SP-130 | Goldback Solar Center (TOT943 - Q1619) | 34.280609;-118.903093 | Moorpark, Ventura County | To interconnect the Goldback Solar Center Project 500 MW solar photovoltaic and battery energy storage system (BESS); Install a new 220 kV position Moorpark Substation, gen-tie line, telecommunication, relays, security, metering, real properties, and environmental, permits and licensing; Moorpark CRAS - telecommunication facilities, relays, security and programming. | Transmission line; Substation - breakers, disconnects, bus, tower, relays and communication. | New | N/A | Work Requested by Others | N/A | N/A - New | N/A - New Equipment | Power Flow, Transient, Post Transient, Short Circuit Duty, Relay Coordination and ground grid evaluation. | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | HFTD Tier 3 | No | High Wind Events, Extreme Temperature Conditions Aside from typical weathering of components, seismic activity can impact retrofits, requiring re-inspection | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | 40 | See Note 21A | 220kV/66kV/12kV | See Note 23B | 4 separate WOs | 4 separate CWBS | 8398 | See Note 27A | Yes | 2021 | 2022 | LGIA | 2019 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Engineering more than 50% completed | See Note 46A | 2024-08-29 | No | 2024-07-15 | 2024-11-19 | N/A | 11072 | 11072 | See Note 53A | 8987.6016 | 384 | 3153.2 | 3411 | 2005.8 | 0 | 0 | 8954 | 0 | 0 | 0 | 0 | 33.6016 | 33.6016 | 7.986 | See Note 57A | 100% | See Note 59A | 33.6016 | None | 100% | 0% | Column 52: Source = Verified PMWIF (Project Summary v.2)
GIDAP | SP-131 | Gwent Storage 1 (SCE WDT 1647) | 34.440, -118.578 | Valencia, Los Angeles County | To interconnect the Gwent Storage 1 Project 135 MW battery energy storage system (BESS); Install a new 66 kV position Moorpark Substation, gen-tie line, telecommunication, relay coordination, security, metering, Static Charging Schedule, Short-Circuit Duty Mitigation real properties, and environmental, permits and licensing; Moorpark CRAS - telecommunication facilities, relays, security and programming. | Subtransmission line; Substation - breakers, disconnects, bus, tower, relays and communication. | New | N/A | Work Requested by Others | N/A | N/A - New | N/A - New Equipment | Power Flow, Transient, Post Transient, Short Circuit Duty, Relay Coordination and ground grid evaluation. | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Tier 3 | No | High Wind Events, Extreme Temperature Conditions Substation can be impacted by temperature extremes and seismic activity. | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | 29.4 | See Note 21A | 220 kV | See Note 23B | 6 separate WOs | 6 separate CWBS | 8456 | See Note 27A | Yes | 2022 | 2022 | LGIA | 2019 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Engineering more than 50% completed | See Note 46A | 2024-02-28 | No | 2024-12-31 | 2024-07-08 | N/A | 1666 | 1666 | See Note 53A | 14.8554 | 6 | 6 | 2 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0.85541 | 0.85541 | 0.28256 | See Note 57A | 100% | See Note 59A | 0.85541 | None | 0% | 100% | Column 52: Source = Verified PMWIF (Project Summary v.0)
TPP | SP-132 | Antelope 66 kV CB Upgrade | 34.688, -118.300 | Lancaster, Los Angeles County | Upgrade Antelope 66 kV Circuit Breakers and associated equipment from 40 kA to 50 kA Circuit Breakers | Circuit Breaker | Upgrade | SP-133.01, SP-133.02, SP-133.03, SP-133.04, SP-133.05, SP-133.06, SP-133.07 | Infrastructure Enhancement | Upgrade Breakers | 10/02/2022 | 31 Years | Bank Capacity, Power Flow, Short Circuit Duty SCE Transmission Planning Criteria and Guidelines | N/A | Non-HFRA | No | High Wind Events, Extreme Temperature Conditions Substation can be impacted by temperature extremes and wind. | Demetric Brown, MPO - Programs | See Note 19B | 86.2 | See Note 21A | 500/220kV | See Note 23B | 7 separate WOs | 7 separate CWBS | 8474 | See Note 27A | Yes | 2022 | 2022 | See Note 31A | 2020 - 2021 | 2020 - 2021 | N/A | CAISO 2020-2021 TPP | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Engineering more than 50% completed | See Note 46A | 2024-10-07 | No | 2025-12-31 | 2025-12-31 | N/A | 20082 | 20082 | See Note 53A | 14650.2782 | 1170.745 | 10103.255 | 3285 | 0 | 0 | 0 | 14559 | 0 | 0 | 0 | 0 | 91.2782 | 91.2782 | 37.2635 | See Note 57A | N/A | See Note 59A | 91.2782 | None | 0% | 100% | Column 52: Source = Verified PMWIF (Project Summary v.1)
TPP | SP-133 | Victor 230 kV Switchrack Reconfiguration | 34.506, -117.387 | Victorville, San Bernardino County | Upgrade the Victor 220 kV Bus configuration to improve operational flexibility and mitigate voltage instability risk during planned/unplanned Victor 220 kV bus outages and associated constraints | Switchrack, Circuit Breaker | New, Upgrade | None | Infrastructure Enhancement | System Design Upgrade | 2022-10-09 | 24 Years | Bank Capacity, Power Flow, Short Circuit Duty SCE Subtransmission Planning Criteria and Guidelines. | N/A | Non-HFRA | No | Extreme Temperature Conditions Aside from typical weathering of components, seismic activity can impact retrofits, requiring re-inspection | Demetric Brown, MPO - Programs | See Note 19B | 33.3 | See Note 21A | 220kV, 115kV and 33kV | See Note 23B | 903911198 | CET-ET-TP-RN-695798 | 8506 | See Note 27A | Yes | 2022 | 2022 | See Note 31A | 2021 - 2022 | 2021 | N/A | CAISO 2021-2022 TPP | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Engineering less than 50% completed | See Note 46A | 2024-06-17 | No | 2024-12-31 | 2025-04-30 | N/A | 10000 | 10000 | See Note 53A | 10000 | 49.239 | 1950.761 | 8000 | 0 | 0 | 0 | 10000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | See Note 57A | N/A | See Note 59A | 0 | None | 100% | 0% | Column 52: Source = Project Summary v.0
TPP | SP-134 | Devers 230 kV Reconfiguration Project | 33.935, -116.578 | North Palm Springs, Riverside County | Upgrade the Devers 220 kV Bus configuration to improve operational flexibility and reduce financial impact during a Devers 220 kV Bus outage. | Switchrack, Circuit Breaker, Relays | Upgrade | None | Infrastructure Enhancement | System Design Upgrade | 2022-10-06 | 24 Years | Bank Capacity, Power Flow, Short Circuit Duty SCE Transmission Planning Criteria and Guidelines. | N/A | Non-HFRA | No | High wind events | Brent Gokbudak, MPO-Project Development & Execution | See Note 19B | 98 | See Note 21A | 220 kV | See Note 23B | 3 Separate WOs | CET-ET-TP-RL-847300 | 8473 | See Note 27A | Yes | 2022 | 2022 | See Note 31A | 2021 | 2021 | N/A | CAISO 2021-2022 TPP | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Engineering less than 50% completed | See Note 46A | 2024-06-12 | No | 2025-06-01 | 2024-12-31 | Coordination/sequencing of other projects | 10891 | 10891 | See Note 53A | 10888.0473 | 220.531 | 6919.388 | 3747 | 0 | 0 | 0 | 10886.919 | 0 | 0 | 0 | 0 | 1.1283 | 1.1283 | 0.38249 | See Note 57A | N/A | See Note 59A | 1.1283 | None | 100% | 0% | Column 52: Source = Verified PMWIF (Project Summary v.0)
GIDAP | SP-135 | Atlas Solar Project (TOT870Q1402) | 33.56, -133.56 | Salome, La Paz County, Arizona | To interconnect the Atlas Solar Project, 3200MW solar photovoltaic and battery energy storage facility. Install telecommunications, relays, power system controls; West of Colorado River CRAS - relays, telecommunication, power system controls. | Transmission line; Substation - breakers, disconnects, bus, tower, relays and communication. | New | None | Work Requested by Others | N/A | N/A - New | N/A - Installing New Assets | Power Flow, Transient, Post Transient, Short Circuit Duty, Relay Coordination and ground grid evaluation. | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Non HFRA | See Note 16C | No Significant Environmental Factors | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | 77 | 500kV | See Note 22A | See Note 23B | 2 Separate WOs | CET-ET-CR-WC-833600 | 8336 | See Note 27A | Yes | 2020 | 2022 | LGIA | 2019 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Engineering more than 50% completed | See Note 46A | 2024-07-03 | No | 2022-10-01 | 2024-09-24 | Not readily available | 1754 | 1754 | See Note 53A | 1601.0391 | 371.545 | 400 | 350 | 144.367 | 0 | 0 | 1265.912 | 0 | 0 | 0 | 239.0593 | 96.0678 | 335.1271 | 138.8065 | See Note 57A | 100% | See Note 59A | 46.3271 | None | 100% | 0% | Column 52: Source = (Two separate work orders) 903269992 = PMWIF (Project Summary V.1) 903207593 = (Project Summary V.0)
GIDAP | SP-136 | SEGS Expansion Hybrid Project TOT914 (Q1617) | 35.039921, -117.347748 | Hinkley, San Bernardino County | To interconnect the SEGS Expansion Hybrid Project, 150MW solar photovoltaic and battery energy storage system. Install telecommunications, relays, metering, programming, power system controls, security, real properties, environmental, permits, and licensing. | Transmission line; Substation - breakers, disconnects, bus, tower, relays and communication. | New | None | Work Requested by Others | N/A | N/A - New | N/A - Installing New Assets | Power Flow, Transient, Post Transient, Short Circuit Duty, Relay Coordination and ground grid evaluation. | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Non HFRA | See Note 16C | High Wind Events, Extreme Temperature Conditions | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | 20.6 | 220kV | See Note 22A | See Note 23B | 903334019 | CET-ET-CR-WC-834302 | 8343 | See Note 27A | Yes | 2020 | 2022 | LGIA | No | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Pre-Construction | See Note 46A | 2025-01-02 | No | 2023-03-01 | 2025-03-26 | Coordination with other projects and material delays | 2502 | 2502 | See Note 53A | 105.2538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.2302 | 79.0237 | 105.2538 | 11.6952 | See Note 57A | 100% | See Note 59A | 105.2538 | None | 0% | 100% | Column 52: Source = PMWIF (Project Summary V.0)
GIDAP | SP-137 | Aratani Solar (TOT904/Q1604) | 34.985706, -117.633395 | Boron, Kern County | To interconnect Aratani Solar Center 2 project, 200MW solar photovoltaic and battery energy storage generator facility. Install a new 220kV position Kramer Substation, gen-tie line, relays, telecommunications, metering, programming, power system controls, security, real properties, environmental, permits, and licensing; Mojave Desert RAS and North of Lugo CRAS - relays, programming, telecommunications, power system controls, security. | Substation - relays and communication. | New | SP-41 | Work Requested by Others | N/A | N/A - New | N/A - Installing New Assets | Power Flow, Transient, Post Transient, Short Circuit Duty, Relay Coordination and ground grid evaluation. | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Non HFRA | See Note 16C | No Significant Environmental Factors | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | 20.6 | 220kV | See Note 22A | See Note 23B | 3 Separate WOs | CET-ET-TP-RN-838000 | 8380 | See Note 27A | Yes | 2021 | 2022 | LGIA | 2021 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Planning | See Note 46A | 2025-06-02 | No | 2024-08-01 | 2025-06-27 | The Schedule is under Development | 1243 | 1243 | See Note 53A | 1087.5647 | 56.45 | 443.091 | 287.27 | 276.124 | 0 | 0 | 1062.935 | 0 | 0 | 0 | 9.9772 | 14.6525 | 24.6297 | 6.6949 | See Note 57A | 100% | See Note 59A | 24.6297 | None | 100% | 0% | Column 52: Source = PMWIF (Project Summary V.0)
GIDAP | SP-138 | TOT903 - Q1625 - Angeleno Solar Farm | 34.58857, -118.009261 | Palmdale, Los Angeles County | To interconnect Angeleno Solar Farm project 1150MW hybrid solar photovoltaic and battery energy storage system (BESS). Install a new 500kV position Vincent Substation, gen-tie line, relays, telecommunications, metering, power system controls, real properties, environmental, permits, and licensing. | Transmission line; Substation - breakers, disconnects, bus, tower, relays and communication. | New | None | Work Requested by Others | N/A | N/A - New | N/A - Installing New Assets | Power Flow, Transient, Post Transient, Short Circuit Duty, Relay Coordination and ground grid evaluation. | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Non HFRA | See Note 16C | High Wind Events | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | 55 | 500kV | See Note 22A | See Note 23B | 903659196 | CET-ET-CR-WC-843401 | 8434 | See Note 27A | Yes | 2022 | 2023 | LGIA | 2022 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Engineering less than 50% completed | See Note 46A | 2025-10-01 | No | 2026-04-01 | 2027-12-31 | POCO location recently defined/extended major material times Change of Customer COD | 7494 | 7494 | See Note 53A | 6184.5949 | 131.562 | 967.27 | 2566.461 | 359.487 | 2150.778 | 0 | 6175.558 | 0 | 0 | 0 | 0 | 9.0368 | 9.0368 | 2.4009 | See Note 57A | 100% | See Note 59A | -1179.5811 | None | 100% | 0% | Column 52: Source = PMWIF (Project Summary V.0)
GIDAP | SP-139 | Lycan Solar (TOT921; Q1643) | 33.7083, -115.27949 | Desert Center, Riverside County | To interconnect Lycan Solar project, 400MW solar photovoltaic and battery energy storage system (BESS). Install a new 500kV position Redbluff Substation, gen-tie line, relays, telecommunications, metering, power system controls, security, real properties, environmental, permits, and licensing; West of Colorado River CRAS - relays, telecommunications, power system controls. | Transmission line; Substation - breakers, disconnects, bus, tower, relays and communication. | New | None | Work Requested by Others | N/A | N/A - New | N/A - Installing New Assets | Power Flow, Transient, Post Transient, Short Circuit Duty, Relay Coordination and ground grid evaluation. | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Non HFRA | See Note 16C | High Wind Events, Extreme Temperature Conditions | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | 75.7 | 500kV | See Note 22A | See Note 23B | 2 separate WOs | 2 Separate CWBS | 8457 | See Note 27A | Yes | 2023 | 2023 | LGIA | 2023 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Planning | See Note 46A | 2025-06-12 | No | 2025-10-15 | 2025-07-10 | N/A | 8415 | 8415 | See Note 53A | 6900.3 | 180.332 | 1112.736 | 3148.2 | 2459.032 | 0 | 0 | 6900.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | See Note 57A | 100% | See Note 59A | 0 | None | 100% | 0% | Column 52: Source = (Two separate work orders) 903803892 = PMWIF (Project Summary V.0) 903803894 = (Project Summary V.0)
GIDAP | SP-140 | Keyhole Wind (TOT983) | 34.886769. -118.482995 | Rosamond, Kern County | To interconnect the Keyhole Wind project, 100MW wind generating facility. Install new 220kV position Whirlwind Substation, gen-tie line, relays, telecommunications, metering, power system controls, security, real properties, environmental, permits, and licensing; Tehachapi CRAS and New South of Vincent CRAS - relays, telecommunications power system controls. | Transmission line; Substation - breakers, disconnects, bus, tower, relays and communication. | New | None | Work Requested by Others | N/A | N/A - New | N/A - Installing New Assets | Bank Capacity, Power Flow, Short Circuit Duty SCE Transmission Planning Criteria and Guidelines | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Tier 2 | See Note 16C | No Significant Environmental Factors | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | 92 | 220kV | See Note 22A | See Note 23B | 6 separate WOs | CET-ET-CR-WC-848300 | 8483 | See Note 27A | Yes | 2022 | 2024 | LGIA | 2022 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Engineering less than 50% completed | See Note 46A | 2025-02-03 | No | 2026-04-15 | 2027-12-15 | Material Delay | 3956 | 3956 | See Note 53A | 2611.7256 | 85.513 | 329.721 | 602.173 | 611.665 | 111.646 | 869.299 | 2610.017 | 0 | 0 | 0 | 0 | 1.7086 | 1.7086 | 0.84491 | See Note 57A | 100% | See Note 59A | -269.5454 | None | 100% | 0% | Column 52: Source - PMWIF (Project Summary V.0)
GIDAP | SP-141 | Delamar Energy Storage (TOT995; Q1796) | 35.849166, -114.995833 | Boulder City, Clark County, Nevada | To interconnect the Delamar Energy Storage project, 250MW battery energy storage system (BESS). Install a new 220kV position Eldorado Substation, gen-tie line, relays, telecommunications, metering, power system controls, real properties, environmental, permits, and licensing; Lugo-Victorville CRAS and Ivanpah RAS - relays, telecommunications, programming, power system controls, security, real properties, environmental, permits, and licensing. | Transmission line; Substation - breakers, disconnects, bus, tower, relays and communication. | New | None | Work Requested by Others | N/A | N/A - New | N/A - Installing New Assets | Power Flow, Transient, Post Transient, Short Circuit Duty, Relay Coordination and ground grid evaluation. | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Non HFRA | See Note 16C | Extreme Temperature Conditions | Brent Gokbudak, MPO-Project Development & Execution | See Note 19B | 86.7 | 220kV | See Note 22A | See Note 23B | 2 separate WOs | CET-ET-CR-WC-479102 | 8498 | See Note 27A | Yes | 2022 | 2024 | LGIA | 2022 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Planning | See Note 46A | 2025-04-08 | No | 2026-02-01 | 2025-05-05 | N/A | 4584 | 4584 | See Note 53A | 3885 | 26 | 625 | 1374 | 1452 | 408 | 0 | 3885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | See Note 57A | 100% | See Note 59A | 0 | None | 100% | 0% | Column 52: Source - PMWIF (Project Summary V.0)
GIDAP | SP-142 | Roadhouse Storage Project (TOT1008/Q1768) | 34.008805, -117.572009 | Ontario, San Bernardino County | To interconnect the Roadhouse Storage project, 300MW battery energy storage system (BESS). Install a new 220kV position Mira Loma Substation, gen-tie line, relays, telecommunications, metering, power system controls, security, real properties, environmental, permits, and licensing. | Transmission line; Substation - breakers, disconnects, bus, tower, relays and communication. | New | None | Work Requested by Others | N/A | N/A - New | N/A - Installing New Assets | Power Flow, Transient, Post Transient, Short Circuit Duty, Relay Coordination and ground grid evaluation. | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Non HFRA | See Note 16C | High Wind Events | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | 102.1 | 230kV | See Note 22A | See Note 23B | 60286 | CET-ET-CR-WC-479102 | 8525 | See Note 27A | Yes | 2022 | 2024 | LGIA | 2022 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Planning | See Note 46A | 2026-06-08 | No | 2025-12-01 | 2027-01-27 | Material Delay | 5937 | 5937 | See Note 53A | 7290.62 | 184.776 | 910 | 3644.127 | 2551.717 | 0 | 0 | 7290.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | See Note 57A | 100% | See Note 59A | 0 | None | 100% | 0% | Column 52: Source - PMWIF (Project Summary V.4)
N/A | SP-143 | El Segundo Sub: Remove CB 432 and 442 including associated equipment at 220 kV Position # 3 and #4 | 33.908, -118.423 | Manhattan Beach, Los Angeles County | El Segundo Sub: Remove CB 432 and 442 including associated equipment at 220 kV Position # 3 and #4 Reconfigure relays scheme | Electric System Planning | Upgrade | None | Removal | System Operations | 03/02/2021 | 55+ | Removal due to criticality and age | See Note 14A | Non HFRA | See Note 16C | Salt Corrosion (Coastal Areas) | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | 2.1 | See Note 21A | 220 kV | See Note 23B | 903035789 | CET-ET-AF-CF-827200 | 8272 | See Note 27A | Yes | 2020 | 2021 | Annual Capital Operating Plan Process | N/A | N/A | N/A | N/A | See Col. 37 | 2021 = 1,558 2022 = 5 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2021-03-08 | No | 2021-06-01 | 2021-05-07 | N/A | 416 | 416 | See Note 53A | 1562.7297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.1281 | 1484.9711 | 4.6306 | 1562.7297 | 189.2832 | See Note 57A | N/A | See Note 59A | -8.7766e-14 | None | 100% | 0% | Column 52: Source = PMWIF (Project Summary V.0)
GIDAP | SP-144 | ED&P scope of work for 500kV Gen-Tie TOT905/Q1647 Angora Solar Farm | 35.135326, -114.679725 | Laughlin, Clark County, Nevada | To interconnect the Angora Solar Farm project, 700MW solar photovoltaic and battery energy storage system (BESS). Install a new 500kV position Mohave Switchyard, gen-tie line, telecommunications, metering, power system controls, security, real properties, environmental, permits, and licensing; Lugo-Victorville CRAS - relays, programming, telecommunications, power system controls, real properties. | Transmission line; Substation - breakers, disconnects, bus, tower, relays and communication. | New | SP-115 | Work Requested by Others | N/A | N/A - New | N/A - Installing New Assets | Power Flow, Transient, Post Transient, Short Circuit Duty, Relay Coordination and ground grid evaluation. | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Non HFRA | See Note 16C | Extreme Temperature Conditions | Brent Gokbudak, MPO-Project Development & Execution | See Note 19B | 11.5 | 500kV | See Note 22A | See Note 23B | 7 separate WOs | 2 Separate CWBS | 8433 | See Note 27A | Yes | 2021 | 2023 | LGIA | 2021 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Planning | See Note 46A | 2025-06-12 | No | 2025-06-02 | 2025-07-10 | N/A | 1511 | 1511 | See Note 53A | 1238 | 30 | 233 | 542 | 433 | 0 | 0 | 1238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | See Note 57A | 100% | See Note 59A | -600 | None | 100% | 0% | Column 52: Source = PMWIF (Project Summary V.0)
GIDAP | SP-145 | Quartzite Solar 11 (TOT872/Q1526) | 33.573914, -114.77482 | Blythe, Riverside County | To interconnect Quartzite Solar 11 project, 150MW solar photovoltaic and batter energy storage system (BESS). Install a new 220kV position Colorado River Substation, relays, gent-tie line, telecommunications, metering, power system controls, security, real properties, environmental, permits, and licensing; West of Colorado River CRAS - relays, programming, telecommunications, power system controls, security. | Transmission line; Substation - breakers, disconnects, bus, tower, relays and communication. | New | SP-55 | Work Requested by Others | N/A | N/A - New | N/A - Installing New Assets | Power Flow, Transient, Post Transient, Short Circuit Duty, Relay Coordination and ground grid evaluation. | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Non HFRA | See Note 16C | High Wind Events, Extreme Temperature Conditions | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | 77 | 230kV | See Note 22A | See Note 23B | 903506481 | CET-ET-TP-RN-838100 | 8381 | See Note 27A | Yes | 2021 | 2022 | LGIA | 2021 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Canceled | See Note 46A | 2023-07-10 | No | 2023-07-01 | Canceled | N/A | 522 | 522 | See Note 53A | 785.6488 | 12.9 | 5.5 | 758.796 | 0 | 0 | 0 | 777.196 | 0 | 0 | 0 | 1.7218 | 6.731 | 8.4528 | 3.6492 | See Note 57A | 100% | See Note 59A | 8.4528 | None | 100% | 0% | Column 52: Source = PMWIF (Project Summary V.0)
GIDAP | SP-146 | TOT830/Q1302 Sol Catcher | 33.632078, -114.593966 | Blythe, Riverside County | To interconnect the Sol Catcher project, 213.50MW solar photovoltaic and battery energy storage system (BESS). Install a new 220kV position Red Bluff Substation, relays, gen-tie line, telecommunications, metering, power system controls, real properties, environmental, permits, and licensing; West of Colorado River CRAS - relays, programming, telecommunications, power system controls, real properties, environmental, permits, and licensing. | Transmission line; Substation - breakers, disconnects, bus, tower, relays and communication. | New | SP-44, SP-39 | Work Requested by Others | N/A | N/A - New | N/A - Installing New Assets | Power Flow, Transient, Post Transient, Short Circuit Duty, Relay Coordination and ground grid evaluation. | Because this was triggered by new generation interconnection requests in the CAISO GIDAP, no other alternatives were considered. | Non HFRA | See Note 16C | High Wind Events | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | See Note 19B | 75.7 | 230kV | See Note 22A | See Note 23B | 903531605 | CET-ET-CR-WC-839202 | 8392 | See Note 27A | Yes | 2021 | 2022 | LGIA | 2021 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Canceled | See Note 46A | 2023-03-06 | No | 2023-08-01 | Canceled | N/A | 550 | 550 | See Note 53A | 467.3876 | 345 | 3.656 | 117.472 | 0 | 0 | 0 | 466.128 | 0 | 0 | 0 | 0.21282 | 1.0468 | 1.2596 | 0.47232 | See Note 57A | 100% | See Note 59A | 1.2596 | None | 100% | 0% | Column 52: Source = PMWIF (Project Summary V.0)
TPP | SP-147 | Barre 230 kV Switchrack Conversion to Breaker-And-A-Half Project | 33.8087, -117.982 | Stanton, Orange County | Convert Barre 230kV switchrack to breaker-and-a-half configuration, add sectionalizing CBs and split Barre 230kV to lower SCD. | Transmission line relocations, substation - breakers | New | N/A | Infrastructure Enhancement, Operations Support | N/A | 2023-10-14 | N/A | Power Flow, Transient, Post Transient, and Short Circuit Duty | Rebuilding switchrack to 80 kA would require rebuilding the entire switchrack. | Non-HFRA | See Note 16C | General Urban/Suburban Impacts | Demetric Brown, MPO - Programs | N/A | 18.6 | 220 kV | 220 kV, 66 kV | See Note 23B | 4 separate WOs | 2 Separate CWBS | 8519 | See Note 27A | Yes | 2023 | 2022 | Annual Capital Operating Plan Process | 2022 | 2023 | N/A - see column 33 | http://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Engineering less than 50% completed | See Note 46A | 2025-05-29 | No | 2026-06-30 | 2026-06-30 | N/A | 43600 | 41856 | See Note 53A | 41830.3892 | 546.0478 | 3715.386 | 12933.6921 | 12285.8991 | 12349.3642 | 0 | 41830.3892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | See Note 57A | N/A | See Note 59A | 0 | None | 100% | 0% | 49 and 52 Origination = Verified PMWIF (Project Summary V.1) PMWIF Approval Date = 02/03/2023 Latest Approved Project Summary Version = V.1 Original Project Cost updated per FRM
GIDAP | SP-148 | Gracesol Substation: Colorado River Substation-(IRNU-Shared) - TOT1006 (Q1761) Grace Energy Center | 33.652683, -114.675482 | Blythe, Riverside County | The IC, Next Era Energy, is proposing to interconnect to Colorado River 220 kV Substation with a POI of 500 MW consisting of Solar PV and Battery Energy Storage Systems. | New Generation Interconnection Customer | Install facilities for TOT Generation Station | N/A | Generation Interconnection | N/A | 2023-10-11 | N/A | Power Flow, Transient, Post Transient, and Short Circuit Duty | N/A | Non-HFRA | See Note 16C | Extreme Temperature Conditions | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | 15 | 2843 | 220 kV | 220/34.5 kV, 280 MVA | See Note 23B | 3 Separate WOs | CET-ET-TP-RN-695798 | 8546 | See Note 27A | Yes | 2023 | 2023 | LGIA | 2023 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | Not Yet Operational | Not Yet Operational | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | See Note 46A | 2025-08-11 | No | 2026-07-01 | 2026-04-16 | N/A | 8997 | 8997 | See Note 53A | 3375.122 | 79.775 | 488.628 | 1585.54 | 39.887 | 1181.292 | 0 | 3375.122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | See Note 57A | 100% | See Note 59A | 0 | None | 100% | 0% | 49 and 52 Origination = Verified PMWIF (Project Summary V.0) PMWIF Approval Date = 07/14/2023 Latest Approved Project Summary Version = V.0
GIDAP | SP-149 | Bolt Substation: Colorado River Substation-(IRNU-Shared) - TOT1013 (Q1757) Cobalt Project | 33.57676, -114.82714 | Blythe, Riverside County | The IC, RE Colbalt LLC, is proposing to interconnect to Colorado River 220 kV Substation with a POI of 250 MW consisting of Solar PV and Battery Energy Storage Systems. | New Generation Interconnection Customer | Install facilities for TOT Generation Station | N/A | Generation Interconnection | N/A | 2023-10-11 | N/A | Power Flow, Transient, Post Transient, and Short Circuit Duty | N/A | Non-HFRA | See Note 16C | Extreme Temperature Conditions | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | 1 | 1182 | 220, 34.5, 12.47 kV | 220/34.5 kV, 140 MVA | See Note 23B | 6 Separate WOs | CET-ET-TP-RN-695798 | 8547 | See Note 27A | Yes | 2023 | 2023 | LGIA | 2022 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | Not Yet Operational | Not Yet Operational | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | See Note 46A | 2025-03-03 | No | 2026-05-01 | 2026-04-30 | The Schedule is under Development | 12547 | 12547 | See Note 53A | 6200.722 | 100.761 | 1209.142 | 2720.567 | 2170.252 | 0 | 0 | 6200.722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | See Note 57A | 100% | See Note 59A | 0 | None | 100% | 0% | 49 and 52 Origination = Verified PMWIF (Project Summary V.0) PMWIF Approval Date = 07/14/2023 Latest Approved Project Summary Version = V.0
TPP | SP-150 | Mira Loma 500 kV CB Upgrade | 34.0084, -117.565 | Ontario, San Bernardino County | Replace four (4) 50 kA CBs at Mira Loma 500kV with new 63kA rated CBs to mitigate SCD. | substation - breakers | replacement, upgrade | N/A | Infrastructure Enhancement, Operations Support | Substation capacity | 2023-10-08 | 31 | Power Flow, Short Circuit Duty | Develop operating procedure to open elements in real time which may be burdensome to Grid Operators, may not be possible due to other real time system issues, and could result in significant curtailment of renewable resources. | Non-HFRA | See Note 16C | General Urban/Suburban Impacts | Demetric Brown, MPO - Programs | N/A | 100 | N/A | 500 kV, 220 kV, 66 kV | See Note 23B | 904143442 | CET-ET-TP-RN-855700 | 8557 | See Note 27A | Yes | 2023 | 2023 | Annual Capital Operating Plan Process | 2023 | 2023 | N/A - see column 33 | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Planning | See Note 46A | 2028-05-18 | No | 2026-12-31 | 2028-12-31 | 5 year lead time for 500 kV CB | 10000 | 10000 | See Note 53A | 10000 | 5 | 300 | 2000 | 7695 | 0 | 0 | 10000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | See Note 57A | N/A | See Note 59A | 0 | None | 100% | 0% | 49 and 52 Origination = Verified PMWIF (Project Summary V.1) PMWIF Approval Date = 06/19/2023 Latest Approved Project Summary Version = V.1
TPP | SP-151 | New Lugo 3AA 500/230 kV Bank | 34.366383, -117.369108 | Lugo, San Bernardino County | Lugo Substation: Install four (4) single phase transformer units to create one (1) new No. 3AA 500/220 kV transformer bank. Equip 500 kV Bank Position (Position 1X - TBD) with double breakers, associated equip. and structures Extend 220 kV double operating bus Equip 220 kV Bank Position (Position 1 - TBD) with double breakers, associated equip. and structures. | substation - transformer | New Installation | N/A | Capacity Increase | Reliability of Transmission facilities | 2023-10-18 | N/A | Power Flow, Transient, Post Transient, and Short Circuit Duty | Llano-Kramer 500 kV Substation and New Circuit (Estimate Billions of Dollars) | Tier 2 | See Note 16C | High Wind and Extreme Temp | Demetric Brown, MPO - Programs | N/A | 60 | 500/220 kV | 500/220 kV, 1120 MVA | See Note 23B | 904187434 | CET-ET-TP-RN-695798 | 8600 | See Note 27A | Yes | 2023 | 2023 | Annual Capital Operating Plan Process | 2023 | 2023 | 2023 | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Planning | See Note 46A | 2027-03-01 | No | 2027-12-31 | 2027-12-30 | N/A | 70000 | 70000 | See Note 53A | 70000 | 0 | 1400 | 7000 | 14000 | 47600 | 0 | 70000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | See Note 57A | N/A | See Note 59A | 0 | None | 100% | 0% | 49 and 52 Origination = Verified PMWIF (Project Summary V.2) PMWIF Approval Date = 08/10/2023 Latest Approved Project Summary Version = V.2
TPP | SP-152 | New Coolwater A 115/230 kV Bank | 34.863128, -116.854228 | Daggett, San Bernardino County | Coolwater Substation:Install one (1) new No. 1A 230/115 kV transformer bank Equip one (1) 230 kV Bank Position (Position 6 - TBD) with breaker and a half scheme and install associated equip. and structures. Equip one (1) 115 kV Bank Position (Position 10 - TBD) with double breakers and install associated equip. and structures. | substation - transformer | New Installation | N/A | Capacity Increase | Reliability of Transmission facilities | 2023-10-10 | N/A | Power Flow, Transient, Post Transient, and Short Circuit Duty | N/A | Non-HFRA | See Note 16C | High Wind and Extreme Temp | Demetric Brown, MPO - Programs | N/A | 7 | 220/115 kV | 220/115 kV, 280 MVA | See Note 23B | 904164457 | CET-ET-TP-Rl-695798 | 8564 | See Note 27A | Yes | 2023 | 2023 | Annual Capital Operating Plan Process | 2023 | 2021 | 2023 | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Planning | See Note 46A | 2027-06-28 | No | 2026-12-31 | 2027-12-10 | Resource Constraints and Material Delays | 47000 | 47000 | See Note 53A | 47000 | 0 | 200 | 11832 | 34968 | 0 | 0 | 47000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | See Note 57A | N/A | See Note 59A | 0 | None | 100% | 0% | 49 and 52 Origination = Verified PMWIF (Project Summary V.2) PMWIF Approval Date = 08/10/2023 Latest Approved Project Summary Version = V.3 V.3 requested by LRP Substation to reflect a 04/30/2027 Need date/Operating Date as 12/31/2026 date may not be feasible
TPP | SP-153 | New Control 115 kV Shunt Reactor | 37.336231, -118.481047 | Bishop, Inyo County | Inyo 230 kV Substation: Install a new 25 MVAR shunt reactor. Install one 220 kV CB, one set of group operated disconnects, and associated equipment required for the installation of the 25 MVAR shunt reactor. | substation - shunt reactor | New Installation | N/A | Reliability of Transmission facilities | N/A | 2023-10-09 | N/A | Power Flow, Transient, Post Transient, and Short Circuit Duty | N/A | Tier 2 | See Note 16C | High Wind and Extreme Temp | Demetric Brown, MPO - Programs | N/A | 3 | 230/115 kV | 230/115 kV | See Note 23B | 904188170 | CET-ET-TP-Rl-695798 | 8599 | See Note 27A | Yes | 2023 | 2023 | Annual Capital Operating Plan Process | 2023 | 2023 | 2023 | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | On Hold | See Note 46A | 2026-06-01 | No | 2026-12-31 | 2026-09-25 | N/A | 21000 | 21000 | See Note 53A | 4000 | 0 | 560 | 800 | 2640 | 0 | 0 | 4000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | See Note 57A | N/A | See Note 59A | 0 | None | 100% | 0% | 49 and 52 Origination = Verified PMWIF (Project Summary V.4) PMWIF Approval Date = 08/10/2023 Latest Approved Project Summary Version = V.4
TPP | SP-154 | New Serrano 4AA 500/230 kV Bank and 230 kV GIS Rebuild | 33.8298, -117.79 | Villa Park, Orange County | Install a 4th 500/230kV 1120/1344 MVA Transformer bank at Serrano Substation to address Serrano Transformer Bank overload under the loss of any two of the three Serrano 500/230 kV transformer banks (P6). The 230 kV switchrack will be rebuilt to 80 kA. | Transmission line - relocation, substation-GIS rebuild, breakers | replacement, upgrade | N/A | Infrastructure Enhancement, Operations Support | Substation capacity | 2023-09-20 | Approximately 1983 (Serrano 220 kV GIS switchgear) | Power Flow, Transient, Post Transient, and Short Circuit Duty | Continue to use CAISO operating procedure that opens two 230 kV transmission lines in Orange County and/or build new 500 kV transmission line and 500/230 kV transformer bank into Orange County. | Tier 2 | See Note 16C | General Urban/Suburban Impacts | Demetric Brown, MPO - Programs | N/A | 19.3 | 500/220 kV | 500/220 kV, 1120 MVA | See Note 23B | 904187129 | CET-ET-TP-Rl-695798 | 8567 | See Note 27A | Yes | 2023 | 2023 | Annual Capital Operating Plan Process | 2023 | 2023 | N/A - see column 33 | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | Not Yet Operational | Not Yet Operational | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | See Note 46A | 2026-06-15 | No | 2027-12-31 | 2027-12-30 | N/A | 120000 | 120000 | See Note 53A | 120000 | 0 | 1920 | 12000 | 24000 | 82080 | 0 | 120000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | See Note 57A | N/A | See Note 59A | 0 | None | 100% | 0% | 49 and 52 Origination = Verified PMWIF (Project Summary V.3) PMWIF Approval Date = 08/31/2023 Latest Approved Project Summary Version = V.3
TPP | SP-155 | Sylmar Sub: Replace 230kV/220kV Transformer with one rated for 1290 MVA normal and 1610 MVA Emergency (Procurement Only) | 34.311814, -118.480911 | Sylmar, Los Angeles County | Replace 230/220 kV transformer bank F at Sylmar substation with 1,290 MVA transformer. LADWP will replace bank E at Sylmar substation. | substation - transformers | replacement, upgrade | N/A | Capacity Increase | Reliability of Transmission facilities | Performed by LADWP | 55 years (Factory test report dated 1968) | Power Flow, Transient, Post Transient, and Short Circuit Duty | Reconfigure the switchyard by adding one-and-half breaker scheme (eliminated due to space constraints at Sylmar Substation) | Non-HFRA | See Note 16C | General Urban/Suburban Impacts | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | N/A | 46.4 | 230/220 kV | 230/220 kV, 1290 MVA | See Note 23B | 904209302 | CET-ET-TP-RN-695798 | 8602 | See Note 27A | Yes | 2023 | 2023 | Annual Capital Operating Plan Process | 2023 | 2023 | N/A - see column 33 | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Planning | See Note 46A | 2024-10-31 | No | 2026-06-01 | 2024-12-02 | N/A | 23000 | 23000 | See Note 53A | 23000 | 0 | 1719.314 | 14969.263 | 6311.423 | 0 | 0 | 23000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | See Note 57A | N/A | See Note 59A | 0 | None | 100% | 0% | 49 and 52 Origination = Verified PMWIF (Project Summary V.0) PMWIF Approval Date = 09/12/2023 Latest Approved Project Summary Version = V.0
TPP | SP-156 | Antelope - Whirlwind - Raise approximately 9 towers in order to fix ground clearance and increase line rating to 3421/3880 MVA | 34.685404, -118.297530 | Del Sur, Los Angeles County | Upgrade Antelope-Whirlwind 500 kV line by increasing the ground clearance for nine (9) towers to increase line rating to 3421/3880 MVA. | transmission line - mitigate ground clearance | upgrade | N/A | Capacity Increase | Reliability of Transmission Line | 2023-09-29 | 50 years old, towers originally installed in 1973 | Power Flow, Transient, Post Transient | Not recommended due to criteria violations. | Non-HFRA | See Note 16C | General Urban/Suburban Impacts | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | 9 | N/A | 500 kV | 500/220 kV, 1120 MVA | See Note 23B | 904186957 | CET-ET-TP-Rl-695798 | 8576 | See Note 27A | Yes | 2023 | 2023 | Annual Capital Operating Plan Process | 2023 | 2023 | N/A - see column 33 | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | Not Yet Operational | Not Yet Operational | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | See Note 46A | 2024-12-06 | No | 2025-12-31 | 2025-12-31 | N/A | 6018 | 6018 | See Note 53A | 5998 | 0 | 880 | 5118 | 0 | 0 | 0 | 5998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | See Note 57A | N/A | See Note 59A | 0 | None | 100% | 0% | 49 and 52 Origination = Verified PMWIF (Project Summary V.1) PMWIF Approval Date = 09/14/2023 Latest Approved Project Summary Version = V.1
TPP | SP-157 | Mesa - Del Amo - Serrano 500 kV Upgrade | N/A | Orange County & Los Angeles County | New 500 kV switchyard at Del Amo complete with three (3) 500/230 kV transformers. Utilize the existing conductor on Mesa-Mira Loma 500 kV line and build approximately a 2 mile new section into Mesa and an 13 mile new 500 kV line to Serrano. Interconnect the new Mesa-Serrano 500 kV line with 2 new lines from Del Amo to form the Del Amo-Mesa and Del Amo-Serrano 500 kV lines. Loop Alamitos-Barre No.1 and No.2 230 kV lines into Del Amo substation | substation - new, transmission line - new, relocation | new, upgrade | N/A | Capacity Increase | Reliability of Transmission Line | 2023-10-11 | Pre-1983 for both Mesa and Del Amo 220 kV switchracks. Approximately 1983 for Serrano 220 kV GIS switchgear Mesa - Mira Loma 500 kV line was energized when Mira Loma - Vincent 500 kV line looped into Mesa Substation in 2022. Original Mira Loma - Vincent 500 kV (Pre-Mesa 500 kV) line was energized around 2012. | Power Flow, Transient, Post Transient, and Short Circuit Duty | Serrano-Mesa-Del Amo 500 kV Development ($1.2 billion) HVDC alternatives involving 2500 MW converter station at Del Amo identified to address constraints in SDG&E and Eastern areas ($7-7.8 billion) | Tier 2, Tier 3 | See Note 16C | General Urban/Suburban Impacts | John Keelin, MPO - Project Dev. & Execution | 13 | N/A | 500 kV | 500/220 kV, 1120 MVA | See Note 23B | 23 Separate WOs | CET-ET-TP-RN-695798 | 8575 | See Note 27A | Yes | 2023 | 2023 | Annual Capital Operating Plan Process | 2023 | 2023 | N/A - see column 33 | https://www.caiso.com/Documents/ISO-Board-Approved-2022-2023-Transmission-Plan.pdf | Not Yet Operational | Not Yet Operational | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | See Note 46A | Not Available | No | 2033-12-31 | 2033-12-31 | N/A | 1124995 | 1124995 | See Note 53A | 1125003.598 | 0 | 2000.001 | 4849.412 | 6417.427 | 6410.366 | 1105326.392 | 1125003.598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | See Note 57A | N/A | See Note 59A | 0 | None | 100% | 0% | 49 and 52 Origination = Verified PMWIF (Project Summary V.2) PMWIF Approval Date = 08/28/2023 Latest Approved Project Summary Version = V.2
GIDAP | SP-158 | Ellis Ph2 RLA SCE:Re | 33.685251, -117.945258 | Huntington Beach, Orange County | The IC, AES Huntington Beach Energy, LLC and AES Huntington Beach, L.L.C., is proposing to interconnect to Ellis 220 kV Substation with a POI of 888.5 MW consisting of combustion turbine generators, steam turbine generators and gas turbine generators. This project is to remove equipment from the Radial Lines Agreement that is no longer necessary for this project. | Removal of equipment - removing of position on Ellis 220 kV Substation | Removal of equipment no longer necessary for new facilities for TOT Generation Station | N/A | Generation Interconnection | N/A | 2018-12-15 | 57 Years (only removal) | Power Flow, Transient, Post Transient, and Short Circuit Duty | N/A | Non-HFRA | See Note 16C | Salt Corrosion (Coastal Areas) | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | 4.2 | N/A | 220 kV | N/A | See Note 23B | 902179842 | CET-ET-CR-WS-803800 | 8038 | See Note 27A | Yes | 2017 | 2017 | LGIA | 2017 | NA, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | See Col. 37 | 2019 = 63 | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Operational | See Note 46A | 2018-12-26 | No | 2019-03-05 | 2019-01-04 | N/A | 69 | 17.388 | See Note 53A | 111.7687 | 0 | 6.3 | 42.2327 | 0 | 0 | 0 | 48.5327 | 11.654 | 51.5821 | 0 | 0 | 0 | 63.2361 | 26.5165 | See Note 57A | 100% | See Note 59A | 0 | None | 100% | 0% | 49 and 52 Origination = Verified PMWIF (Project Summary V.5) PMWIF Approval Date = 08/18/2017 Latest Approved Project Summary Version = V.14
GIDAP | SP-159 | VISTA RNU-SCD | 34.020344, -117.332386 | Grand Terrace, San Bernardino County | Vista RNU-SCD Ground grid study | substation - ground grid | Study | N/A | Generation Interconnection | N/A | 2023-10-15 | N/A | Power Flow, Transient, Post Transient, and Short Circuit Duty | N/A | Non-HFRA | See Note 16C | Not Applicable | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | N/A | N/A | 115 kV | N/A | See Note 23B | 903901445 | CET-ET-TP-RN-837603 | 8376 | See Note 27A | Yes | 2021 | 2021 | LGIA | 2021 | NA, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Pre-construction | See Note 46A | 2024-01-19 | No | 2023-12-31 | 2024-02-16 | N/A | 51 | 51 | See Note 53A | 43.3539 | 0.117 | 3.55 | 39.591 | 0 | 0 | 0 | 43.258 | 0 | 0 | 0 | 0 | 0.09585 | 0.09585 | 0.00361 | See Note 57A | 100% | See Note 59A | 0.09585 | None | 100% | 0% | 49 and 52 Origination = Project Summary V.1 PMWIF Approval Date = 08/19/2021 Latest Approved Project Summary Version = V.1 Work order 903901445 is part of "Transmission Subs" that was added after PMWIF issuance. Hence not included in the PMWIF
GIDAP | SP-160 | Menifee Power Bank (TOT934/Q1645) | 33.738420, -117.170142 | Menifee, Riverside County | The IC, Inland Empire Energy Center LLC, is proposing to interconnect to Colorado River 220 kV Substation with a POI of 680 MW consisting of Battery Energy Storage Systems. | New Generation Interconnection Customer | Install facilities for TOT Generation Station | N/A | Generation Interconnection | N/A | 2023-09-14 | N/A | Power Flow, Transient, Post Transient, and Short Circuit Duty | N/A | Non-HFRA | See Note 16C | Extreme Temperature Conditions | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | 0.75 | N/A | 500 kV | 500/34 kV, 295 MVA | See Note 23B | 2 Separate WOs | 2 Separate CWBS | 8430 | See Note 27A | Yes | 2022 | 2021 | LGIA | 2021 | NA, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | Not Yet Operational | Not Yet Operational | N/A | N/A | N/A | N/A | N/A | Exempt: Not subject to GO 131-D licensing | N/A | Pre-construction | See Note 46A | 2024-02-29 | No | 2024-03-01 | 2024-05-01 | N/A | 3763 | 3763 | See Note 53A | 988.1585 | 510.495 | 172.429 | 273.507 | 0 | 0 | 0 | 956.431 | 0 | 0 | 0 | 0 | 31.7275 | 31.7275 | 14.1245 | See Note 57A | 100% | See Note 59A | 31.7275 | None | 100% | 0% | 49 and 52 Origination = Verified PMWIF (Project Summary V.1) PMWIF Approval Date = 02/04/2022 Latest Approved Project Summary Version = V.1
GIDAP | SP-161 | Centennial Flats (TOT899/Q1529) | 33.5736, -113.5246 | Salome / La Paz County / AZ | The IC, Upstream HC-1 LLC, is proposing to interconnect to Cielo Azul 500 kV Switchyard at the DCRT System (Arizona) with a POI of 913.56 MW consisting of PV and Battery Energy Storage Systems. This project is only to add CRAS and remote monitoring from the West of Colorado River CRAS. | New Generation Interconnection Customer | Install facilities for TOT Generation Station | N/A | Generation Interconnection | N/A | 2023-10-11 | N/A | Power Flow, Transient, Post Transient, and Short Circuit Duty | N/A | Non-HFRA | See Note 16C | Extreme Temperature Conditions | Donald Johnson, MPO - Project Dev. & Execution (3rd Party) | N/A | N/A | 500 kV | N/A | See Note 23B | 4 Separate WOs | 4 separate CWBS | 8541 | See Note 27A | Yes | 2023 | 2023 | LGIA | 2023 | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | N/A, considered under the CAISO Generation Interconnection Process | Not Yet Operational | Not Yet Operational | TBD | TBD | TBD | TBD | TBD | TBD | TBD | Planning | See Note 46A | 2026-01-12 | No | 2026-07-18 | 2026-02-09 | N/A | 1248 | 1248 | See Note 53A | 943.903 | 20.451 | 83.379 | 313.96 | 195.747 | 330.366 | 0 | 943.903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | See Note 57A | 100% | See Note 59A | 0 | None | 100% | 0% | 49 and 52 Origination = Verified PMWIF (Project Summary V.0) PMWIF Approval Date = 06/23/2023 Latest Approved Project Summary Version = V.0

## Supplement- Part 1
2239.9401
FERC Stakeholder Review Process
Supplemental Response - Part 1
Utility Prioritization Code Rank
Introduction:
SCE does not currently maintain an enterprise-wide quantitative mechanism that scores and prioritizes all programs and projects. However, several programs have prioritization methods applicable to projects within the program. To illustrate this, SCE is providing additional detail for how work is identified and prioritized for many of these programs. SCE’s analysis and prioritization is continually evolving as it seeks to continuously improve – as such, the methods by which assets are identified for replacement, and the prioritization of those replacements, may change over time. In this document, SCE represents and explains the most recent methods used, which follow and summarize those presented in SCE’s 2021 General Rate Case application (A.19-08-013), filed August 30, 2019. Note that the explanations contained herein are meant to provide descriptions of the prioritization processes that SCE uses for various types of equipment replacements and work efforts, the specific prioritization criteria and details contained in the accompanying program manuals and related documents are controlling and prevail over the explanations contained herein.
In general, and where applicable, replacement of assets such as transformers and circuit breakers are identified using a risk informed prioritization. Reprioritization occurs as field conditions change and/or as new projects are identified to address other issues at the same substation, which can allow projects to be performed together for operational and/or cost efficiency purposes. In some cases, coordination or bundling of projects may be the optimal solution due to engineering and/or construction resource constraints. Assets are typically replaced on a preventive basis based on equipment health assessment and the results of visual inspections.
This document describes the prioritization process for certain programs/projects included in SCE’s Stakeholder Review Process submission, including:
Asset and Item in Stakeholder Review Process (#2 – Project Name)
Circuit Breakers
Replace Bulk CBs - 220kV & 500kV (FERC)
Transformers
Substation Transformer Bank Replacement Program (AA-Bank & A-Bank)
Relays, Protection, Control
Non-Bulk Relay Replacement Program ("SRRP")
Bulk Power 500kV & 220kV Line Relay Replacement
Relays, Protection and Control Replacements
Substation Switchracks
Substation Switchrack Rebuild
Transmission Lines
Line Rating Mitigation-Transmission Lines
Circuit Breakers
Blanket “Projects” applicable to this section:
Replace Bulk CBs - 220kV & 500kV (FERC)
Replace Non-Bulk CBs-115kV & Below (CPUC)
Program Description:
Circuit breakers are major pieces of equipment used to interrupt the flow of electricity through a circuit. Circuit breakers are essential in preventing equipment damage and public injury when faults occur in their downstream circuits. The Substation – Infrastructure Replacement (Sub IR) program identifies and replaces bulk power circuit breakers approaching the end of their service lives that contain parts known to be problematic or no longer available, or that can no longer be cost-effectively maintained.
Prioritization Process:
Weibull Analysis: The first part of developing the Circuit Breaker Replacement program forecast is to identify the annual quantity and type of circuit breakers that need to be replaced. Since 2012, SCE continues to improve the data quality and the data refresh frequency supporting the evaluation process for circuit breaker replacement. Currently, the Weibull analysis shows the relationship between age and the probability of in-service failure based on historical removals and failures of circuit breakers. From this analysis, a Weibull curve determines the mean time to wear-out of circuit breakers. By multiplying the probability of failure of circuit breakers by the number of circuit breakers in each age group, the number of circuit breakers reaching the end of their service lives in future years can be determined.
Prioritization: Once the forecast quantity of circuit breakers expected to reach the end of their service lives each year is identified, the next step is to select the specific circuit breakers to be replaced each year. To accomplish this, SCE incorporates factors such as a circuit breaker’s age, number of operations, number of faults experienced, the mechanism type, the number of corrective maintenance orders, results of oil analysis (when applicable), and severity of consequences that would result from an in-service failure in relation to cost to mitigate risk of circuit failures. This collectively helps to determine the “health” of the asset.
Further Risk Analysis: As part of its 2021 GRC, SCE introduced another tool which evaluates the risks associated with distribution circuit breakers within the system to further inform circuit breaker prioritization. Through this analysis, SCE assesses safety and reliability risks associated with circuit breaker failures due to deterioration overtime. This analysis considers the frequency and consequence of circuit breakers. For failure at service frequency, the risk analysis is based on equipment age, type (gas, oil, magnetic, vacuum, etc.), and condition to calculate probability of failure. For failure consequences, the analysis is based on population density, potential severity of crew injuries, and outage durations. The results of the risk analysis provide SCE with an understanding of the relative risk prioritization of circuit breakers within its system. It also helps to inform the prioritization for which circuit breakers to select for replacement. In addition to risk assessment results, several other factors including dependencies with other programs, field observations, and the existing queue of breaker replacements inform the final prioritization of circuit breaker replacements. From this algorithm-derived replacement prioritization, five-year replacement schedules are drafted.
Final Adjustments: Two adjustments are then made. First, the draft schedule is adjusted as necessary by a team of technical experts to ensure that factors difficult to quantify are incorporated into the prioritization process such that high-risk circuit breakers are not overlooked. In some cases, this may mean that circuit breakers are added to the five-year plan based on real-time conditions and circumstances within the electrical system. Second, if equipment conditions allow, the draft schedule is adjusted to optimize the construction aspect of the replacements. In other words, efforts are made to combine multiple projects (involving transformer replacement, circuit breaker replacement, or some other major work activity) at a substation into a larger single project to avoid return visits to a substation within a reasonable planning horizon.
Transformers
Blanket “Projects” applicable to this section:
Substation Transformer Bank Replacement Program (AA-Bank & A-Bank)
Program Description:
Substation transformers are major pieces of equipment used to either (1) increase electricity voltage to reduce energy losses during its transmission over long distances, or (2) reduce electricity voltage to make it more practical for use by the customer. SCE identifies and replaces transformers approaching the end of their service lives, which contain parts known to be problematic or are no longer available.
Prioritization Process:
Weibull Analysis: The Substation Transformer Bank Replacement also utilizes the same scoping selection process as the Sub IR Circuit Breaker Replacement program. This includes using a Weibull Curve Analysis to identify the volume of transformers replacements needed.
Prioritization: After deriving the number of transformers to be replaced each year, SCE identifies those transformers whose replacement is most urgent. SCE accomplishes this by analyzing each transformer’s age, loading, fault counts, maintenance orders, oil quality, oil dissolved gas analysis results, manufacturer, and severity of consequences that would result from an in-service failure. This collectively helps to determine the “health” of the asset.
Further Risk Analysis: Similar to the analysis of CBs, SCE will also evaluate risks associated with A- and B-bank transformers within the system, and to help prioritize replacements of those assets. SCE assesses safety and reliability risks associated with transformer failures due to deterioration over time. The failure consequence calculations are based on population density, potential severity of crew injuries, and outage durations. The results of this analysis provide SCE with an understanding of the relative risk prioritization of transformers within its system. It also helps to inform the prioritization for which transformers to select for replacement.
In addition to risk assessment results, several other factors are considered to inform the final prioritization of transformer replacements, including dependencies with other programs, field observations, and the existing queue of other infrastructure replacements. From this replacement prioritization, a five-year replacement schedule is drafted.
Final Adjustments: Two adjustments are then made to this draft replacement schedule. The draft schedule is adjusted as necessary by a team of technical experts to ensure that factors difficult to quantify are incorporated into the prioritization process such that high-risk transformers are not overlooked. In some cases, this results in additional transformers, or a different mix of transformers, identified as requiring replacement compared to the Weibull analysis. Second, if equipment conditions allow, the draft schedule is adjusted to optimize the construction aspects of the replacements. In other words, efforts are made to combine multiple projects (involving transformer replacement, circuit breaker replacement, or some other major work activity) at a substation into a larger single project to avoid return visits to that substation within a reasonable planning horizon.
In summary, the replacement of substation transformers is managed in Substation Infrastructure Replacement program through engineering analysis combined with expert judgment to ensure that the appropriate number of transformers are replaced each year and those which are replaced are the most at-risk of failure.
Relay Replacements
Blanket “Projects” applicable to this section:
Non-Bulk Relay Replacement Program ("SRRP")
Bulk Power 500kV & 220kV Line Relay Replacement
Relays, Protection and Control Replacements
Program Description:
The Substation Relays, Protection, and Control Replacement program identifies and proactively replaces substation protective relays, control, automation, monitoring and event recording equipment to address equipment obsolescence, meet compliance requirements (where applicable), and improve functionality. Upgrading obsolete electromechanical and solid-state relays with fast acting microprocessor relays improves power grid reliability, power quality, and safety to the public and to SCE personnel.
Prioritization:
Relay replacements are selected and prioritized based upon a number of factors, including the age of the relay; relay obsolescence; level of effort required to maintain and operate; system criticality; incorporating newer technologies and capabilities; and current protection and compliance requirements.
Age of the relay and Obsolescence: Relays that have reached their end of life and are longer serviceable are targeted for replacement. This reduces the likelihood of an in-service relay failure as older relays have a higher probability of failure.
Newer relays have improved functionality and capabilities such as the ability to perform multiple functions within one unit and additional capabilities, such as sequence of events recording. SCE may want to replace an electromechanical relay with a digital relay for added functions that are included with a digital relay.
Level of required effort: There are some relays that require excessive resources to maintain. It may not be prudent to keep maintaining such relays due to the complexity and uniqueness of the relay and a need for unique, specified knowledge to maintain them.
System criticality: The criticality of the system the relay protects is also taken into consideration if a relay were to fail or have a mis-operation. In this scenario, SCE decides to replace an older relay proactively, rather than react to a failure or other emergency involving the relay.
Current protection and compliance requirements: The current relay may not be capable of meeting new compliance requirements or protection needs, such as relay coordination parameters.
Due to the obsolescence of the communication interfacing hardware that support some of SCE’s substation automation, SCE plans to accelerate its proactive replacement projects starting in calendar year 2021. The number of projects takes into consideration available resources and outage coordination required to execute the replacements.
Substation Switchrack Rebuild
Blanket “Projects” applicable to this section:
Substation Switchrack Rebuild
Program Description:
A substation switchrack is the skeletal/structural system used to support substation assets such as circuit breakers, disconnects, and conductors. This program captures the expenditures related to rebuilding existing substation racks based on conditions and circumstances found in the field, as well as through various analyses including structural and seismic analysis. Substation structures degrade over time and need to be replaced and/or upgraded.
Prioritization Process:
The switchracks/structure needs are initially identified at the scoping job walk, typically driven by circuit breaker and transformer replacements, and in some cases disconnect switch replacements. Various other drivers can trigger a switchrack rebuild, some include, but are not limited to:
Deteriorated condition of structures such as wood poles, lattice or pipe-steel;
Cubicle switchgear due to aged equipment, deteriorated enclosure and confined working space;
Seismic needs;
Feasibility of new equipment installation, such as Circuit Breaker or Transformer Replacements on or within the switchrack;
Physical congestion and/or lack of required clearances that create unsafe operating conditions;
Non-standard electrical switchrack configurations.
At the scoping job walk the field personnel (operations, construction, maintenance, etc.) and engineering personnel evaluate and determine the project scope. These workers evaluate the condition of foundations, equipment, structures, and working areas/to identify the need to potentially perform a switchrack rebuild project.
Transmission Line Rating Remediation
Blanket “Projects” applicable to this section:
Line Rating Mitigation-Transmission Lines
Program Description:
This program remediates transmission line discrepancies in accordance with CPUC GO 95.
Prioritization Process:
SCE surveyed all of SCE’s CAISO-controlled transmission lines built before 2005 to identify spans potentially not meeting CPUC’s GO 95 clearance requirements under certain operating and atmospheric conditions. Based on the results of the survey, SCE prioritized the transmission line discrepancies that will require line clearance remediation. A discrepancy is any condition found in the field requiring remediation to meet GO 95 requirements during peak loading conditions. Discrepancies have been prioritized based on criteria such as line sag when operating at or below 130 degrees Fahrenheit, and potential risk to public safety and system reliability based on location of span, terrain, encroachment type, and extent of deviation from standards. The study prioritized the discrepancies within a span into six levels, with A1 being the highest priority, followed by A2, A3, B1, B2, and B3. Remediation work to address discrepancies includes replacing towers and poles, clearing brush, replacing insulators, removing slack from lines, etc. to remediate line clearance issues.
SCE analyzes entire circuits holistically to identify the most cost-efficient and least-disruptive strategy to remediate the discrepancies. SCE considers the following factors when identifying the most cost-efficient and least-disruptive strategy to remediate circuits:
Geographic proximity
Government land or land agency overlap
Permitting similarities
Engineering design
Construction methods
Outage opportunities or restrictions
Material and procurement efficiency
Remediation by working on lower voltages
TLRR discrepancies are initiated and planned based on the following constraints:
Outage constraints and opportunities within the system and other TLRR and SCE projects
Government land and other agency permitting schedule impacts
Balancing of workload based on resourcing capabilities and to ensure work can be performed safely and efficiently
Bundling of projects for construction efficiencies that include the same scope in similar regions

## Supplement- Part 2
Project Description
FERC Stakeholder Review Process
Supplement to Response - Part 2
Utility Capital Approval Processes
SCE has an internal capital planning process that governs and allocates capital across the company. This involves two general processes:
Annual Capital Operating Plan Process
SCE’s annual capital operating plan process is the mechanism through which each organizational unit, and the Company, reviews and approves initial capital plans. Program funding levels are approved through this process. Planning teams within the organizational unit develop capital forecasts for work over a five year period. Within the substation and bulk transmission areas specifically, the development of these forecasts considers work already released for execution through a Project Management Work Initiation Form (PMWIF), as well as anticipated work required to support the safety, reliability and affordability of the electric service we provide to our customers.
After capital plans have been reviewed and approved by each organizational unit, they are consolidated into a corporate forecast for further review. SCE’s senior management then reviews and approves the company capital plan. SCE’s Finance department leads this process.
Capital Governance Committee
In some cases, capital projects that meet predefined thresholds are required to be further reviewed and approved by SCE senior management through SCE’s capital governance committee, known as the Finance and Risk Management Committee (FRM), prior to implementation. The purpose of FRM is to oversee and approve the allocation of SCE’s financial resources, energy procurement activities, and enterprise risk management. T&D projects greater than $25 million require FRM review and approval. FRM was established in October 2016, and replaced SCE’s previous capital governance body – the SCE Capital Review Team (CRT).
The Audit and Finance Committee of the Board of Directors’ ultimately reviews and approves individual capital projects with total expected costs in excess of $250 million which are not included in the Annual Capital Budget.
Note: Within this response, SCE has identified the approval process for each project in column 31.